## Sheet1
VR BENGALURU (VRB MALL) - FOOD BOX AREA SNAG LIST
Engineering & Facility Management ¦ VR Dakshin Pvt Ltd
Report Start Date |  | 2026-08-17 |  | Prepared By: | Total Snags:124
Completion Date |  | 2026-08-22
S.No | Area / Location | Category | Snag Description | Risk Level | Status | Remarks
1 | Food Box - General | Fire & Life Safety | Detector cables are hanging and not properly laid. Proper conduit routing is required. | High | Open
2 | Food Box - General | Electrical | LED light drivers are not properly fixed, and wire joints are exposed outside. | High | Open
3 | Opp. McD Shop | HVAC - Chilled Water | Chilled water line insulation needs to be completed in front of the McD shop. | Medium | Open
4 | Food Box - Passages | Lighting | Lux level in all Food Box passages is very low and needs to be improved. | Medium | Open
5 | Food Box - General | HVAC - CSU | All CSU units have accumulated dust and need to be cleaned properly. | Low | Open
6 | Food Box Entry | Electrical | Food Box entry CSU unwanted cables and cable joints are exposed outside. Unwanted cables need to be removed and joints properly enclosed. | High | Open
7 | Food Box - General | HVAC - CSU | CSU incoming cables are not properly laid and need proper routing and securing. | Medium | Open
8 | Food Box Entry | Electrical | Food Box entry CSU incoming cable box is damaged and needs to be replaced. | High | Open
9 | Food Box - General | CCTV | All camera cables are laid without conduit. Cables are hanging and visible; proper conduit routing and dressing is required. | Medium | Open
10 | Food Box - General | HVAC - CSU | All CSU units are operating only in manual mode. Auto mode is not functioning and needs to be rectified. | High | Open
11 | Food Box - General | HVAC - CSU | All CSU units need proper naming and numbering. | Low | Open
12 | Near 3rd Puller CSU | HVAC - Chilled Water | Chilled water line leakage observed near the 3rd Puller CSU. | High | Open
13 | Food Box - General | HVAC - CSU | All CSU sensor cables are hanging around the CSU units and need proper cable dressing. | Medium | Open
14 | Food Box - General | Lighting | All Food Box LED lighting cables are visible outside and need proper routing/concealing. | Medium | Open
15 | Food Box - General | Electrical | LED light drivers are not properly fixed. Proper connectors must be used for cable joints, and all exposed joints need to be properly enclosed. | High | Open
16 | Food Box - General | HVAC - CSU | Operation of all CSU units needs to be demonstrated to the operations team. | Low | Open
17 | Opp. McD Shop | HVAC - CSU | CSU unit opposite the McD shop: Filter is not available and needs to be provided. | Medium | Open
18 | Food Box - General | Documentation | Installation and service reports for all CSU units need to be shared. | Low | Open
19 | Food Box - General | HVAC - Chilled Water | Flow direction markings are missing on all chilled water lines. Proper flow direction arrows need to be provided. | Low | Open
20 | Food Box - General | Lighting | All LED light cables are laid without conduit pipes. Cables are hanging and exposed outside; proper conduit routing and cable dressing is required. | Medium | Open
21 | Near Piller No. 4 CSU | Electrical | PVC box near Piller No. 4 CSU is damaged and needs to be replaced. | High | Open
22 | Near Piller No. 4 CSU | HVAC - Chilled Water | Piller No. 4 CSU drain line insulation is not properly done and needs to be rectified. | Medium | Open
23 | Food Box - General | HVAC - Ducting | All AC ducts have accumulated dust and need to be cleaned properly. | Medium | Open
24 | Opp. McD Shop | Electrical | In front of McD shop CSU, the connection box is damaged and needs to be replaced. | High | Open
25 | Opp. McD Shop | Electrical | Near the McD shop CSU unit, cable joints are not properly done and need to be rectified using proper connectors and enclosures. | High | Open
26 | Food Box - General | Electrical | All unwanted hanging cables in the ceiling across the Food Box area need to be removed. | Medium | Open
27 | Opp. McD Shop | Electrical | Junction box beside the McD CSU unit is damaged and the cover is missing. It needs to be replaced/properly covered. | High | Open
28 | Food Box Entry | Electrical | Near the Food Box entry corner, cables and cable joints are visible from the passage and need to be properly concealed and dressed. | Medium | Open
29 | West-Side Wall | HVAC - Ducting | Duct grille is missing beside the west-side wall and needs to be provided. | Medium | Open
30 | Food Box - General | Lighting | EL lighting identification is not done and needs to be provided. | Low | Open
31 | Food Box - General | CCTV | Camera naming and numbering are not done and need to be completed. | Low | Open
32 | Near McD Shop / Piller 3 | HVAC - CSU | Abnormal sound observed from the CSU near the McD shop and Piller No. 3. Need to inspect and rectify. | High | Open
33 | LT Room | Electrical | Unwanted materials inside the Food Box LT room need to be removed. | Low | Open
34 | LT Room | Electrical | LT room incoming and outgoing cables are not properly named/marked. Proper cable identification and marking need to be completed. | Medium | Open
35 | LT Room | Networking | Network cable connection work is pending, and cables are hanging inside the LT room. | Medium | Open
36 | Food Box - General | HVAC - Ducting | All duct grills have accumulated dust and need to be cleaned properly. | Low | Open
37 | Food Box - General | HVAC - Mechanical | All exhaust and FTA units need to be operational, and their operation should be demonstrated to the operations team. | Medium | Open
RISK SUMMARY
High | 13
Medium | 18
Low | 13
FOOD BOX AREA - FIRE & LIFE SAFETY (FLS)
Observation Date: 20-07-2026 ¦ Total FLS Observations: 93
S.No | Area / Location | Category | Snag Description | Risk Level | Status | Remarks
1 | Food Box Extension | Fire & Life Safety | Food Box extension area upright sprinkler bulb needs to be replaced with a new sprinkler bulb. | High | Pending
2 | Food Box - General | Fire & Life Safety | Sprinkler line painting needs to be completed. | High | Pending
3 | Food Box - General | Fire & Life Safety | Sprinkler bulb cap needs to be removed. | High | Pending
4 | Food Box Extension | Fire & Life Safety | Extension area detector cable SS gland needs to be installed. | High | Pending
5 | Food Box - General | Fire & Life Safety | Sprinkler flexible alignment work needs to be completed. | High | Pending
6 | Food Box - General | Fire & Life Safety | Existing PNG gas line needs to be removed from the true ceiling. | Medium | Pending
7 | Food Box - General | Fire & Life Safety | PVR Drain pipe line red painted. Pipe line naming/identification marking needs to be done. | Low | Pending
8 | Food Box - General | Fire & Life Safety | Fire cable dressing above the false ceiling needs to be completed. | Medium | Pending
9 | BOH Area | Fire & Life Safety | Emergency lights need to be installed in the common area and BOH area. | High | Pending
10 | BOH Area | Fire & Life Safety | LED fire exit signage needs to be installed in the Food Box common area and BOH area. | Medium | Pending
11 | Food Box - General | Fire & Life Safety | BFC detector cable dressing needs to be completed with proper cable support. | High | Pending
12 | Food Box - General | Fire & Life Safety | Speaker cable dressing needs to be completed. | Medium | Pending
13 | Food Box - General | Fire & Life Safety | BFC detector connection cable is fully skinned out and needs to be reconnected properly. | High | Pending
14 | Opp. McD Shop | Fire & Life Safety | Fire exit door near MCD store requires installation of push bar and door closer. | Medium | Pending
15 | Opp. McD Shop | Fire & Life Safety | Pressure gauge needs to be installed on the sprinkler line coming from Staircase-04 near MCD. | High | Pending
16 | Electrical Room | Fire & Life Safety | BFC detector needs to be installed in the electrical room passage area. | High | Pending
17 | Food Box - General | Fire & Life Safety | Fire cables inside all stores need to be dropped through enclosure boxes with proper cable dressing and cable glands. | Medium | Pending
18 | BOH Area | Fire & Life Safety | BOH area sprinkler bulb is obstructed by the duct and needs to be relocated below the duct. | High | Pending
19 | BOH Area | Fire & Life Safety | Existing 79°C sprinkler bulb in BOH area needs to be replaced with a 68°C sprinkler bulb. | High | Pending
20 | BOH Area | Fire & Life Safety | Detector needs to be installed in the BOH area. | High | Pending
21 | BOH Area | Fire & Life Safety | Emergency lighting fixtures shall be provided and installed throughout all BOH (Back of House) areas to ensure safe evacuation and adequate illumination during power failures and emergency situations | High | Pending
22 | Food Box - General | Fire & Life Safety | All emergency lights shall be installed to ensure easy identification during emergency situations and power failures. The markings shall be clearly visible | High | Pending
23 | Food Box - General | Fire & Life Safety | PNG line painting needs to be completed. | Low | Pending
24 | Food Box - General | Fire & Life Safety | Pressure gauges need to be installed on PNG lines in all stores. | Medium | Pending
25 | Food Box - General | Fire & Life Safety | PNG line direction arrow marking needs to be completed. | Low | Pending
26 | Food Box - General | Fire & Life Safety | Copper jumpers need to be installed across all PNG line flanges. | Medium | Pending
27 | Food Box - General | Fire & Life Safety | Dummy caps need to be installed at PNG line ends inside all stores. | Medium | Pending
28 | Food Box - General | Fire & Life Safety | GLDS sensor installation work is under progress. | High | Pending
29 | Store-05 | Fire & Life Safety | GLDS sensor installation at Store-05 is not in the correct location and requires rectification. | High | Pending
30 | Store-06 | Fire & Life Safety | GLDS sensor is not installed at Store-06. | High | Pending
31 | Dish Wash Room | Fire & Life Safety | Sprinkler flexible inside the dish wash room needs to be removed and terminated with a dummy connection. | High | Pending
32 | Dish Wash Room | Fire & Life Safety | Sprinkler line painting inside the dish wash room needs to be completed. | High | Pending
33 | Dish Wash Room | Fire & Life Safety | Sprinkler pipe support opposite the dish wash room needs to be installed. | High | Pending
34 | KFC Backside | Fire & Life Safety | Smoke detector needs to be installed at the KFC backside with proper access provision. | High | Pending
35 | KFC Backside | Fire & Life Safety | Sprinkler flexible at the KFC backside needs to be removed and the sprinkler dropped below the duct. | High | Pending
36 | Staircase-04 | Fire & Life Safety | BFC detector cable near the staircase needs to be dropped. | High | Pending
37 | BOH Area | Fire & Life Safety | Sprinkler flexible in BOH Room-01 needs to be removed and install sprinkler bulb, | High | Pending
38 | BOH Area | Fire & Life Safety | BFC detector cable in the BOH passage area needs to be dropped. | High | Pending
39 | Electrical Room | Fire & Life Safety | Mall loop cable needs to be dropped inside the electrical room for mall integration. | Medium | Pending
40 | Food Box - General | Fire & Life Safety | Direct UPS power supply needs to be provided to the fire alarm panel. | High | Pending
41 | Food Box - General | Fire & Life Safety | Commissioning of all devices is pending. | High | Pending
42 | Food Box - General | Fire & Life Safety | Naming stickers need to be installed for all fire alarm panel buttons. | High | Pending
43 | Food Box - General | Fire & Life Safety | All integration modules need to be installed above the fire alarm panel. | High | Pending
44 | Food Box - General | Fire & Life Safety | GLDS panel integration with the fire alarm panel needs to be completed. | High | Pending
45 | Food Box - General | Fire & Life Safety | Fire alarm panel battery needs to be installed. | High | Pending
46 | Electrical Room | Fire & Life Safety | One additional detector needs to be installed inside the electrical room, as the existing detector is inadequate | High | Pending
47 | Food Box - General | Fire & Life Safety | Direct UPS power supply needs to be provided to the GLDS panel. | High | Pending
48 | Electrical Room | Electrical | ISI-marked rubber mat needs to be placed in front of all panels inside the electrical room. | Medium | Pending
49 | Electrical Room | Fire & Life Safety | Emergency lights need to be installed inside the electrical room. | High | Pending
50 | Electrical Room | Electrical | 30 mA RCCB protection needs to be provided in the electrical room wherever pending. | Medium | Pending
51 | Electrical Room | Fire & Life Safety | PA speaker needs to be installed inside the electrical room. | Medium | Pending
52 | Food Box - General | Electrical | Door earthing needs to be provided for all electrical panels. | Medium | Pending
53 | Food Box - General | Electrical | Existing MCB in Electrical DB Panel-01 needs to be replaced with a 30 mA RCCB. | Medium | Pending
54 | Food Box - General | Electrical | Labeling of all electrical DB panels needs to be completed. | Low | Pending
55 | Food Box - General | Electrical | Earthing strip connection needs to be provided for all electrical panel cable glands. | Medium | Pending
56 | Food Box - General | Fire & Life Safety | 2kg tube suppression system cylinders need to be installed for four electrical panels and integrated with the fire alarm panel. | High | Pending
57 | Electrical Room | Fire & Life Safety | 5kg 3no modular fire extinguishers need to be installed in the electrical room above the Electrical DB Panel, Exhaust Panel, and Fresh Air Panel. And warranty certificate need to be submit | High | Pending
58 | Food Box - General | Electrical | Gland earthing needs to be provided for all CSU panels. | Medium | Pending
59 | Food Box - General | Electrical | Double earthing with nut and bolt connections needs to be provided for all CSU starter panels. | Medium | Pending
60 | Food Box - General | Fire & Life Safety | All CSU units need to be integrated with the Fire Alarm Panel. Upon activation of any fire alarm condition, all CSU units shall automatically shut down. | High | Pending
61 | Food Box - General | Fire & Life Safety | Food Box Fresh Air Panel needs to be integrated with the Fire Alarm Panel. Upon activation of any fire alarm condition, the Fresh Air System shall automatically shut down | High | Pending
62 | Food Box - General | Fire & Life Safety | Food box Fire alarm panel need to be integrate with BMS fire panel ( Fire and Fault integration) | High | Pending
63 | Food Box - General | Fire & Life Safety | Tube Suppression System shall be integrated with the Fire Alarm Panel for alarm, monitoring, and activation status indication. | High | Pending
64 | Food Box - General | Fire & Life Safety | Emergency escape route maps with auto-glow signage shall be installed at multiple locations. | High | Pending
65 | BOH Area | Fire & Life Safety | Fire extinguishers (ABC, Foam, and CO₂ type) shall be installed in all common areas and BOH (Back of House) areas. | High | Pending
66 | Food Box - General | Fire & Life Safety | Auto-glow signage for all fire extinguishers shall be installed. | High | Pending
67 | Food Box - General | Fire & Life Safety | Dummy caps shall be provided and installed on all unused openings | Medium | Pending
68 | Electrical Room | Electrical | Electrical Room 440 Volts Danger warning signage shall be provided and installed in 7 languages with auto-glow (photoluminescent) signage to ensure visibility during power failures and emergency conditions | High | Pending
69 | Food Box - General | Fire & Life Safety | Warranty certificates for all fire extinguishers shall be submitted. | High | Pending
70 | Food Box - General | Fire & Life Safety | Sprinkler line pressure testing certificate shall be submitted. | High | Pending
71 | Food Box - General | Fire & Life Safety | GLDS (Gas Leak Detection System) panel warranty certificate along with as-built drawings shall be submitted. | High | Pending
72 | Food Box - General | Fire & Life Safety | GLDS panel and sensor demonstration/start-up shall be conducted with the mall team. | High | Pending
73 | Food Box - General | Fire & Life Safety | Fire alarm panel and all associated devices shall be commissioned. Upon completion, a demonstration shall be conducted with the mall team. | High | Pending
74 | Food Box - General | Fire & Life Safety | PNG (Piped Natural Gas) line leak test and nitrogen gas pressure testing shall be completed, and the test certificates shall be submitted. | Low | Pending
75 | Food Box - General | Fire & Life Safety | As-built drawings for the Fire Alarm System, Public Address (PA), PNG pipeline, and Gas Leak Detection System shall be submitted. | High | Pending
76 | Food Box - General | Fire & Life Safety | Third-party inspection and audit of the PNG pipeline shall be completed, and the corresponding audit certificate/report shall be submitted. | Low | Pending
77 | Food Box - General | Fire & Life Safety | PNG meter warranty certificate and manufacturer warranty documents shall be submitted | Low | Pending
78 | Food Box - General | Fire & Life Safety | Warranty certificate for the PNG gas line pressure gauge shall be submitted. | Low | Pending
79 | Food Box - General | Fire & Life Safety | Public Address (PA) system installation, testing, and commissioning shall be completed, and a demonstration shall be conducted with the mall team. | High | Pending
80 | Food Box - General | Fire & Life Safety | As-built drawings of the complete sprinkler piping system, including all installed components and routing details, shall be submitted | High | Pending
81 | Opp. McD Shop | Fire & Life Safety | McDonald's store inside GLDS panel needs to be integrated with the Food Box fire alarm panel | High | Pending
82 | Food Box - General | Fire & Life Safety | Sprinkler bulb rosette caps shall be installed at all applicable locations. | High | Pending
83 | Food Box - General | Fire & Life Safety | Protective caps were observed on the detectors above and below the false ceiling. All detector caps shall be removed prior to system commissioning. | High | Pending
84 | Food Box - General | Fire & Life Safety | Gland earthing was not provided at the GLDS panels. Gland earthing shall be installed for all panels as per applicable standards and specifications | High | Pending
85 | Electrical Room | Fire & Life Safety | Fire door installation in all BOH store areas remains pending. Although the electrical room fire door has been installed, all fire door certification documents shall be submitted for review and record purposes. | Medium | Pending
86 | Food Box - General | Fire & Life Safety | Food Box PA system should be connected to the Mall PA system to ensure that, in the event of an emergency, the Mall evacuation message is automatically broadcast in the Food Box area as well. Kindly review the existing setup and complete the required integration on high priority. This is a critical life safety requirement and should be addressed at the earliest | High | Pending
87 | Opp. McD Shop | Fire & Life Safety | The main sprinkler line butterfly valve at the back side of the MCD store is not accessible for operation. Kindly inspect the location and make the valve easily accessible for operation. | High | Pending
FLS RISK SUMMARY
High | 59
Medium | 26
Low | 8
Medium | 9
Low | 5