## ASSUMPTIONS & EXCLUSIONS-ELECTR
ELECTRICAL WORKS FOR COWRKS, MORGAN STANLEY,6A-1ST & 2ND FLOOR,BANGALORE
CLIENT | : MORGAN STANLEY | DATE / REV NO. | :10.03.2026 / R1
ARCHITECTS | : COWORKS | SUBJECT | : ASSUMPTIONS & EXCLUSIONS
PMC | : | CONSULTANTS | : ESOLLUTIONS
ASSUMPTIONS & EXCLUSIONS
1 | Lighting for modification area is considered as same light fixtures. Removal cost is considered as a lumpsum & Supply cost is considered as separately
2 | Washroom area light fixtures area considered as recess mounted and included supply & installation for the same.
3 | Circuit mains & looping are considered for demolition area for lighting
4 | Cables for HVAC circuits are considered from existing floor panel
5 | Power sockets are only considered for HVAC circuits and washroom area
6 | Cable trays are considered for VRF ODU from existing panels
7 | Open office area removal & refixing is not considered
8 | Phone booth sockets are considered

## ELECTRICAL - SUMMARY
ELECTRICAL WORKS FOR COWRKS, MORGAN STANLEY,6A-1ST & 2ND FLOOR,BANGALORE
CLIENT | : MORGAN STANLEY |  | DATE / REV NO. | :10.03.2026 / R1
ARCHITECTS | : COWORKS |  | SUBJECT | : SUMMARY
PMC | : |  | CONSULTANTS | : ESOLLUTIONS
BILL OF QUANTITIES - SUMMARY
SL.NO. | DESCRIPTION | AMOUNT IN INR
|  | SUPPLY | INSTALLATION | TOTAL
1 | LT PANELS | 13736 | 2080 | 15816
2 | LT CABLES | 170236 | 37160 | 207396
3 | MCB DISTRIBUTION BOARDS | 0 | 0 | 0
4 | CIRCUITMAINS / SUBMAINS | 298600 | 59120 | 357720
5 | POWER RECEPTACLES | 25936 | 5632 | 31568
6 | POINT WIRING | 49408 | 9991 | 59399
7 | CABLE TRAY | 149730 | 29450 | 179180
8 | RACEWAYS/CONDUITS | 21880 | 5310 | 27190
9 | EARTHING | 18312 | 3108 | 21420
10 | MISCELLANEOUS ITEMS | 52927.5 | 18876.25 | 71803.75
|  | 0 | 0
| SUB TOTAL-1 |  |  | 971492.75
11 | FUNCTIONAL & DECORATIVE LIGHT FIXTURE |  | 62400 | 62400
0
| SUB TOTAL-2 |  |  | 62400
| GRAND TOTAL |  |  | 1033892.75
| GST 18% on Supply Items |  |  | 0
| GST 18% on Supply Items |  |  | 0
| GST 18% on Supply Items |  |  | 0
| GST 18% on Installation Items |  |  | 0
| GRAND TOTAL |  |  | 1033892.75

## LT WORKS
ELECTRICAL WORKS FOR COWRKS, MORGAN STANLEY,6A-1ST & 2ND FLOOR,BANGALORE
CLIENT | : MORGAN STANLEY | [5 empty] | DATE / REV NO. |  | :10.03.2026 / R1
ARCHITECTS | : COWORKS | [5 empty] | SUBJECT |  | : LT WORKS
PMC | : | [5 empty] | CONSULTANTS |  | : ESOLLUTIONS
BILL OF QUANTITIES - LT WORKS
SL. NO. | DESCRIPTION | UNIT | Quantity |  |  | RATE IN INR |  | AMOUNT IN INR |  | TOTAL
|  |  | 1F | 2F | Total | SUPPLY | INSTALLATION | SUPPLY | INSTALLATION
1 | LT PANELS:
Panels as per technical specifications & schematic diagram.
Supply, Installation, Testing and Commissioning of Indoor type LT Switchboards, Floor mounting type, Bottom/Top entry. Refer enclosed SLD.
Enclosure: Compartmentalized Single front CRCA (Cold rolled Cold Annealed sheet steel)
Doors:2mm Body:2mm Gland:3mm covers and partitions:1.6mm
IP class:IP42 for Indoor/IP55 with weather proof enclosure for outdoor
Bus bars: Electrolytic grade conductivity as per standard IS 5082
Bus bar Material: As per SLD
Bus bar supports: DMC/FRP/SMC
Bus bar joints: Shrouded/Tinned
Protection releases: As per SLD (Adjustable over current & short circuit unless otherwise specified)
Ics=Icu for all breakers
Utilization category: All MCCB/ACB's shall be Cat: A except ACB's for Ltg & raw power input distribution panel shall be with Cat: B .
Loovers: Busbar chamber shall have louvers with fine mesh inside
Shade: Epoxy powder coated RAL 7032
Design: Modular type
Cable entry: As per site condition
Bus bar insulation: Aluminum bus bars shall be bare with color coding at the ends/Copper shall be bare with color coding at the ends/For Humidified areas the copper bus bars shall be coated with tin.
Note:
1. The Panel shall be fully as per the requirement of Electrical Inspectorate/ EB authorities.
1. Panel Should be as per IEC 61439 Design
2. Auxilliary contactor to be provided along with auto-manual switch where ever required.
3. All MCCB Breakers both Incoming & Outgoing shall have LED 'ON / OFF / TRIP' indications without fail.
4. CTs shall be with dual ratio and cast resin type only.
5. All doors to have double rubber gasket with shutter assembly & door seating frame.
6. All AC feeders will have time delays of 0-60 Seconds.
7. All MCCBs of 250A and above will be microprocessor based only.
8. Any panel if more than 1.5m width should be made in parts each part not exceeding 1.5m.
9. The current density for Aluminium busbars shall be 0.8 only.
10. The current density for Copper busbars shall be 1.2 only.
11. All UPS outgoing panels shall have neutral busbars double the size of phase.
12. All MCCB's shall have plug setting from (40or50)-100%.
13. All Lighting / RP and Lift panels shall have ELR for incomer of Prok. Dvs. Make only.
14. All test certificates must be provided immediately after commissioning.
15. SAFETY CERTIFICATE FOR THE PANELS SHALL BE PRODUCED FROM CEIG.
16. All meters shall be Digital type only.
17. FRLS PVC copper wires shall be used for control wiring
18. The MCCB should be current limiting type with trip time of less than 10 msec under short circuit conditions. The MCCB should be either 3 or 4 poles as specified in BOQ. MCCB shall comply with the requirements of the relevant standards IS13947 – Part 2/IEC 60947-2 and should have test certificates for Breaking capacities from independent test authorities CPRI / ERDA or any accredited international lab.
19. All Panel with Fire Suppression System
Important Note : - Breaker discrimination study need to carried out & Breaker/Breaker frames need to be selected accordingly.
1.1.1 | METERING CUBICLE * CT RATING OF EB METER SHOULD BE AS PER LOCAL EB REGULATION | No |  |  | 0 |  |  | 0 | 0 | 0
1.1.2 | CHANGE OVER PANEL | No |  |  | 0 |  |  | 0 | 0 | 0
1.1.3 | MAIN LT PANEL | No |  |  | 0 |  |  | 0 | 0 | 0
1.1.4 | UPS INPUT PANEL | No |  |  | 0 |  |  | 0 | 0 | 0
1.1.4 | UPS OUTPUT PANEL | No |  |  | 0 |  |  | 0 | 0 | 0
1.2 | 4P (300mA) RCBO with enclosures
1.2.1 | 16A | No |  |  | 0 |  |  | 0 | 0 | 0
1.2.2 | 25A | No |  |  | 0 |  |  | 0 | 0 | 0
1.2.3 | 63A | No |  |  | 0 |  |  | 0 | 0 | 0
1.3 | 4P MCB with enclosures (IP44)
1.3.1 | 16A 4P C-MCB | No | 1 | 1 | 2 | 1890 | 284 | 3780 | 568 | 4348
1.3.1 | 20A 4P C-MCB | No |  |  | 0 |  |  | 0 | 0 | 0
1.3.2 | 40A 4P C-MCB | No | 2 | 2 | 4 | 2489 | 378 | 9956 | 1512 | 11468
1.3.3 | 63A 4P C-MCB | No |  |  | 0 |  |  | 0 | 0 | 0
1.4 | 4P MCCB with enclosures (IP44)
1.4.1 | 80A FP MCCB | No |  |  | 0 |  |  | 0 | 0 | 0
1.4.2 | 320A FP MCCB | No |  |  | 0 |  |  | 0 | 0 | 0
| TOTAL PART - 1 - LT PANELS | [6 empty] | 13736 | 2080 | 15816
2 | LT CABLES & ENDTERMINATIONS
Supply, Laying, Testing and Commissioning of stranded XLPE insulated, Armoured/Unarmoured/Flexible, Aluminum / Copper conductor, laid in tray / hume pipe / in ready made trenches, with nylon cable ties / MS Clamps @ 600mm interval etc., as required. The cost of the nylon tie and overlapping GI strip shall be included in the cost of installation.
Supply, Installation, Testing and Commissioning of Compression type cable gland, aluminum sockets for aluminum cables / copper sockets for copper cables, insulation tape, anti corrosive paste, brass clamps for gland earthing with 14 SWG copper wire to connect to nearest earth flat.
Insulation: XLPE
Inner sheath: Extruded PVC only for Multicore
Outer sheath: Extruded Type ST2 PVC with FRLS
Voltage grade:1100Volts
Armoure: Galvanized Steel strip/Wire for multicore
Non Magnetic Aluminum Wire/Strip for Single core
Gland type : Brass with nickel plated
Compression : Double compression above 35 Sq.mm
Sealing Ring : Natural rubber for indoor, Neoprene for Outdoor
Note : Bimetalic lugs/strips need to be considered where copper cables connected to Aluminium busbars
2.1 | XLPE insulated, steel armoured, aluminium conductor 3.5 Core cables. | [8 empty] | 0
0
2.1.1a | 3.5 C x 300sq.mm (XLPE) | Rm |  |  | 0 |  |  | 0 | 0 | 0
2.1.1b | End Termination | No |  |  | 0 |  |  | 0 | 0 | 0
2.1.2a | 3.5 C x 185 sq.mm (XLPE) | Rm |  |  | 0 |  |  | 0 | 0 | 0
2.1.2b | End Termination | No |  |  | 0 |  |  | 0 | 0 | 0
2.1.3a | 3.5 C x 35 sq.mm (XLPE) | Rm |  |  | 0 |  |  | 0 | 0 | 0
2.1.3b | End Termination | No |  |  | 0 |  |  | 0 | 0 | 0
2.2 | XLPE/ PVC Insulated & Steel Armoured Aluminium Conductor cables
2.2.1a | 4C X 25 sq.mm (XLPE) | Rm |  |  | 0 |  |  | 0 | 0 | 0
2.2.1b | End Termination | No |  |  | 0 |  |  | 0 | 0 | 0
2.2.2a | 4C X 16 sq.mm (XLPE) | Rm |  |  | 0 |  |  | 0 | 0 | 0
2.2.2b | End Termination | No |  |  | 0 |  |  | 0 | 0 | 0
2.2.3a | 4C X 10 sq.mm (XLPE) | Rm | 170 | 170 | 340 | 195 | 42 | 66300 | 14280 | 80580
2.2.3b | End Termination | No | 4 | 4 | 8 | 95 | 32 | 760 | 256 | 1016
2.2.4a | 4C X 6 sq.mm (XLPE) | Rm |  |  | 0 |  |  | 0 | 0 | 0
2.2.4b | End Termination | No |  |  | 0 |  |  | 0 | 0 | 0
0
2.2.5a | 4C X 4 sq.mm (pvc) | Rm | 180 | 180 | 360 | 112 | 32 | 40320 | 11520 | 51840
2.2.5b | End Termination | No | 4 | 4 | 8 | 74 | 21 | 592 | 168 | 760
2.3 | XLPE / PVC Insulated & Steel Armoured Copper Conductor cables (2XFY Type)
2.3.1a | 4C X 25 sq.mm (XLPE) | Rm |  |  | 0 |  |  | 0 | 0 | 0
2.3.1b | End Termination | No |  |  | 0 |  |  | 0 | 0 | 0
0
2.3.2a | 4C X 16 sq.mm (XLPE) | Rm |  |  | 0 |  |  | 0 | 0 | 0
2.3.2b | End Termination | No |  |  | 0 |  |  | 0 | 0 | 0
2.3.3a | 3C X 10 sq.mm (PVC) | Rm |  |  | 0 |  |  | 0 | 0 | 0
2.3.3b | End Termination | No |  |  | 0 |  |  | 0 | 0 | 0
2.4 | PVC insulated, sheathed, unarmoured, flexible copper conductor cables - single Core | [8 empty] | 0
2.4.1a | 1 C x 95 sq.mm | Rm |  |  | 0 |  |  | 0 | 0 | 0
2.4.1b | End Termination | No |  |  | 0 |  |  | 0 | 0 | 0
2.4.2a | 1 C x 25 sq.mm | Rm |  |  | 0 |  |  | 0 | 0 | 0
2.4.2b | End Termination | No |  |  | 0 |  |  | 0 | 0 | 0
2.4.3a | 1 C x 16 sq.mm | Rm |  |  | 0 |  |  | 0 | 0 | 0
2.4.3b | End Termination | No |  |  | 0 |  |  | 0 | 0 | 0
2.4.4a | 1 C x 10 sq.mm | Rm | 100 | 100 | 200 | 221 | 32 | 44200 | 6400 | 50600
2.4.4b | End Termination | No | 4 | 4 | 8 | 84 | 21 | 672 | 168 | 840
2.4.5a | 1 C x 4 sq.mm | Rm | 100 | 100 | 200 | 84 | 21 | 16800 | 4200 | 21000
2.4.5b | End Termination | No | 4 | 4 | 8 | 74 | 21 | 592 | 168 | 760
| TOTAL PART -2 | [6 empty] | 170236 | 37160 | 207396
3 | MCB DISTRIBUTION BOARDS (DB)
Supply, Installation, Testing and Commissioning of MCB Distribution board as per approved installation dwgs.
Wall mounted MCB DBs with MS wire way box on top / bottom & on sides. MCBs shall be rated for 10kA with current limiting feature. Dummy ways to be covered with blank plates. All out going ways shall be labelled & laminated.
Enclosure:1.6mm CRCA Sheet Steel, Powder Coated
Door : Single Door, with fixing on both sides
Protection : IP 42
Cable Entry : Top & Bottom
Bus bar : Shall be tinned Copper and 200% rating for UPS DB Neutral Link
MCB's : 10kA 'C' Curve for Lighting & Raw power, 10kA 'D' Curve for UPS Distribution
Note:
1) Separate Earth bus/Neutral bus for each phase
2) Each Circuit shall have yellow ferrules with circuit number.
3) Accessories required for installation of DB's on Wall/Column/Gyp Board shall be considered
4) DB's shall be covered with powder coated (paint should match with DB Color) wire ways all around and up to ceiling to receive incoming circuits, how ever raceway shall be considered as a separate items
5) Laminated A3 OR A4 size SLD copy shall be pasted inside DB door
6) Safe shroud for Neutral link shall be provided
7) For all the DB details refer respective floor drawing, DB schematic
3.1 | LDB's :
3.1.1 | 4Tier 40 Module TPN DB - Lighting DB
Incomer : 1No. 40A, 4P, MCB of 'C' Curve
Phase Isolator : 3Nos, 40A, DP, RCCB of 30mA
| Outgoing : 24 Nos. 10A SP MCB of 'C' curve | No. |  |  | 0 |  |  | 0 | 0 | 0
3.1.2 | 16 Way SPN DB - Emergency Lighting DB
Incomer : 1No. of 32A, DP, MCB
| Outgoing : 14 Nos. of 6A, SP, 'C' curve MCB | No. |  |  | 0 |  |  | 0 | 0 | 0
3.1.3 | 12 Way SPN DB - Emergency Lighting DB
Incomer : 1No. of 32A, DP, MCB
| Outgoing : 10 Nos. of 6A, SP, 'C' curve MCB | No. |  |  | 0 |  |  | 0 | 0 | 0
3.1.4 | 12 Way SPN DB - Emergency Lighting Output DB
Incomer : 1No. of 40A, DP, MCB
| Outgoing : 5 Nos. of 32A, DP, 'C' curve MCB | No. |  |  | 0 |  |  | 0 | 0 | 0
3.2 | RDB's :
3.2.1 | 4Tier 40 Module TPN DB
Incomer : 1No. of 63A, 4P, 'C' Curve MCB
Phase Isolator : 3Nos. of 40A, DP, RCCB 300mA
| Outgoing : 24 Nos. of 16A, SP, 'C' curve MCB | No. |  |  | 0 |  |  | 0 | 0 | 0
3.2.2 | 4Tier 56 Module TPN DB
Incomer : 1No. of 63A, 4P, 'C' Curve MCB
Phase Isolator : 3Nos. of 40A, DP, RCCB 300mA
| Outgoing : 36 Nos. of 16A, SP, 'C' curve MCB | No. |  |  | 0 |  |  | 0 | 0 | 0
3.3 | UDB's :
3.3.1 | 4Tier 56 Module TPN DB
Incomer : 1No. of 63A, 4P, 'D' Curve MCB
Phase Isolator : 3Nos. of 40A, DP, SI Type RCCB 100mA
| Outgoing : 36 Nos. of 16A, SP, 'D' curve MCB | No. |  |  | 0 |  |  | 0 | 0 | 0
3.3.2 | 4Tier 40 Module TPN DB
Incomer : 1No. of 63A, 4P, 'D' Curve MCB
Phase Isolator : 3Nos. of 40A, DP, SI Type RCCB 100mA
| Outgoing : 24 Nos. of 16A, SP, 'D' curve MCB | No. |  |  | 0 |  |  | 0 | 0 | 0
3.4 | Server Room UDB's :
3.4.1 | 8 WAY TPN DB
Incomer : 1No. of 63A, 4P, 'D' Curve MCB
Phase Isolator : 3Nos. of 40A, DP, 'D' curve MCB
| Outgoing : 9Nos. of 32A, DP, 'D' curve MCB | No. |  |  | 0 |  |  | 0 | 0 | 0
3.5 | HVAC DB's :
3.5.1 | 8Way VTPN DB
Incomer : 1 No. 63A FP,MCCB
Outgoing : 2 No. 20A TP, MCB of 'C' curve along with CT & MFM
Outgoing : 1 No. 40A TP, MCB of 'C' curve
Outgoing : 1 No. 20A TP, MCB of 'C' curve
Outgoing : 1 No. 16A TP, MCB of 'C' curve
| Outgoing : 9 No. 16A TP, MCB of 'C' curve | No. |  |  | 0 |  |  | 0 | 0 | 0
3.5.2 | 8Way VTPN DB
Incomer : 1 No. 80A FP,MCCB
Outgoing : 3 No. 40A TP, MCB of 'C' curve along with CT & MFM
Outgoing : 1 No. 40A TP, MCB of 'C' curve
Outgoing : 2 No. 16A TP, MCB of 'C' curve
| Outgoing : 6 No. 16A SP, MCB of 'C' curve | No. |  |  | 0 |  |  | 0 | 0 | 0
| TOTAL PART -3 | [6 empty] | 0 | 0 | 0
4 | CIRCUIT / SUB MAINS:
Circuit mains using 1.1kV grade PVC insulated copper conductor (MSCC) wires / PVC insulated PVC sheathed three core cables drawn in MS conduit or in existing raceway. For Lighting Rates quoted shall include supply of conduits, wires, Switches & other conduiting accessories. Circuit mains shall be measured from respective DB to the last point, looping from switch / socket to another switch /socket board will not be paid seperatelly. For RP & UPS points Rates quoted shall include supply of conduits & cables, Circuit mains shall be measured from respective DB to the last point, looping from switch / Socket to another switch / socket board will not be paid seperatelly. All circuit terminations shall be provided with solder less crimping type copper sockets / lugs, ferrules indicating source code on load side & load code on source side. There shall not be any joints in the circuits, only looping is allowed in terminal blocks & in switches / socket outlets.
NOTE:
1) Conduits running above false ceiling in multiples shall be supported by Slotted GI 'C' channel at distance not more than 0.5mtrs intervals. OR else with spacers & saddles at an intervals of 0.5mtrs
2) Accessories shall includes Bends, Collars, junction boxes, Spacers, saddles, screws, Flexibles
3) Conduits shall be ISI marked
4) The number of wires drawn in each conduit shall be as per IS 694 code.
5) No different phases shall be drawn in same conduit
6) Conduit joints shall be done with threading proper accessories only
4.01 | 3C x 2.5 sq.mm cable with PVC-FRLS insulated outer sheath & multi strand copper conductors, unarmoured, cable to be laid in 20mm Dia 1.6mm thick MS Conduit (Lighting Circuits) | Rm | 380 | 380 | 760 | 205 | 42 | 155800 | 31920 | 187720
4.02 | 3C x 6 sq.mm cable with PVC-FRLS insulated outer sheath & multi strand copper conductors, unarmoured, cable to be laid in raceways / conduits (cost of raceways/conduits to exclude) for IT Racks | Rm |  |  | 0 |  |  | 0 | 0 | 0
4.03 | 3C x 4 sq.mm cable with PVC-FRLS insulated outer sheath & multi strand copper conductors, unarmoured, cable to be laid in raceways, modular partitions, conduits (Cost of Raceways & Conduit to exclude) for Raw Power upto First Point | Rm |  |  | 0 |  |  | 0 | 0 | 0
4.04 | 3C x 2.5 sq.mm cable with PVC-FRLS insulated outer sheath & multi strand copper conductors, unarmoured, cable to be laid in raceways, modular partitions, conduits (Cost of Raceways & Conduit to exclude) for Raw Power,UPS Circuit & VAV - Circuit main & Looping | Rm | 400 | 450 | 850 | 168 | 32 | 142800 | 27200 | 170000
| TOTAL PART -4 | [6 empty] | 298600 | 59120 | 357720
5 | POWER RECEPTACLES.
Supply, Installation, Testing and Commissioning of the following Modular/Industrial Switch, sockets with modular front plate, and accessories as per the site conditions.
The quoted rate for power socket outlets shall include a. Socket outlets - round / round cum flat / flat multi pin socket outlets b.Switches c. 14SWG metal boxes with knockout on all sides d. Front plate of required colours with accessories
Industrial type sockets shall be of Metal clad / Polycarbonate body with plug top. All switch / sockets shall be provided with printed labels / stickers indicating source code. Colour code for UPS socket plates : White/ as per architect. Colour code for RP socket plates : Black/Grey/ as per architect. All switch / sockets including front plate & frame which will be mounted on the metal boxes shall have removable film coat to protect from scraches & paint during installation.
Note: Safety shutters to prevent accidental contact with live parts shall be provided. No indicator shall be provided for switches
a. All switches and sockets are modular type which shall be made of fire retardant; selfextinguish polycarbonate plastic, able to withstand the glow wire test ai 960 deg. C. b. The switches shall confirm IS 3854 :1997, The internal design of terminals and contact shall make the switch capable of high overload conditions, the switch shall be of flush type with silver inlay contact on pure copper. c. Socket outlets shall be of the three pins. All sockets shall fully comply with IS 1293: 2005 specifications. All wiring accessories shall be BIS approved.
5.1 | Modular : Round multipin type Without Box
5.1.1 | 6A 3/5pinsocket controlled by 6A switch, excluding box (For Raw power) | No. |  |  | 0 |  |  | 0 | 0 | 0
5.1.2 | 2 x 6A 3/5pinsocket controlled by 16A switch, excluding box (For UPS) | No. |  | 6 | 6 | 672 | 137 | 4032 | 822 | 4854
5.1.3 | 2x 6A 3/5pin socket controlled by 16A switch, excluding box (For - Raw) | No. |  |  | 0 |  |  | 0 | 0 | 0
5.1.4 | 3 x 6A 3/5pinsocket controlled by 16A switch , excluding box (For UPS power) | No. |  |  | 0 |  |  | 0 | 0 | 0
5.1.5 | 1 no. 6/16A socket controlled by 16A switch, excluding box. (For UPS Power) | No. |  |  | 0 |  |  | 0 | 0 | 0
5.1.6 | 1 no. 6/16A socket controlled by 16A switch, excluding box. (For Raw Power) | No. |  |  | 0 |  |  | 0 | 0 | 0
5.1.7 | 1 no. 6A socket outlet without switch excluding box. (For UPS Power) | No. |  |  | 0 |  |  | 0 | 0 | 0
Modular : Round multipin type With Box
5.1.8 | 1 no. 6A 3/5pin socket controlled by 6A SP switch, Including Box (UPS power - For Fire Damper +Security room+cctv etc) | No. | 5 | 5 | 10 | 294 | 63 | 2940 | 630 | 3570
5.1.9 | 1 x 6A 3/5pin socket controlled by 6A switch, Including box (For UPS power) | No. |  |  | 0 |  |  | 0 | 0 | 0
5.1.10 | 2 x 6A 3/5pin socket controlled by 16A switch, Including box (For UPS power - For Meeting Rooms & Collab) | No. |  |  | 0 |  |  | 0 | 0 | 0
5.1.11 | 3 x 6A 3/5pinsocket controlled by 16A switch, Including box (For UPS power - For TV's) | No. |  |  | 0 |  |  | 0 | 0 | 0
5.1.12 | 1 no. 6/16A socket controlled by 16A switch, Including box. (For HVAC Power) | No. | 10 | 12 | 22 | 431 | 95 | 9482 | 2090 | 11572
5.1.13 | 1 no. 6/16A socket controlled by 16A switch, Including box. (For Raw Power - For Maintenance Purpose, Repro,Workstation ,cabin & Pantry) | No. | 11 | 11 | 22 | 431 | 95 | 9482 | 2090 | 11572
5.1.14 | 1 no. 6/16A socket controlled by 16A switch, Including box. (For UPS Power) | No. |  |  | 0 |  |  | 0 | 0 | 0
5.1.15 | Readymade floor mounted Junction box - To locate 1 Set of 2 x 6A socket + 1no of 16A Switch and 4 Data outlets Similar to FrazerTechno make - 12 Module Cost need to include power outlets + Data outlets |  |  |  | 0 |  |  | 0 | 0 | 0
5.1.15 | Readymade floor mounted Junction box - To locate 1 Set of 4 x 6A socket + 1no of 16A Switch and 4 Data outlets Similar to FrazerTechno make - 12 Module Cost need to include power outlets + Data outlets | No. |  |  | 0 |  |  | 0 | 0 | 0
5.2 | SERVER/HUB Room Rack Sockets - With Box
5.2.1 | 1No. 16A 3 pin 1phase Interlocked type socket with plug top controlled by 16A DP MCB | No. |  |  | 0 |  |  | 0 | 0 | 0
5.2.2 | 1No. 32A 3 pin 1phase Interlocked Industrial type socket with plug top controlled by 32A DP MCB | No. |  |  | 0 |  |  | 0 | 0 | 0
5.2.3 | 1No. 32A 5 pin 3phase interlocked Industrial type socket with plug top controlled by 32A 4P MCB | No. |  |  | 0 |  |  | 0 | 0 | 0
5.3 | Industrial Sockets (IP 67)
5.3.1 | 16A 3pin 1phase Industrial socket with plug top controlled by 16A DP MCB | No. |  |  | 0 |  |  | 0 | 0 | 0
5.3.2 | 32A 3pin 1phase Industrial socket with plug top controlled by 32A DP MCB | No. |  |  | 0 |  |  | 0 | 0 | 0
5.3.3 | 16A 5pin 3phase Industrial socket with plug top controlled by 16A TPN MCB - Rawpower | No. |  |  | 0 |  |  | 0 | 0 | 0
5.3.3 | 32A 5pin 3phase Industrial socket with plug top controlled by 32A TPN MCB - Rawpower | No. |  |  | 0 |  |  | 0 | 0 | 0
5.4 | Data Backbox
5.4.1 | 2 Module GI back box for data,TV, HDMI outlets in partitions | No. |  |  | 0 |  |  | 0 | 0 | 0
5.5 | Removal of sockets in phone booths & discussion booths | Ls |  |  | 1 |  |  | 0 | 0 | 0 | *Details Required
| TOTAL PART -5 | [6 empty] | 25936 | 5632 | 31568
6 | POINT WIRING
LIGHT POINTS
Supply, installation, testing & commissioning of light points using 1100V, 3Rx1.5Sqmm FRLS multi-strand copper conductor wire in 20mm Dia 1.6mm thick MS Conduit, ISI marked & specified type switches, metal boxes and accessories. The point wiring shall be terminated in a terminal block inside the junction box. Point wiring shall commence from the control box to light points. The quoted rate shall be inclusive of conduits with bush adapter for light fixture connection wherever required. All switches & accessories shall be covered with removable film coat to protect from scratches and paint.
A | Switch control
6.01 | One (1) light point controlled by a 6A modular type switch | No. |  |  | 0 |  |  | 0 | 0 | 0
6.02 | Two (2) light points controlled by one(1) 10A modular type switch. | No. | 3 | 1 | 4 | 2258 | 452 | 9032 | 1808 | 10840
6.03 | Three (3) light points controlled by one(1) 10A modular type switch. | No. | 3 | 3 | 6 | 2741 | 557 | 16446 | 3342 | 19788
6.04 | Four (4) light points controlled by one(1) 16A modular type switch. | No. | 2 | 3 | 5 | 3213 | 651 | 16065 | 3255 | 19320
6.05 | Five (5) light points controlled by one(1) 16A modular type switch. | No. | 1 |  | 1 | 3696 | 746 | 3696 | 746 | 4442
6.06 | Six (6) light points controlled by one(1) 16A modular type switch. | No. |  | 1 | 1 | 4169 | 840 | 4169 | 840 | 5009
6.07 | Seven (7) light points controlled by one(1) 16A modular type switch. | No. |  |  | 0 |  |  | 0 | 0 | 0
6.08 | Eight (8) light points controlled by one(1) 16A modular type switch. | No. |  |  | 0 |  |  | 0 | 0 | 0
6.09 | Nine (9) light points controlled by one(1) 16A modular type switch. | No. |  |  | 0 |  |  | 0 | 0 | 0
6.1 | Ten (10) light points controlled by one(1) 16A modular type switch. | No. |  |  | 0 |  |  | 0 | 0 | 0
6.11 | Eleven(11) light points controlled by one(1) 16A modular type switch. | No. |  |  | 0 |  |  | 0 | 0 | 0
6.12 | Twelve(12) light points controlled by one(1) 16A modular type switch. | No. |  |  | 0 |  |  | 0 | 0 | 0
B | Sensor control |  |  |  | 0
6.13 | Single light point controlled by Occupancy Sensor | No. |  |  | 0 |  |  | 0 | 0 | 0
6.14 | Two light points controlled by Occupancy Sensor | No. |  |  | 0 |  |  | 0 | 0 | 0
6.15 | Three light points controlled by Occupancy Sensor | No. |  |  | 0 |  |  | 0 | 0 | 0
6.16 | Four light points controlled by Occupancy Sensor | No. |  |  | 0 |  |  | 0 | 0 | 0
6.17 | Five light points controlled by Occupancy Sensor | No. |  |  | 0 |  |  | 0 | 0 | 0
6.18 | Six light points controlled by Occupancy Sensor | No. |  |  | 0 |  |  | 0 | 0 | 0
6.19 | Seven light points controlled by Occupancy Sensor | No. |  |  | 0 |  |  | 0 | 0 | 0
6.2 | Eight light points controlled by Occupancy Sensor | No. |  |  | 0 |  |  | 0 | 0 | 0
6.21 | Nine light points controlled by Occupancy Sensor | No. |  |  | 0 |  |  | 0 | 0 | 0
6.22 | Ten light points controlled by Occupancy Sensor | No. |  |  | 0 |  |  | 0 | 0 | 0
6.23 | Eleven light points controlled by Occupancy Sensor | No. |  |  | 0 |  |  | 0 | 0 | 0
6.24 | Twelve light points controlled by Occupancy Sensor | No. |  |  | 0 |  |  | 0 | 0 | 0
c | Sensor + Switch control |  |  |  | 0 |  |  | 0 | 0 | 0
6.25 | Single light point controlled by Occupancy Sensor + Switch | No. |  |  | 0 |  |  | 0 | 0 | 0
6.26 | Two light points controlled by Occupancy Sensor + Switch | No. |  |  | 0 |  |  | 0 | 0 | 0
6.27 | Three light points controlled by Occupancy Sensor + Switch | No. |  |  | 0 |  |  | 0 | 0 | 0
6.28 | 'Four light points controlled by Occupancy Sensor + Switch | No. |  |  | 0 |  |  | 0 | 0 | 0
6.29 | Five light points controlled by Occupancy Sensor + Switch | No. |  |  | 0 |  |  | 0 | 0 | 0
6.3 | Six light points controlled by Occupancy Sensor + Switch | No. |  |  | 0 |  |  | 0 | 0 | 0
6.31 | Seven light points controlled by Occupancy Sensor + Switch | No. |  |  | 0 |  |  | 0 | 0 | 0
6.32 | Eight light points controlled by Occupancy Sensor + Switch | No. |  |  | 0 |  |  | 0 | 0 | 0
6.33 | Nine light points controlled by Occupancy Sensor + Switch | No. |  |  | 0 |  |  | 0 | 0 | 0
6.34 | Ten light points controlled by Occupancy Sensor + Switch | No. |  |  | 0 |  |  | 0 | 0 | 0
6.35 | Eleven light points controlled by Occupancy Sensor + Switch | No. |  |  | 0 |  |  | 0 | 0 | 0
6.36 | Twelve light points controlled by Occupancy Sensor + Switch | No. |  |  | 0 |  |  | 0 | 0 | 0
D | MCB control
Supply, installation, testing & commissioning of light points using 1100V, 3Rx1.5Sqmm FRLS multi-strand copper conductor wire in 20mm Dia 1.6mm thick MS Conduit, ISI marked. The cost for MCB & wiring from DB to first light point shall not be included.
6.37 | Five light points controlled by MCB (Excluding MCB) | No. |  |  | 0 |  |  | 0 | 0 | 0
6.38 | Six light points controlled by MCB (Excluding MCB) | No. |  |  | 0
6.39 | Seven light points controlled by MCB (Excluding MCB) | No. |  |  | 0 |  |  | 0 | 0 | 0
6.4 | Eight light points controlled by MCB (Excluding MCB) | No. |  |  | 0 |  |  | 0 | 0 | 0
6.41 | Nine light points controlled by MCB (Excluding MCB) | No. |  |  | 0 |  |  | 0 | 0 | 0
6.42 | Ten light points controlled by MCB (Excluding MCB) | No. |  |  | 0 |  |  | 0 | 0 | 0
6.43 | Eleven light points controlled by MCB (Excluding MCB) | No. |  |  | 0 |  |  | 0 | 0 | 0
6.44 | Twelve light points controlled by MCB (Excluding MCB) | No. |  |  | 0 |  |  | 0 | 0 | 0
| TOTAL PART - 6 | [6 empty] | 49408 | 9991 | 59399
7 | CABLE TRAYS
Slotted angle Hot Dip Galvanized - GI (65 - 70 Micron as per IS2629) ready made cable trays of 14SWG. Quoted rates for installation shall include necessary anchor fasteners / 'L' angle supports @ 1200mm interval & all accessories, etc., to suit site conditions. Tray shall be made out of 2mm thick sheet, standard length 2.5mtr GI coupler plate 2.5 mm thick with eight holes and 8 nos. 1 1/2' x 3/8 GI passivated nut bolts with 2 no's plain washers & GI clamp for tray fixing along with GI hardware.
7.1 | Ladder type cable tray
7.1.1 | 750 x 75mm Size | M | [5 empty] | 0 | 0 | 0
7.1.2 | 600 x 50mm Size | M |  |  | 0 |  |  | 0 | 0 | 0
7.1.3 | 450 x 50mm Size | M
7.1.4 | 300 x 50mm Size | M | [5 empty] | 0 | 0 | 0
7.1.5 | 200 x 50mm Size | M | [5 empty] | 0 | 0 | 0
7.1.6 | 150 x 50mm Size | M | [5 empty] | 0 | 0 | 0
7.1.7 | 100 x 50mm Size | M | [5 empty] | 0 | 0 | 0
7.2 | Perforated Type Cable tray with cover (For LT Cables & Communication Cables)
Supply, installation, testing & commissioning of 2 mm Powder quoted Galvanized - GI (65 - 70 Micron as per IS2629) perforated type cable tray complete with all necessary coupler plates, elbows, tees, bends, reducers, stiffeners, grip/Anchor bolts or fasteners and other accessories and hardware need to be considered. Also the Quoted rate shall be inclusive of all hardware i.e. bolts, nuts, screws. washers, etc. Tray shall be made out of 2mm thick sheet, standard length 2.5mtr GI coupler plate 2.5 mm thick with eight holes and 8 nos. 1 1/2' x 3/8 GI passivated nut bolts with 2 no's plain washers & GI clamp for tray fixing along with GI hardware.
1.The quoted rate for the cable tray size up to 450mm shall be inclusive of suitable size threaded rod with suitable "C" channel at every 1000 mm interval of supports.
2.The quoted rate for above 450mm cable tray shall be with 25X25X5 mm thick MS angles at every 1000 mm interval of support.
3.Colour of the tray should be as per Interior views / Finalised by Architects during GFC stage
7.2.1 | 1000 x 75mm Size | M |  |  | 0 |  |  | 0 | 0 | 0
7.2.2 | 750 x 75mm Size | M |  |  | 0 |  |  | 0 | 0 | 0
7.2.3 | 600 x 50mm Size | M |  |  | 0 |  |  | 0 | 0 | 0
7.2.4 | 450 x 50mm Size | M |  |  | 0 |  |  | 0 | 0 | 0
7.2.5 | 300 x 50mm Size | M |  |  | 0 |  |  | 0 | 0 | 0
7.2.6 | 200 x 50mm Size | M |  |  | 0 |  |  | 0 | 0 | 0
7.2.7 | 150 x 50mm Size | M |  |  | 0 |  |  | 0 | 0 | 0
7.2.8 | 100 x 50mm Size | M | 160 | 150 | 310 | 483 | 95 | 149730 | 29450 | 179180
7.2.9 | 80 x 50mm Size | M |  |  | 0 |  |  | 0 | 0 | 0
7.3 | SolidType with Cover (For Lighting Cables) | [8 empty] | 0
Supply, installation, testing & commissioning of 2 mm Powder quoted Galvanized - GI(65 - 70 Micron as per IS2629) Solid type cable tray complete with all necessary coupler plates, elbows, tees, bends, reducers, stiffeners, grip/Anchor bolts or fasteners and other accessories and hardware need to be considered. Also the Quoted rate shall be inclusive of all hardware i.e. bolts, nuts, screws. washers, etc. Tray shall be made out of 2mm thick sheet, standard length 2.5mtr GI coupler plate 2.5 mm thick with eight holes and 8 nos. 1 1/2' x 3/8 GI passivated nut bolts with 2 no's plain washers & GI clamp for tray fixing along with GI hardware.
1.The quoted rate for the cable tray size up to 450mm shall be inclusive of suitable size threaded rod with suitable "C" channel at every 1000 mm interval of supports.
2.The quoted rate for above 450mm cable tray shall be with 25X25X5 mm thick MS angles at every 1000 mm interval of support.
3.Colour of the tray should be as per Interior views / Finalised by Architects during GFC stage
7.3.1 | 300 x 40mm Size | M |  |  | 0 |  |  | 0 | 0 | 0
7.3.2 | 200 x 40mm Size | M |  |  | 0 |  |  | 0 | 0 | 0
7.3.3 | 150 x 40mm Size | M |  |  | 0 |  |  | 0 | 0 | 0
7.3.4 | 50 x 50mm Size | M |  |  | 0 |  |  | 0 | 0 | 0
7.4 | Basket Tray (For SERVER Room - Network cables)
Providing and Fixing of Cabloffill wire mesh cable tray system made out of Electrozinc Steel Wire Cable trays [As per ISO-20-81/82, NF/EN-12-329, DIN 50961] and bent into final shape , All cable trays, shall be manufactured with a longitudinal ‘T-welded’ safety edge and Trays shall be constructed with a 50 mm x 100 mm mesh configuration complete with couplers, C mountings and all accessories as required.
Note: The rate shall include all necessary supporting structure using appropriate L angles/ Channels etc for the tray size.
7.4.1 | 300 mm wide x 100 mm depth x 4 mm dia Cablofil | M |  |  | 0 |  |  | 0 | 0 | 0
7.4.2 | 400 mm wide x 100 mm depth x 4 mm dia Cablofil | M |  |  | 0 |  |  | 0 | 0 | 0
7.4.3 | 500 mm wide x 100 mm depth x 4 mm dia Cablofil | M |  |  | 0 |  |  | 0 | 0 | 0
| TOTAL PART - 7 | [6 empty] | 149730 | 29450 | 179180
8 | RACEWAYS
Supply & Installation of following size Pregalvanized - GI raceway / wire way with cover, made out of 16 SWG for body and 14 SWG for cover. Junction boxes to be provided with enough supports inside the box. Raceway installed above false ceiling/floor shall include necessary mounting supports, junction boxes and accessories to fix it firmly to the ground/ ceiling. The raceways shall be fixed to the floor with GI/MS (25mm x 3mm) strips so that there is no movement of the channels when civil work (pouring of cement concrete) is being done. Rate includes necessary floor cutting and chipping with machine of minimum 50mm depth, removal of debris out of site and neatly finished with M15 grade concrete up to the finished floor level. Race ways to be covered with Chicken mesh before concreting. Curing compound to be applied after initial setting of the concrete. All edges, cut faces shall be free of burrs & shall be smooth. The channels shall be earthed at the boxes and at the joints with 14 SWG bare copper wire with screws so that earth is continuous. Jointing of the race ways to be done with welding.
8.1 | Junction boxes
8.1.1 | Junction Boxes - Power
8.1.1a | 410 x 410 x 50mm Size | No. |  |  | 0 |  |  | 0 | 0 | 0
8.1.1b | 310 x 310 x 50mm Size | No. |  |  | 0 |  |  | 0 | 0 | 0
8.1.1c | 260 x 260 x 50mm Size | No. |  |  | 0 |  |  | 0 | 0 | 0
8.1.1d | 210 x 210 x 50mm Size | No. |  |  | 0 |  |  | 0 | 0 | 0
8.1.1e | 160 x 160 x 50mm Size | No. |  |  | 0 |  |  | 0 | 0 | 0
8.1.1f | 110 x 110 x 50mm Size | No. |  |  | 0 |  |  | 0 | 0 | 0
8.1.1g | 90 x 90 x 50mm Size | No. |  |  | 0 |  |  | 0 | 0 | 0
8.1.2 | Junction Boxes - Network
8.1.2a | 460 x 460 x 50mm Size | No. |  |  | 0 |  |  | 0 | 0 | 0
8.1.2b | 410 x 410 x 50mm Size | No. |  |  | 0 |  |  | 0 | 0 | 0
8.1.2c | 310 x 310 x 50mm Size | No. |  |  | 0 |  |  | 0 | 0 | 0
8.1.2d | 260 x 260 x 50mm Size | No. |  |  | 0 |  |  | 0 | 0 | 0
8.1.2e | 210 x 210 x 50mm Size | No. |  |  | 0 |  |  | 0 | 0 | 0
8.1.2f | 160 x 160 x 50mm Size | No. |  |  | 0 |  |  | 0 | 0 | 0
8.1.2g | 110 x 110 x 50mm Size | No. |  |  | 0 |  |  | 0 | 0 | 0
8.1.2h | 90 x 90 x 50mm Size | No. |  |  | 0 |  |  | 0 | 0 | 0
8.2 | Floor Raceways
Supply & Installation of following size Tubular Pre galvanised raceway , made out of 16 SWG GI.
8.2.1 | Floor Raceways - Power
8.2.1a | 300 x 40mm Size | M |  |  | 0 |  |  | 0 | 0 | 0
8.2.1b | 250 x 40mm Size | M |  |  | 0 |  |  | 0 | 0 | 0
8.2.1c | 200 x 40mm Size | M |  |  | 0 |  |  | 0 | 0 | 0
8.2.1d | 150 x 40mm Size | M |  |  | 0 |  |  | 0 | 0 | 0
8.2.1e | 100 x 40mm Size | M |  |  | 0 |  |  | 0 | 0 | 0
8.2.1f | 80 x 40mm Size | M |  |  | 0 |  |  | 0 | 0 | 0
8.2.2 | Floor Raceways - Network
8.2.2a | 450 x 40mm Size | M |  |  | 0 |  |  | 0 | 0 | 0
8.2.2b | 400 x 40mm Size | M |  |  | 0 |  |  | 0 | 0 | 0
8.2.2c | 300 x 40mm Size | M |  |  | 0 |  |  | 0 | 0 | 0
8.2.2d | 250 x 40mm Size | M |  |  | 0 |  |  | 0 | 0 | 0
8.2.2e | 200 x 40mm Size | M |  |  | 0 |  |  | 0 | 0 | 0
8.2.2f | 150 x 40mm Size | M |  |  | 0 |  |  | 0 | 0 | 0
8.2.2g | 100 x 40mm Size | M |  |  | 0 |  |  | 0 | 0 | 0
8.2.2h | 80 x 40mm Size | M |  |  | 0 |  |  | 0 | 0 | 0
8.2.2i | PVC trunk-100 x 50mm - similar to MK make | M |  |  | 0 |  |  | 0 | 0 | 0
8.3 | Ceiling Raceways
Supply & Installation of following size Powder Quoted Galvanized - GI (65 - 70 Micron as per IS2629) raceway / wire way with cover, made out of 14 SWG GI for body and 14 SWG GI for cover. Junction boxes to be provided with enough supports inside the box. Raceway installed above false ceiling shall include necessary mounting supports, junction boxes and accessories to fix it firmly to the ceiling. All edges, cut faces shall be free of burrs & shall be smooth. The channels shall be earthed at the boxes and at the joints with 14 SWG bare copper wire with screws so that earth is continuous. Jointing of the race ways to be done using fisher plates & 'Slotted Channel' angle supports @ 600mm interval etc., to suit site conditions.
Colour of the tray should be as per Interior views / Finalised by Architects during GFC stage
Junction boxes
Supply & Installation of following size junction boxes, made out of 14 SWG Powder quoted Galvanized - GI (65 - 70 Micron as per IS2629) for body and cover.
8.3.1 | Junction Boxes - Power
8.3.1a | 410 x 410 x 50mm Size | No. |  |  | 0 |  |  | 0 | 0 | 0
8.3.1b | 310 x 310 x 50mm Size | No. |  |  | 0 |  |  | 0 | 0 | 0
8.3.1c | 260 x 260 x 50mm Size | No. |  |  | 0 |  |  | 0 | 0 | 0
8.3.1d | 210 x 210 x 50mm Size | No. |  |  | 0 |  |  | 0 | 0 | 0
8.3.1e | 160 x 160 x 50mm Size | No. |  |  | 0 |  |  | 0 | 0 | 0
8.3.1f | 110 x 110 x 50mm Size | No. |  |  | 0 |  |  | 0 | 0 | 0
8.3.1g | 90 x 90 x 50mm Size | No. |  |  | 0 |  |  | 0 | 0 | 0
8.3.2 | Junction Boxes - Network
8.3.2a | 460 x 460 x 50mm Size | No. | [5 empty] | 0 | 0 | 0
8.3.2b | 410 x 410 x 50mm Size | No. |  |  | 0 |  |  | 0 | 0 | 0
8.3.2c | 310 x 310 x 50mm Size | No. |  |  | 0 |  |  | 0 | 0 | 0
8.3.2d | 260 x 260 x 50mm Size | No. |  |  | 0 |  |  | 0 | 0 | 0
8.3.2e | 210 x 210 x 50mm Size | No. |  |  | 0 |  |  | 0 | 0 | 0
8.3.2f | 160 x 160 x 50mm Size | No. |  |  | 0 |  |  | 0 | 0 | 0
8.3.2g | 110 x 110 x 50mm Size | No. |  |  | 0 |  |  | 0 | 0 | 0
8.3.2h | 90 x 90 x 50mm Size | No. |  |  | 0 |  |  | 0 | 0 | 0
8.4 | Ceiling Raceways - Power
8.4.1 | Supply & Installation of following size raceway, made out of 14 SWG Powder quoted - GI (65 - 70 Micron as per IS2629).
Colour of the tray should be as per Interior views / Finalised by Architects during GFC stage
8.4.1a | 400 x 40mm Size | M |  |  | 0 |  |  | 0 | 0 | 0
8.4.1b | 300 x 40mm Size | M |  |  | 0 |  |  | 0 | 0 | 0
8.4.1c | 250 x 40mm Size | M |  |  | 0 |  |  | 0 | 0 | 0
8.4.1d | 200 x 40mm Size | M |  |  | 0 |  |  | 0 | 0 | 0
8.4.1e | 150 x 40mm Size | M |  |  | 0
8.4.1f | 100 x 40mm Size | M |  |  | 0 |  |  | 0 | 0 | 0
8.4.1g | 80 x 40mm Size | M |  |  | 0 |  |  | 0 | 0 | 0
8.4.2 | Ceiling Raceways - Network
8.4.2a | 450 x 40mm Size | M |  |  | 0 |  |  | 0 | 0 | 0
8.4.2b | 400 x 40mm Size | M |  |  | 0 |  |  | 0 | 0 | 0
8.4.2c | 300 x 40mm Size | M |  |  | 0 |  |  | 0 | 0 | 0
8.4.2d | 250 x 40mm Size | M |  |  | 0 |  |  | 0 | 0 | 0
8.4.2e | 200 x 40mm Size | M |  |  | 0 |  |  | 0 | 0 | 0
8.4.2f | 150 x 40mm Size | M |  |  | 0 |  |  | 0 | 0 | 0
8.4.2g | 100 x 40mm Size | M |  |  | 0 |  |  | 0 | 0 | 0
8.4.2h | 80 x 40mm Size | M |  |  | 0 |  |  | 0 | 0 | 0
8.5 | Floor Raceways (For IT Rack)
8.5.1 | 600 x 100mm Size | M |  |  | 0 |  |  | 0 | 0 | 0
8.5.2 | 500 x 100mm Size | M |  |  | 0 |  |  | 0 | 0 | 0
8.5.3 | 300 x 100mm Size | M |  |  | 0 |  |  | 0 | 0 | 0
8.6 | Supply & Installation of following size Powder coated raceway made out of 16 SWG GI/MS for body and 14 SWG GI/MS for cover. - The shade shall be as per site approval Minimum 2 colours need to be considered in the Quote. Colour will be finalised as per IT team requirement.
Vendor need to take confirmation from Architect/Consultant team before procuring the above line iteam.
8.6.1 | 300 x 150mm Size | M |  |  | 0 |  |  | 0 | 0 | 0
8.6.2 | 150 x 150mm Size | M |  |  | 0 |  |  | 0 | 0 | 0
8.6.3 | 100 x 150mm Size | M |  |  | 0 |  |  | 0 | 0 | 0
8.7 | Raceways for AV
Supply & Installation of following size Hot Dip Galvanized - GI (65 - 70 Micron as per IS2629) raceway / wire way with cover, made out of 16 SWG GI for body and 14 SWG GI for cover. Junction boxes to be provided with enough supports inside the box. Raceway installed above false ceiling/floor shall include necessary mounting supports, junction boxes and accessories to fix it firmly to the ground/ ceiling. The raceways shall be fixed to the floor with GI strips so that there is no movement of the channels when civil work (pouring of cement concrete) is being done. All edges, cut faces shall be free of burrs & shall be smooth. The channels shall be earthed at the boxes and at the joints with 14 SWG bare copper wire with screws so that earth is continuous. Jointing of the race ways to be done with welding.
8.7.1 | 300 x 40mm Size | M |  |  | 0 |  |  | 0 | 0 | 0
8.7.2 | 100 x 40mm Size | M |  |  | 0 |  |  | 0 | 0 | 0
8.8 | Supply & Laying of following size ISI Marked MS conduits.Rate shall include wall chasing & rough plastering, clamping / fixing arrangement.
8.8.1 | 32mm dia - For Network | M |  |  | 0 |  |  | 0 | 0 | 0
8.8.2 | 25mm dia - For Power | M | 40 | 40 | 80 | 142 | 27 | 11360 | 2160 | 13520
8.8.3 | 20mm dia | M | 30 | 30 | 60 | 105 | 21 | 6300 | 1260 | 7560
8.8.4 | Flexble Conduit 25mm | M | 20 | 20 | 40 | 53 | 21 | 2120 | 840 | 2960
8.8.5 | Flexble Conduit 20mm | M | 25 | 25 | 50 | 42 | 21 | 2100 | 1050 | 3150
8.8.6 | 50 x 50 mm Casing & Caping | M |  |  | 0 |  |  | 0 | 0 | 0
8.8.7 | 40 mm width chipping and refilling to lay the conduit in floor | M |  |  | 0 |  |  | 0 | 0 | 0
| TOTAL PART -8 | [6 empty] | 21880 | 5310 | 27190
9 | EARTHING
9.1 | EARTH ELECTRODES
9.1.1 | GI Pipe Electrode Earthing System
| Pipe Earth Electrode using 38 mm dia class B GI pipe complete as per IS 3043 with salt, charcoal, brick masonary chamber with heavy duty RCC cover (suitable to take fire tender load) tender truckmovement) of 450mm x 450mm x 300mm chamber.(Earth strip to be left upto the Earthpit for Connection) | No. | [5 empty] | 0 | 0 | 0
9.1.2 | Copper plate Electrode Earthing System
| Plate Earth Electrode using 19 mm dia Class B copper plate of size 600 x 600 x 3 mm thick.with heavy duty RCC cover (suitable to take fire tender truck load) of 450mm x 450mm x 300mm chamber.(Earth strip to be left upto the Earthpit for Connection) | No. | [5 empty] | 0 | 0 | 0
9.1.3 | Maintenance Free Copper Pipe Electrode Earthing System
| Providing, installing, testing and commissioning of maintance free earthing station including the following items 1.400(L)x400(W)x450(D)mm, 150mm thick block work inspection chamber with CI Cover/ Lid. 2.25x 6 Cu Strips links for main connection of Pipe with external strips inside the chamber with exothermic welding. 3. 20mm dia Copper Pipe 4. 40Kg Chemical earth enhancing material System shall be in full compliance with IS:3043 Earthing Standards/ NBC 2016 (latest). 5. Cost to include necessary excavation to an extent of 400(W & L), back filling around the Rod/ Pipe. | No. |  |  | 0 |  |  | 0 | 0 | 0
9.2 | EARTH STRIPS
GI/Cu earth strips on cable tray or below ground as per site condition. All Cu. Strips shall be run in pvc heat shrinkable sleeve & mounted on insulation mounts. Cost of civil works shall be included for strips laid below ground.
9.2.1 | 6 Sq.mm Copper Wire | M |  |  | 0 |  |  | 0 | 0 | 0
9.2.2 | 4 Sq.mm Copper Wire | M |  |  | 0 |  |  | 0 | 0 | 0
9.2.3 | 25 x 3mm GI Earth flat | M |  |  | 0 |  |  | 0 | 0 | 0
9.2.4 | 25 x 6mm GI Earth flat | M |  |  | 0 |  |  | 0 | 0 | 0
9.2.5 | 25 x 10mm GI Earth flat | M |  |  | 0 |  |  | 0 | 0 | 0
9.2.6 | 50 x 6mm GI Earth flat | M |  |  | 0 |  |  | 0 | 0 | 0
9.2.7 | 50 x 10mm GI Earth flat | M |  |  | 0 |  |  | 0 | 0 | 0
9.2.8 | 25 x 3mm Cu Earth flat | M |  |  | 0 |  |  | 0 | 0 | 0
9.2.9 | 25 x 6mm Cu Earth flat | M |  |  | 0 |  |  | 0 | 0 | 0
9.3 | XLPE Insulated Copper Conductor Unarmoured Cables (2XY Type)
| 1.1kV grade, copper conductor, XLPE insulated, unarmoured, power cables. The cables shall be laid on tray / hume pipe /in ready made trenches, with nylon cable ties / MS Clamps @ 600mm interval etc., as required. Rate quoted shall exclude cost of tray. Cost of civil works like earth escavation & refilling shall be included for strips laid below ground. |  |  |  | 0
9.3.1a | 1 Core x 150 Sq. mm | M |  |  | 0 |  |  | 0 | 0 | 0
9.3.1b | End terminations | Nos |  |  | 0 |  |  | 0 | 0 | 0
9.3.1a | 1 Core x 70 Sq. mm | M |  |  | 0
9.3.1b | End terminations | Nos |  |  | 0
9.3.1a | 1 Core x 50 Sq. mm | M |  |  | 0 |  |  | 0 | 0 | 0
9.3.1b | End terminations | Nos |  |  | 0 |  |  | 0 | 0 | 0
9.3.1a | 1 Core x 35 Sq. mm | M |  |  | 0 |  |  | 0 | 0 | 0
9.3.1b | End terminations | Nos |  |  | 0 |  |  | 0 | 0 | 0
9.3.2a | 1 Core x 25 Sq. mm | M |  |  | 0 |  |  | 0 | 0 | 0
9.3.2b | End terminations | Nos |  |  | 0 |  |  | 0 | 0 | 0
9.3.3a | 1 Core x 16 Sq. mm | M |  |  | 0 |  |  | 0 | 0 | 0
9.3.3b | End terminations | Nos |  |  | 0 |  |  | 0 | 0 | 0
9.3.4a | 1 Core x 10 Sq. mm | M |  |  | 0 |  |  | 0 | 0 | 0
9.3.4b | End terminations | Nos |  |  | 0 |  |  | 0 | 0 | 0
9.3.5a | 1 Core x 6 Sq. mm | M | 70 | 70 | 140 | 126 | 21 | 17640 | 2940 | 20580
9.3.5b | End terminations | Nos | 4 | 4 | 8 | 84 | 21 | 672 | 168 | 840
9.3.6a | 1 Core x 4Sq. mm | M |  |  | 0 |  |  | 0 | 0 | 0
9.3.6b | End terminations | Nos |  |  | 0 |  |  | 0 | 0 | 0
9.4 | Busbar of 0.5 Mtr length made out of 50x6 mm GI strip with drill holes of M8 at 25mm interval mounted on insulators. | No. |  |  | 0 |  |  | 0 | 0 | 0
9.5 | Busbar of 0.5 Mtr length made out of 25x6 mm GI strip with drill holes of M8 at 25mm interval mounted on insulators. | No. |  |  | 0 |  |  | 0 | 0 | 0
9.6 | Busbar of 0.5 Mtr length made out of 25x3 mm GI strip with drill holes of M8 at 25mm interval mounted on insulators. | No. |  |  | 0 |  |  | 0 | 0 | 0
9.7 | Busbar of 0.5 Mtr length made out of 25x3 mm Cu strip with drill holes of M8 at 25mm interval mounted on insulators. | No. |  |  | 0 |  |  | 0 | 0 | 0
9.8 | Busbar of 0.5 Mtr length made out of 25x6 mm Cu strip with drill holes of M8 at 25mm interval mounted on insulators. | No. |  |  | 0 |  |  | 0 | 0 | 0
9.9 | Bimetallic Connectors for Connecting Copper cable to GI Busbar | No. |  |  | 0 |  |  | 0 | 0 | 0
9.1 | Antistatic Earthing Mat with all interconnecting accessories | Sq. Mt. |  |  | 0 |  |  | 0 | 0 | 0
| TOTAL PART - 9 | [6 empty] | 18312 | 3108 | 21420
10 | MISCELLANEOUS ITEMS
10.01 | Rubber mats of 1.1 KV grade 1.8 Mtrs x 0.9 Mtrs and of sufficient thickness as required by the Electrical Inspectorate and confirming to IS 5424. | No. |  |  | 0 |  |  | 0 | 0 | 0
10.02 | Shock treatment chart as approved by the Electrical Inspectorate mounted on teak wood frame and suitable for wall mounting. | No. |  |  | 0 |  |  | 0 | 0 | 0
10.03 | First aid kit | No. |  |  | 0 |  |  | 0 | 0 | 0
10.04 | Danger boards mention voltage level in min three languages marked in red as per EB requirements. | No. |  |  | 0 |  |  | 0 | 0 | 0
10.05 | MS Fabricated Items | Kg. | 5 | 5 | 10 | 174 | 37 | 1740 | 370 | 2110
10.06 | Supply & fixing of rubber gloves of Approved Make & as per supply voltage | No. |  |  | 0 |  |  | 0 | 0 | 0
10.07 | Laminated Schematic with glass frame | No |  |  | 0 |  |  | 0 | 0 | 0
10.08 | MS Powder coated pipe support to mount the Occupancy sensor in the office Area. Necessary hardwares to install the same need to consider in the quote. | No. |  |  | 0 |  |  | 0 | 0 | 0
10.09 | 2 hour fire rated fire retardant material sealing (UL Listed) all electrical ducts and openings made in the slab / wall / partition to take conduits / cable trays / raceways etc as required complete / as directed by the site incharge | Sqm. | 0.1 | 0.15 | 0.25 | 5250 | 2625 | 1312.5 | 656.25 | 1968.75
10.1 | 150mm wide x 100mm depth 18G DB cabinet MS Powder coated including supply & installation. | Rm |  |  | 0 |  |  | 0 | 0 | 0
10.11 | Construction Power related Works including Panel, Isolator, Sockets, Light fixture, Cable, Wires & Earthing etc | Ls | 1 |  | 1 | 13125 | 2100 | 13125 | 2100 | 15225
10.12 | Professional Charges: CEIG Inspection : Professional charges towards filing application, preparation of drawings in necessary formats for approval, follow up and arranging approval of drawings, scheme by Local electricity authority / Electrical Inspectorate, obtaining clearance from electricity authority / Electrical Inspectorate. | LS |  |  | 0 |  |  | 0 | 0 | 0
10.13 | As built drawings
| Preparation and Submission of as built drawings, (3 sets of hard copies and soft copy in a CD) 1. Schematic distribution diagram 2. Floor plans 3. Reflected ceiling plans if any. 4. Earthing schemes and plans. and other related drawings. | LS |  | 1 | 1 | 36750 | 15750 | 36750 | 15750 | 52500
| TOTAL PART - 10 | [6 empty] | 52927.5 | 18876.25 | 71803.75

## FUNCTIONAL & DECORATIVE LTG
ELECTRICAL WORKS FOR COWRKS, MORGAN STANLEY,6A-1ST & 2ND FLOOR,BANGALORE
CLIENT | : MORGAN STANLEY | [7 empty] | DATE / REV NO. | :10.03.2026 / R1
ARCHITECTS | : COWRKS | [7 empty] | SUBJECT | : FUNCTIONAL & DECORATIVE LIGHTING
PMC | : | [7 empty] | CONSULTANTS | : ESOLLUTIONS
BILL OF QUANTITIES - FUNCTIONAL LIGHTING
SL. NO. | DESCRIPTION | IMAGE (INDICATIVE IMAGE ARE ONLY FOR REFERENCE) | UNIT | QUANTITY |  |  | RATE IN INR |  | AMOUNT IN INR |  | TOTAL
|  |  |  | 1F | 2F | TOTAL | SUPPLY | INSTALLATION | SUPPLY | INSTALLATION
11 | LIGHT FIXTURE
Note: Catalogue numbers indicated are only to describe type of light fixture required. Lamp Colour shall be - 84 or as approved by Architect / Consultant.
a. Whether explicitly mentioned or not vendor shall consider light fixtures with necessary powerfactor improvement condensors. b. Unless specified all light fixtures shall be considered with electromagnetic ballasts. The loss of ballasts shall not exceed 5.5 Watts c. Vendor shall consider necessary fixing hardware and components to install light fixtures. The hardware viz., anchor fasteners, suspending GI chains, down rods will not be measured seperately. Vendor shall assume a minimum suspension length of 1.2 to 1.5 Mtrs
Light Fixtures. Quoted rate shall include mounting bracket and lamps
Supply, transportation, delivery, unloading, Installation, Testing and Commissioning the below indicated light fixtures to site.
Light fixtures complete with accessories like control gear, low loss (<5W ) HF Electronic ballast , HPF condensor (PF shall be >0.85 lag.), energy efficient high lumen output fluorescent tubes / CFL lamps etc.,
Note : The make mentioned here is only indicative & any of the make mentioned in recommended list of makes is preferred.
The electronic / Digital ballast shall be with THD < 10%. & low loss copper ballast.
Gripple/steel ropes need to be considered for suspended light fixtures
All Functional light fixtures shall have 5 Years of warranty on Diffuser, Lamp and Driver
Rate shall include Branded LEDs (Philphs, Samsung, Nichia, Osram, Cree), BAG, Philphs, Osram Driver. Lamp colour shall be kelvin. Quantity to be supplied based on the final GFC drawing not as per the BOQ.
All the fixtures shall be ordered based on the final GFC Drawing.
Linear light should be wired intenally for seemless connectivity
The luminaries shall have IP-20 degree of protection.
LED shall be of high efficiency, long life in warm white or cool day light, The estimated lifetime of LED shall be minimum 50,000 burning hours.
R9>=50, CRI of 90 & UGR < 19 shall be considered.
| Technical points: | Confirmation from bidders:
a. Type of Body shall be Aluminium
b. Profile / Body should not be less than 2mm thick
c. UGR19 or less than 19
d. Class of LED
e. LED Make & Country of origin
f. Lumens per watt
g. Driver Make & from which Country
h. Burning hours
i. Percentage of LED depreciation after specificied burning hours
j. 5years complete fixture replacement warranty
k. Performance Gaurantee
11.1 | Pendatn light fixture |  | Nos |  | 10 | 10 |  | 250 | 0 | 2500 | 2500
11.2 | 600 MM dia pendant light |  | Nos |  |  | 0 |  |  | 0 | 0 | 0
11.3 | Decorative pendant light |  | Nos | 2 |  | 2 |  | 300 | 0 | 600 | 600
11.4 | Globe Industrial pendant light |  | Nos | 3 | 4 | 7 |  | 250 | 0 | 1750 | 1750
11.5 | Suspened Bulbs type-1 |  | Nos | 6 |  | 6 |  | 300 | 0 | 1800 | 1800
11.6 | Suspended light |  | Nos | 6 |  | 6 |  | 350 | 0 | 2100 | 2100
11.7 | Framed chandiler type-1 |  | Nos | 2 |  | 2 |  | 350 | 0 | 700 | 700
11.8 | Framed chandiler type-2 |  | Nos | 2 | 2 | 4 |  | 350 | 0 | 1400 | 1400
11.9 | Black fame pendant-Single |  | Nos | 9 | 15 | 24 |  | 350 | 0 | 8400 | 8400
11.1 | Decorative pendant-Industrial fixture |  | Nos |  | 4 | 4 |  | 350 | 0 | 1400 | 1400
11.11 | Recessed downlight luminaire Blaire with HPE (High-Performance Efficiency) LED (Light Emitting Diode) system power: 15 W, Luminous flux of luminaire 950 lm, Colour temperature of 4000 K, Neutral white, SDCM 3, CRI > 90, 230 V constant current driver, 70% of luminous flux after 60,000 operating hours; Energy efficient LEDs, Direct light emission, Luminaire housing in aluminium, Polyester powder white coloured coat applied over a 5- stage pre-treatment, Prismatic diffuser for homogenous light distribution, ZHLS (ZERO HALOGEN LOW SMOKE) wiring, Electronic control gear, Protection class II, IP 40 Ø = 175 mm, DA(Ø) = 160 mm, H = 59 mm |  | Nos | 52 | 52 | 104 |  | 250 | 0 | 26000 | 26000
11.12 | FIXTURE TYPE: COVE LIGHT WATTAGE: 14.4W/MTR MATERIAL: 1.8MM THICKNESS ALUMINIUM LIGHT COLOR: 3000K MOUNTING: SURFACE MOUNTED DIMENSION: W17.4 X H7 MM BODY COLOR: GREY DIFFUSER: ACRYLIC LIGHT SOURCE:LED STRIP DRIVER: ON/OFF |  | Mtr |  |  | 0 |  | 60 | 0 | 0 | 0
11.13 | LED Driver for Sl. No. 11.7 |  | Nos |  |  | 0 |  |  | 0 | 0 | 0
11.14 | 10W LED Track Light Fixture , LIGHT COLOR: 3000K |  | Mtr | 30 | 15 | 45 |  | 300 | 0 | 13500 | 13500
11.15 | Track / Trackway / Rail Support channel for Track Light Installation |  | Mtr | 6 | 3 | 9 |  | 250 | 0 | 2250 | 2250
11.16 | Digital PIR presence / Motion detection sensor of range 7.0 m Dia coverage recessed mounting at height of 2.4-3 meter to control 6A lighting load with 3 meter four core power cable. To be commissioned by hand held programmer with programmable features of delay time 5 min - 35 min, photocell and power up (status of luminaires when power is applied). It shall have provision to manually override luminary ON/OFF status using hand held remote control. |  | Nos. |  |  | 0 |  |  | 0 | 0 | 0
11.17 | Digital PIR presence / Motion detection sensor of range 4 m (W) X5m (L) coverage recessed mounting at height of 2.4-3 meter to control 6A lighting load with 3 meter four core power cable. To be commissioned by hand held programmer with programmable features of delay time 5 min - 35 min, photocell and power up (status of luminaires when power is applied). It shall have provision to manually override luminary ON/OFF status using hand held remote control. |  | Nos. |  |  | 0
11.18 | Removal of Existing light fixutres |  | Lumpsum
| TOTAL PART - 11 | [7 empty] | 0 | 62400 | 62400