## SUMMARY
CLIENT | M/s. Paytm Bengaluru
SUBJECT | Detailed Offer
DATE | 2026-04-13
CARPET AREA | 12377
REVISION | R0
SR NO | PARTICULARS | PER SFT | AMOUNT | REMARKS
PART - C | MEP WORKS
1 | ELECTRICAL WORKS | 458.6212 | 5676354
2 | LIGHT FIXTURES | 10.168 | 125849
3 | UPS | #REF! | #REF!
4 | HVAC WORKS | 339.3391 | 4200000
5 | FIRE AND SAFTY | 233.8479 | 2894335.6
6 | ACCESS AND CCTV | 99.1605 | 1227310
7 | BMS
8 | NETWORKING
9 | HDMI CABLES /USB CABLES
10 | AV WORK
| TOTAL FOR PART - C | #REF! | #REF!
I | TOTAL - WITHOUT TAXES | #REF! | #REF!
a | ADD LABOR CESS @1% | #REF! | #REF!
II | TOTAL - WITH BOCW | #REF! | #REF!
| KITCHEN EQUIPMENTS | 0 | 0 | Not Applicable

## MEP SUMMARY
PAYTM MEP COSTING SUMMERY SHEET
Project Location |  | Bangalore
Area
Sl.No | Package | Supply | Installation | Total | Remarks
1 | ELECTRICAL WORKS | 4715431 | 960923 | 5676354
2 | LIGHT FIXTURES | 0 | 125849 | 125849
3 | HVAC WORKS | 3463623 | 736377 | 4200000
4 | FIRE AND SAFTY | 2437564 | 456771.6 | 2894335.6
5 | ACCESS AND CCTV | 1115510 | 111800 | 1227310
| Grand TOTAL | 11732128 | 2391720.6 | 14123848.6

## PREAMBLE
Preamble Points:
Following is integral part of Contractors Scope of Work points and Contractor to take note of same while quoting and during execution for the work:
1 | The Preamble to the Bills of Quantities must be read with the Drawings, Conditions of Contract and the Specification and the tenderer shall be deemed to have examined the Drawings, Specifications, Conditions of Contract and to have acquainted himself with the Works to be done and the way in which they are to be carried out. This preamble to the Bills of Quantities shall form part of the Contract.
2 | The Tenderers are requested to inspect the site and obtain for themselves at their own expense all necessary information and particulars to enable them to submit the tender.
3 | The dimensions shown in the drawings shall have to be verified by the contractor at site before execution of the items and necessary allowance's) have to be made as per the actual dimensions available at site.
4 | For the items of works having Basic rate of material, price adjustment will be made only on the actual quantity measured. Wastage & Installation shall be to Contractors account. Basic rate indicates loading unloading, transportation etc.
5 | The contractor should refer to the tender drawings / 3D views / Technical specifications for details. In case of any discrepancy, the drawing will take precedence, unless specifically mentioned in the BOQ.
6 | All pre-fabrication works wherever possible shall be carried outside the client's premises, only assembling and finishing work will be allowed within the Site. This is specific to finishing works involving high VOC items which are not permissible to be executed within the premises. The list of such works will be mutually agreed during the kick off meeting.
7 | Unless specifically mentioned otherwise in the contract, the tenderer shall quote for the finished items and shall provide for the complete cost towards labour, materials, plant and machinery, operational costs, levies, taxes, transport, repairs, rectification, maintenance till handing over, revenue expenses, contingencies, overheads, profits and all incidental items not specifically mentioned but reasonably implied and necessary to complete the works according to the contract.
8 | The quantities of the various items mentioned in the schedule of items are approximate and may vary up to any extent or be deleted altogether. The quoted rates of each item shall remain firm for all works. The contractor, in his own interest, should get an indication of the probable extent of the work to be executed under any item in this schedule, before undertaking any preliminary and enabling work or purchasing bought out components related to the work.
9 | Sample: Contractor at his own cost shall produce the samples for approval from Architect or EIC, after the due approval of sample contractor shall go for procurement, if architect ask for more samples contractor shall arrange for the same without delay.
10 | Mock-ups: Contractor shall make or Build mock-ups to verify selections made under sample Submittals and to demonstrate aesthetic effects and qualities of materials and execution as instructed by EIC. Approval of mock-ups does not constitute approval of deviations from the Contract Documents contained in mock-ups unless Architect specifically approves such deviations in writing. Approved mock-ups may become part of the completed Work if undisturbed at time of Substantial Completion. The mock up shall be free of cost.
11 | Procedure of work: The contractor shall arrange the operations that have been agreed to by the Project consultants /Employer. He shall adhere to the schedule presented by him and agreed by the project consultants and shall complete all works allotted to him in time, giving best workmanship to the entire satisfaction of the Project consultants.
12 | Protection of work: Contractor shall do protection of asset’s which are not to be demolished and asset’s which are to be handover to client. He shall also provide and maintain any other temporary covering that required for the protection of financed / unfinished woodwork that may be damaged during the progress of the work if left unprotected.
13 | Contractor should protect with PVC bubble guard sheet of 6mm thk all the completed works in his scope and uncover the same while it’s being handed over.
14 | In case there is possibility of surrounding works carried out by other getting damaged, it is responsibility of the contractor to protect them and uncover on completion.
15 | Masking tapes to be used during silicon filling, painting, polishing works and removing the same properly.
16 | Making required size site offices & store at designated location
17 | Stock / Stack all Contractor supplied materials properly and maintain all records.
18 | Dismantle the stores at the end of works and dispose of all the scarps, balance materials as per the project guidelines.
19 | Safety of contractor supplied material is contractor scope.
20
21 | Items of work provided in this schedule but not covered in the specifications shall be executed strictly as per instructions of the project manager/architect.
22 | All stones mentioned in the tender shall be brought to site only from the lots pre-approved /selected by the architects.
23 | All Samples of tiles, fittings etc. shall be presented after ensuring that the necessary quantities of the relevant item(s) for which the same are invited are available, (ex-stock, or otherwise) and shall be approved by the architect before placing of mass orders.
24 | All the Dado and/ Flooring shall include rates of the 3mm thk spacers with colour matching grouts and Edge Guards of matching colour of the dado wherever the walls are in right angles, as per instructions / related specifications towards the same, by the consulting architects
25 | All joints, wherever necessary, shall be undertaken after prior approval of the same from the Architects.
26 | All materials utilized shall be as per tender recommendations and shall be applied according to manufacturer's specifications.
27 | The rates for all tiles, slabs of marble, granite, Kota or any other stone should be inclusive of all materials, transport, loading unloading, Octroi and all taxes thereon. The rate mentioned is the maximum and in no way should exceed, the one mentioned.
28 | Rates quoted for items of counter, etc. shall be inclusive of making necessary cutouts for sinks, basins and inclusive of polishing the cut edge to the profile as indicated on the drawings, to the entire satisfaction of the supervising architects.
29 | Rates quoted for the Ramps/ treads of the staircases shall be deemed to be inclusive of making all necessary cutouts, for railing balustrades, etc., in 'workmanlike manner, and, to the entire satisfaction of the supervising architects
30 | Unless other wise specified all rates shall be in INR
31 | Work shall be at all heights including double and triple heights and rate shall include the cost of necessary scaffolding and staging
32 | Any/all inserts/U/Hat/Corner etc. profiles/grooving and laying patterns shall be as per architects specifications and shall form part of the relevant panelling detail(s) and shall not be paid for extra, unless otherwise specified/ mentioned
33 | Rates quoted for full height partitions shall be inclusive of insulation of rock wool/ glass wool to be enclosed in a polythene sheet (of pre-approved grains/massing, as specially required/recommended by consultants, for acoustic purposes) as specified unless mentioned otherwise. Insulation can be installed without polythene sheet but fixed with wire frame works
34 | Rates quoted for the partitions & Walls shall be inclusive of making cutouts for Electrical, AV, HVAC Ducts, Data etc., outlets and for making provisions for passing conduits through the framework.
35 | Rates quoted for partitions/Panelling/walls/ etc. shall be inclusive of additional vertical or horizontal frame members as required for skirting, fixing soft board, white board, projection screens, TV's etc. fixing of elec. Boxes etc. apart from the regular framework members @ 600mm c/c both ways.
36 | Rate to include Aluminium 'U' channel of given size in drawings or as instructed by architect of approved make, as per design and detail, in all panelling works of the Second Skin, wherever indicated and required for the finishing of grooves, as per Architect instruction.
37 | All Panelling shall be measured and paid for only up to the false ceiling, even though the panelling is required to be extended 75mm above the false ceiling for the supporting of the false ceiling itself.
38 | All Door frames to be fixed to masonry in proper plumb and in workman like manner, and shall be inclusive of desired number of Anchor fasteners with chemical grouting, per door, as specified, and all other hardware's as required to fix the same, and up to the entire satisfaction of the Architects.
39 | All doors shall be of standard 35 mm thickness unless otherwise specified. In case of concealed door closures mentioned in the specifications the doors shall be min. 42mm thk (even if not specified). Rates to be quoted accordingly.
40 | All tables shall have provision for Wire management as per design and detail.
41 | If required and instructed by the architect, the wire management system of the table shall be separately bought out and fitted on to the table as per design and detail.
42 | All tables to be finished in workman like manner up to desired and approved finishing standards, failing which, the same shall be undertaken and achieved by the Architects at the sole risk and responsibility of the concerned Contractors.
43 | All materials used to be non/ low VOC products. Wood to be FSC certified.
44 | Rate of the BWP ply shall be considered in all dry areas and rate of BRP ply / Marine ply shall be considered in all wet areas .All ply to be green certified
45 | All storages unless otherwise mentioned in the item specifications shall be 450mm depth.
46 | All storages shall be finished internally with 0.8mm laminate unless otherwise specified
47 | Storages shall be inclusive of hardware like locks, brushed steel handles, tower bolts, ball catches, SS hinges or auto close concealed hinges of approved make as per Architect instruction, even if not explicitly mentioned in the specifications unless specifically mentioned otherwise.
48 | Necessary support from below raised flooring for all type of partition to be considered in respective line item rate
49 | Make list to be as per Architect / Consultants choice.

## MAKES - MEP
PROJECT | PAYTM
SUBJECT | MAKE LIST
DATE | 2026-04-01
VERSION | V0
SUBJECT: STANDARD MAKES- PAYTM
| ITEMS | MAKES
A | ELECTRICAL&ELV
1 | LT CABLES | KEI/ POLYCAB/ RR KABEL | Polycab
2 | CABLE GLANDS & LUGS | BRACO / DOWELS / JAISON / SMI / HMI | Dowells
3 | FRLS / ZHFR WIRES & MULTI CORE FLEXIBLE CABLES | POLYCAB / KEI/ RR KABEL | Polycab
4 | TECHNICAL LIGHT FIXTURES | WIPRO/ PHILIPS/ARRAY STORM/ LEGERO / CENZER
5 | DECORATIVE LIGHT FIXTURES | LEGERO/RIPPL/ LUNNARK / PURPLE TURTLES /LANCE
6 | LIGHTING CONTROL SENSORS | HONEYWELL / ZEN CONTROL / LUTRON
7 | FANS & EXHAUST FANS | CROMPTON/ BAJAJ/ HAVELLS | Caryaire
8 | FLOOR BOXES & WORKSTATION POP Ups | Connect System / CJ Infra
9 | SWITCHES / SOCKETS & MODULAR FACE PLATES | ANCHOR- ROMA / SCHNEIDER - LIVIA / LEGRAND / INDOASIA SHYNORA / SIEMENS
10 | DISTRIBUTION BOARDS | ABB / SCHNEIDER/ LEGRAND/ SIEMENS
11 | MCBs/RCCB/RCBOs/ Isolators | ABB / SCHNEIDER/ LEGRAND/ SIEMENS
12 | MCCBs | ABB / SCHNEIDER/ LEGRAND/ SIEMENS
13 | INDUSTRIAL SOCKETS | LEGRAND / SCAME / NEPTUNE / HAGER
14 | PVC CONDUITS & ACCESSORIES | VIP / AVANPLAST | VIP
15 | MS / GI CONDUITS & ACCESSORIES | GUPTA / AKG/ GB
16 | GI RACEWAYS / CABLE TRAYS | CLASSIC / PUSHPAK / PROFAB | Vickram
17 | ALUMINIUM RACEWAYS | JINDAL
18 | UPVC TRUNKING/RACEWAY | MK/ OBO BETTERMANN/ LEGRAND | OBO
19 | HRC SWITCH FUSE UNITS | GE / L&T / SIEMENS / ABB / SCHNEIDER (MERLIN GERIN)
20 | RG59 OUTLETS | ANCHOR / CRABTREE(VERONA)
21 | RG59 COAXIAL CABLE | FINOLEX / POLYCAB
22 | LOAD MANAGERS / MEASURING INSTRUMENT | TRINITY / HPL / ENERCON / SECURE / SCHNEIDER / ELMEASURE
23 | CONTACTORS | L & T / SCHNEIDER (MERLIN GERIN) / LEGRAND
24 | C.T UNIT | INDCOIL / MECO / SIEMENS
25 | CAPACITOR | SUBODHAN / LEGRAND / EPCOS / SIEMENS
26 | P.F. RELAY | TRINITY / ENERCON / SECURE / L&T / SIEMENS
27 | MANUAL CHANGE OVER SWITCH | L & T / SCHNEIDER (MERLIN GERIN) / SOCOMEC
28 | AUTOMATIC TRANSFER SWITCH (ATS) | ASCO / LT / SOCOMEC
29 | PANEL ACCESSORIES | L&T / SIEMENS / MG / GE
30 | SPD/TVSS | LEGRAND / SCHNEIDER (MERLIN GERIN) / HAGER/OBO
31 | LT PANELS & Fabricated DBs | SHARAN CONTROLS/ MASS ENGINEERING/ SAMRUDHI CONTROLS
B | UPS & INVERTERS
1 | UPS | Vertiv / APC Schenider
2 | UPS BATTERY | Amar Raja/ Exide/ Quanta
3 | ONLINE INVERTOR | Microtec/ Luminous/ Su-Kam/ Consul Neowatt | microtec
4 | INVERTOR BATTERY | Amar Raja/ Exide /Rocket/ Quanta | Exide
C | NETWORKING
1 | CAT-6/ Cat6A cable / Patchpanels / IOs & patch cords | COMSCOPE net connect /AMP / MOLEX | commscope
2 | Racks | NETRACK / VALRACK | netrack
3 | Lables | Panduit / Equivalent
4 | MDF & Connectors | KRONE
5 | Telephone wires | DELTON / FINOLEX / Polycab
D | FIRE ALARM SYSTEM
1 | Fire Alarm Panel | Edwards / Simplex / Notifier | Edwards
2 | Loop Cards | Edwards / Simplex / Notifier | Edwards
3 | Repeater Panel | Edwards / Simplex / Notifier | Edwards
5 | Photelectric Smoke Detectors | Edwards / Simplex / Notifier | Edwards
6 | Heat Detectors | Edwards / Simplex / Notifier | Edwards
7 | Multisensor Detectors | Edwards | Edwards
8 | Interface Modules : Monitor / Relay / Control etc. | Edwards | Edwards
9 | Sounders / Sounder cum Strobes | Edwards | Edwards
10 | Manual Pull Stations | Edwards | Edwards
11 | Fault Isolator Modules | Edwards | Edwards
12 | Response indicators | Edwards | Edwards
13 | Control Cables | Varsha / Ravicab / KEI | polycab
14 | MS / GI CONDUITS & ACCESSORIES | GUPTA / AKG/ GB
E | PUBLIC ADDRESS SYSTEMS
1 | Main PA Controller | Bosch / Honeywell / Heinrich | Bosch
2 | Slave Controller | Bosch / Honeywell / Heinrich | Bosch
3 | Audio Amplifier | Bosch | Bosch
4 | Call station / Keypad | Bosch | Bosch
6 | Gooseneck Microphone | Bosch | Bosch
7 | Speakers (Ceiling/Wall Mount) | Bosch | Bosch
8 | Background Music Source | Bosch | Bosch
9 | Control Cables | Varsha / Ravicab / KEI | polycab
10 | PVC Conduits | VIP / AVANPLAST / ISI Marked equivalent | VIP
11 | Cable Tray | CLASSIC / PUSHPAK / PROFAB | Vickram
12 | MS / GI CONDUITS & ACCESSORIES | GUPTA / AKG/ GB
F | SPRINKLER SYSTEM
1 | MS / GI Pipes | Tata / Jindal
2 | Pipe Fittings | On sample approval
3 | Sprinkler bulbs | Tyco / Viking | Tyco
4 | Flexible drops | Tyco / Viking/ Youngjin/ New age | Newage
5 | Butterfly valves | Asian / Normax/ Syatem sensor/ Tyco | Sant
6 | Pressure gauges | H Guru / Equivalent | H guru
7 | Flow switches | Tyco/ System sensor/ Honeywell | Honeywell
8 | Paints | Berger / Asian
9 | Threded rods & supports | Hilti/ Equivalent | Equivalent
G | IP BASED CCTV SYSTEM
1 | IP Dome / Bullet Cameras | PRAMA | Prama
2 | NVR & Softwere | PRAMA | Prama
3 | Storage hard discs | WD / Seagate | Seagate
4 | PC / Monitors | Lenovo/ Dell/ Samsung
5 | Power Supplies | Reputed
6 | Copper Cables | Varsha / Ravicab / KEI
7 | CAT-6 cables & accessories | AMP / BELDEN/ MOLEX
8 | Conduits | VIP / AVANPLAST / ISI Marked equivalent
9 | MS / GI CONDUITS & ACCESSORIES | GUPTA / AKG/ GB
H | ACCESS CONTROL SYSTEMS
1 | Proximity Card Readers | "Current ACS Detailed Spec EM Lock Single 600 LBS with L Bracket 83014090 Make Bel EDR Reputed brand Oryggi 4 Door 4 Reader controller with enclosure and PSU Access Card Reader Smart-I SPR-501 Oryggi 4 Door 4 Reader controller with enclosure and PSU Enclosure Box For Controller Oryggi Controller License Oryggi Bio metric reader for Server Room"
2 | Biomatric readers
3 | Access Controller
5 | Access Control Software
6 | Emergency Break Glass unit | MAG/AUTO COP/ALAGAT/Agni
7 | EM Door Locks | Algatec / Faradays / Ebelco / Insyin
8 | Magnetic Contact | ALAGAT/BEL/EBELCO/System Sensor
9 | PC / Monitors | Lenovo/ Dell/ Samsung
10 | POE/ Network Switches | D-Link / TP Link / Netgear | D link
11 | Power Supplies | Reputed
12 | Panic Bar | Dorma / Geze
13 | MS / GI CONDUITS & ACCESSORIES | GUPTA / AKG/ GB
I | FIRE SUPPRESSION & SIGNAGES
1 | Fire extinguishers | Kanex / Safex / Excellent | Safex
2 | Extinguisher signages | PROLITE / Equivalent on sample approval | Prolite
3 | Auto glow type Exit signages | PROLITE / Equivalent on sample approval | Prolite
4 | LED Signages | PROLITE / EATON / Equivalent on sample approval | Prolite
5 | Fire evacuation route plan | PROLITE / Equivalent on sample approval | Prolite
6 | Gas supression system | Kiddey / Ansul / Siemens
7 | VESDA system | Xtralis / Tyco
8 | Pre action system | Tyco / Viking
9 | WLD System | C System / Maser | C System
10 | Rodent Reppellant system | C System / Star | C system
J | HVAC
1 | DX Type AC Units | Bluestar / Toshiba / Daikin | Bluestar
2 | VRF system | Bluestar / Toshiba / Daikin | Bluestar
3 | PAC Units | Stulz / Vertiv / Clima-Veneta
4 | Chilled water based CSUs / AHUs | Edgetech / Citizen / Zeco / VTS
5 | Chilled water based Casette/ Hi-wall Units | Midea / carriaire / Kubic
6 | Inline Exhaust fans & Fresh air fans / TFA | Kruger / Nicotra / Dynair / System air | Caryaire
7 | Variable Air Volume (VAV) Units | Boxes - Dynacraft /approved Duct fabricator Controllers - Honeywell / Belimo / Neptronics / KMC / Sauter | Dynacraft
8 | Refrererant pipes | Copper Pipes - Mandev / Rajco / Nippon / Bundi; Insulation - Armaflex / K-flex | Rajco, K-flex
9 | Drain Pumps | Aspen / Equivalent | Aspen
10 | Sequence Controllers & Timers | VK Power master/ Tittanix | VK power master
11 | Factory fabricated ducting - Rectangular | Zeco / 7 star / Vedha / Camduct / GP Spira/ Ductofab | Ductofab
12 | Factory fabricated ducting - Ovel / Round | GP Spira / Zeco / 7 star / Vedha / Camduct / Dev duct /Ductofab | Ductofab
13 | Factory fabricated Plenum Boxes | Zeco / Edgetech / Vayhan / Aagam
14 | Insulated Flexible ducting | UP Twiga / ATCO | UP twiga
15 | Double Canvass Connection | Mapro
16 | Thermal Insulation of Ducts | Armaflex / K-flex
17 | Acoustic Lining of Ducts | Armaflex / K-flex
18 | Acoustic Insulation of Walls / AHU RM | Armaflex / K-flex
19 | Underdeck Insulation | Armaflex / Kflex
20 | Fire & Smoke Dampers with Fusible Link | Cosmos / Dynacraft | Caryaire
21 | Fire & Smoke Dampers | Cosmos / Dynacraft | caryaire
22 | Motorised Actutators | Honeywell / Belimo/ Delta | honeywell
23 | Volume Control Dampers | Cosmos / Dynacraft / Air Products / Air Master | Aura
24 | Back Draft Dampers | Cosmos / Dynacraft / Air Products / Air Master | caryaire
25 | Butterfly dampers (spigot) | Cosmos / Dynacraft / Air Products / Air Master | Aura
26 | Grilles & Diffusers | Cosmos / Dynacraft / Air Products / Air Master | caryaire
27 | Acoustic Louvers (Z Pieces) | Factory Fabricated with approved sample Insulation: Armaflex / K-flex; Adhesive - Fevicol / Pidilite
28 | Control Cabling | Polycab / KEI / Finolex | Polycab
29 | Duct static pressure sensor & controller | DP Sensor -Dwyer / ALM & Controller - VEMCO
30 | Disc Valves For Exhaust | Dynacraft / Air Products / Cosmos / Air Master | caryaire
31 | Door Transfer Grilles | Dynacraft / Air Products / Cosmos / Air Master | caryaire
32 | EC Fans | ZEIL ABEGG / EBM
33 | UV lamps | Ensavior / Honeywell / Phillips-Signify /
34 | MERV 13 / MERV 9 Filters | AEROSOL / DYNA / MNR / SPECTRUM / AAF | Spectrum
35 | Air Purifiers | Camfil/Purafil / Euronics
36 | IAQ Monitors | Intelligreen / Honeywell/ Ultra-Pure
37 | Ionizers for Indoor Air Quality | Intelligreen/ Zeco-GPS/Pure-Air
38 | MS / GI CONDUITS & ACCESSORIES | GUPTA / AKG/ GB
K | BMS
1 | Sever and Operator Workstation Hardware | Dell / Lenovo / HP
2 | A4 Colour Inkjet Printer | HP / Epson / Canon
3 | Software - BMS with built-in Energy Management software | Honeywell Trend / Honeywell Tredium/ Eneffen - Sauter / Trane / Schneider/DELTA
4 | DDC Controllers - Bacnet/IP | Honeywell /Greystone/Dwyer/Omicron/DELTA
5 | DDC Panels | Honeywell /Greystone/Dwyer/Omicron/DELTA
6 | Interfaces / Gateways / Network Controllers | Honeywell / Schneider / Trane/DELTA
7 | Magnetic flow meter | Forbes Marshall / Onicon / Endress & Hausser
8 | Pressure indicators | Waaree / Honeywell / Dwyer
9 | Pressure Switches | Honeywell /Greystone/Dwyer/Omicron/DELTA
10 | Temperature sensors | Honeywell /Greystone/Dwyer/Omicron/DELTA
11 | RH Sensors | Honeywell /Greystone/Dwyer/Omicron/DELTA
12 | Indoor Air quality sensors | Honeywell /Greystone/Dwyer/Omicron/DELTA
13 | Duct Smoke Detectors | Honeywell /Greystone/Dwyer/Omicron/DELTA
14 | Hydrogen sensor | Dettronics / MSR / Ambetroncs
15 | Air flow switches | Honeywell /Greystone/Dwyer/Omicron
16 | Pressure Sensors | Honeywell /Greystone/Dwyer/Omicron
17 | Level Switches | Honeywell / Sontay / Dwyer / Filpro
18 | CO2 and CO sensors | Honeywell /Greystone/Dwyer/Omicron
19 | DP switches | Honeywell /Greystone/Dwyer/Omicron
20 | Cable Tray | CLASSIC / PUSHPAK / PROFAB
21 | Copper Cables | KEI / Polycab/ Varsha
22 | CAT-6 cables & accessories | AMP / BELDEN/ MOLEX
23 | Conduits | VIP / AVANPLAST / ISI Marked equivalent
24 | Optic Fiber Cable | AMP / Dlink / Belden
25 | Btuh Meters with Match Pair Sensors | Landis & Gyr / Kamstrup / Onicon
26 | Immerson type temp sensors | Honeywell / produal / Dwyer
27 | Protocol conveerters | Field server / Adfweb / protosensor
28 | MS / GI CONDUITS & ACCESSORIES | GUPTA / AKG/ GB

## ELEC BOQ
PROJECT | : PAYTM BANGALORE
SUBJECT | : BILL OF QUANTITIES - ELECTRICAL
DATE | : 30.03.2026
VERSION | : V0 |  | Quantity
Sl.No. | DESCRIPTION | UNIT | 6F | Total | RATE |  | AMOUNT |  | Total | REMARKS
[5 empty] | Supply | Installation | Supply | Installation
I | LT PANELS :
A | All Panels Should be as per Technical specifications & Power distribution scheme
Supply, installation, testing & commisioning of 3 Phase, 4 wire, 415 V, 50 Hz panels. The fabrication shall be made with cold rolled annealed sheet with Machine pressing. The surface shall be rigorously treated for derusting in 7 tank process with powder coating. The panel shall be totally enclosed metal clad type with double gasketting with rubber / foam gasketting. The panel shall be off- white painted inside and shall be having control directory pasted on the inside surface of the panel door. The panel shall be suitable for mounting on existing trench and shall have cable entry provision from the top and bottom with suitable alley as the case may be. The panel shall be tested for the same KA rating of the relevant highest rating of breaker. All components shall be of approved make and shall have relevant IS/IEC approvals (Fabrication, drawing, list of components and panel detail shall be got approved before fabrication). The panel shall include base frame channel support.All complete as per relevant standard, technical specification, SLD, data sheets and direction of Engineer-in-charge.
Indoor type LT Switchboards, Floor mounting type, Bottom/Top entry. Refer enclosed SLD for component details.
Doors:2mm Body:2mm Gland Plate :3mm covers and partitions:1.6mm
IP class:IP52 for Indoor/IP55 with weather proof enclosure with top cover for outdoor
Bus bars: Electrolytic grade conductivity as per standard IS 5082
Bus bar Material: As per SLD
Bus bar supports: DMC/FRP/SMC
Bus bar joints: Shrouded/Tinned
Protection releases: As per SLD (Adjustable over current & short circuit unless otherwise specified)
Shade: Epoxy powder coated RAL 7032 for RP Panel & another colour for UPS Panel
Design: Modular type & Form 3B Construction
Cable entry: As per site condition
Bus bar insulation: Aluminum bus bars shall be bare with color coding at the ends/Copper shall be bare with color coding at the ends/For Humidified areas the copper bus bars shall be coated with tin.
Note:
1. The Panel shall be fully as per the requirement of CEIG/Electrical Inspectorate/ EB authorities.
2. Auxiliary contactor to be provided along with auto-manual switch where ever required.
3. All Breakers both Incoming & Outgoing shall have LED 'ON / OFF / TRIP' indications without fail.
4. CTs shall be of cast resin /polycarbonate split core type only.
5. All doors to have double rubber/foam gasket with shutter assembly & door seating frame.
6. All AC feeders will have time delays of 0-60 Seconds.
7. All MCCBs of 250A and above for non-ups loads will be microprocessor based only and all UPS Related panels shall be with thermal Magnetic releases only
8. All DLMs to be of dual source meters unless otherwise specified.Make:Elmeasure Model No EN 8410 with maximum demand parameter & RS 485 port or Equivalent
9. The current density for Aluminium busbars shall be 0.8 only.
10. The current density for Copper busbars shall be 1.6 only.
11. All UPS outgoing panels shall have neutral busbars double the size of phase & gland plates should be of alluminium.
12. All MCCB's shall have plug setting from (70 -100%) for < 250A & (40 - 100%) for > 250A
13. All Incomer ACB, MCCB's shall have 2nos. NO + 2nos of NC Auxiliary contacts for BMS integration. Seperate compartment to be provided for BMS cabling with dedicated connectors
14. All Lighting / RP and Lift panels shall have ELR with Rectangular CBCT for incomer.
15. All test certificates must be provided immediately after commissioning.
16. SAFETY CERTIFICATE FOR THE PANELS SHALL BE PRODUCED FROM CEIG.
17. All meters shall be Digital type only.
18. FRLS PVC copper wires shall be used for control wiring
19. Louvers shall be provided for all the bus bars chambers (Horizontal & Vertical) with mesh to meet IP Requirement.
20. All ACBs shall confirm IS 13947-1/IEC 947-1 for general rules & IS 13947 rules & IS 13947-2/IEC 947-2 for Circuit breakers.
21.All breakers shall have spreaders of same make as make of breaker.
22. Panel builder and Switchgear Manufacturer must ensure total selectivity between Upstream and Downstream Breakers for entire electrical distribution network . Switchgear manufacturer shall submit Total Discrimination report along with techno-commercial offer.
23. All vertical bus bars in bus bar alley shall have bottom supports.
24. Panel earthing strip should come out vertically on top/bottom of the panel to suit the site condition.
25. Earthing bus shall be with green colour coding.
27. Door earthings shall be provided for all doors.
28. Base frame shall be with each panel. The size shall be equal to each section.
29. Bi-metallic tape / washers to be used where ever copper & Aluminium are joined.
30. All MCCB's shall have flag indication for tripping.
31. The material of construction shall be CRCA sheet.
32. Live parts shall not be accessible after opening the door, Transparent acrylic sheet to be provided to cover the same & busbar joints section shall be covered with PVC shrouds.
33. In any case Aluminium bus bars should not be connected directly to the breaker without spreaders.
34. Panel should be as per IEC-60439
35. All UPS panels should be with copper bus bar.
36. Panels should be provided with Lifting lugs/ Eye bolts for lifting the panel.
37. All the busbar bolts of 8.8 Grade should be tightened for Torque of 23N-m for 8mm, 45N-m for 10mm, 80N-m for 12mm bolt/nuts using Torque wrench.
38. 3 Point Locks (Front Single Door) and Cam Locks are Provided (Compartments) for Front Doors.
39. Special Retaining washers are provided for busbar chambers to avoid the falling of the bolts from door.
40. Panel Costing shall include base frame also wherever false floor is proposed.600 mm Base frame to be considered for false floor
41. 45 Deg bending construction to achieve the IP.
42. For viewing MCB Chambers Polycarbonate (Unbreakable & High Temperature withstanding) sheets with glass frames to be used. Incoming Panel Meter should be same as Builder Tap -off Box meter
43. All PVC heat shrinkable sleeves should have temperature withstanding capacity of 105 degree celcius.
44. All ACB & MCCB Power feeders should be connected with Busbars.
Only resin cast C.T of suitable burden, class of accuracy, ratio and voltage shall be used as per the SLD
45. All breakers and energy should have BMS compatibility as per BMS schematic drawing provided.
CPRI certified
1.1 | FLOOR LT PANEL | No. | 1 | 1 | 336995 | 30742 | 336995 | 30742 | 367737
[7 empty] | 0 | 0 | 0
1.2 | WORKSTATION UPS OUTPUT PANEL | No. | 1 | 1 | 106006 | 13176 | 106006 | 13176 | 119182
[7 empty] | 0 | 0 | 0
1.3 | Supply, Installation, testing & commisioning of 160A, 36kA 4P MCCB Tapoff Box with RYB indicating lamps with MCB control & Meter.Tap-off to be fixed to existing rising main. For Cable termination Additional Box to be considered in costing. Existing Rising main make : All standrads to be matched with installed tap-off ratings & quality | No. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
1.4 | Supply, Installation, testing & commisioning of 200A, 36kA 4P MCCB Tapoff Box with RYB indicating lamps with MCB control & Meter.Tap-off to be fixed to existing rising main. For Cable termination Additional Box to be considered in costing. Existing Rising main make : All standrads to be matched with installed tap-off ratings & quality | No. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
1.5 | Supply, Installation, testing & commisioning of 400A, 36kA 4P MCCB Tapoff Box with RYB indicating lamps with MCB control & Meter.Tap-off to be fixed to existing rising main. For Cable termination Additional Box to be considered in costing. Existing Rising main make : All standrads to be matched with installed tap-off ratings & quality | No. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
1.6 | Supply, Installation, testing & commisioning of 630A, 36kA 4P MCCB Tapoff Box with RYB indicating lamps with MCB control & Meter.Tap-off to be fixed to existing rising main. For Cable termination Additional Box to be considered in costing. Existing Rising main make : All standrads to be matched with installed tap-off ratings & quality | No. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
1.7 | Supply, installation, testing & commissioning of 160A 4P MCCB 36KA to existing Builder Main panel . Costing shall include all necessary accessories like indication lamp , Meters , CT & control wiring etc. Vendor should do the site survey for better understanding & clarity. Panel RAL colour & Quality of additional works should match with existing panel.Costing shall include opening of cutout , cable box as per site condition & site survey to be done for any clarification .. Required all costing to be quoted in this line item to complete the works | No. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
1.8 | Supply, installation, testing & commissioning of 250A 4P MCCB 36KA to existing Builder Main panel . Costing shall include all necessary accessories like indication lamp , Meters , CT & control wiring etc. Vendor should do the site survey for better understanding & clarity. Panel RAL colour & Quality of additional works should match with existing panel.Costing shall include opening of cutout , cable box as per site condition & site survey to be done for any clarification .. Required all costing to be quoted in this line item to complete the works | No. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
1.9 | Supply, installation, testing & commissioning of 400A 4P MCCB 36KA to existing Builder Main panel . Costing shall include all necessary accessories like indication lamp , Meters , CT & control wiring etc. Vendor should do the site survey for better understanding & clarity. Panel RAL colour & Quality of additional works should match with existing panel.Costing shall include opening of cutout , cable box as per site condition & site survey to be done for any clarification .. Required all costing to be quoted in this line item to complete the works | No. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
1.1 | Supply, installation, testing & commissioning of 630A 4P MCCB 36KA to existing Builder Main panel . Costing shall include all necessary accessories like indication lamp , Meters , CT & control wiring etc. Vendor should do the site survey for better understanding & clarity. Panel RAL colour & Quality of additional works should match with existing panel.Costing shall include opening of cutout , cable box as per site condition & site survey to be done for any clarification .. Required all costing to be quoted in this line item to complete the works | No. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
1.11 | 63A , 4P MCOS FOR CRITICAL HVAC UNITS | No. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
1.12 | 40A , 4P MCOS FOR CRITICAL HVAC UNITS | No. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
B | Supply, Installation, testing & commisioning of Fully Automatic DOL/ Star Delta starters with features like Local/Remote, Auto/Manual & programmable timer for auto operation. The necessary NO NC shall be provided with BMS compatibility. The space provision for VFD with bypass facility shall be provided wherever it is specified as below. Starters will be used in case of VFD Panel Maintenance/Failure. Starters to be tripped in case of fire, hence necessary contactors for the same to be provided.The cost shall include free standing support for starter Isolator Box | [5 empty] | 0 | 0 | 0
| INDOOR TYPE - IP 52 | [5 empty] | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
1.13 | 0.5 kW DOL Starter | No. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
1.14 | 1.0 kW DOL Starter | No. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
1.15 | 1.5kW DOL Starter | No. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
1.16 | 2.2 kW DOL Starter | No. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
1.17 | 4.4 kW DOL Starter | No. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
1.18 | 5.5kW Star/Delta Starter with VFD Space Provision | No. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
1.19 | 7.5kW Star/Delta Starter with VFD Space Provision | No. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
1.2 | 9.3kW Star/Delta Starter with VFD Space Provision | No. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
1.21 | 11kW Star/Delta Starter with VFD Space Provision | No. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
1.22 | 15kW Star/Delta Starter with VFD Space Provision | No. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
| OUTDOOR TYPE - IP 55 | [5 empty] | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
1.23 | 0.5 kW DOL Starter | No. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
1.24 | 1.0 kW DOL Starter | No. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
1.25 | 1.5kW DOL Starter | No. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
1.26 | 2.2 kW DOL Starter | No. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
1.27 | 4.4 kW DOL Starter | No. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
1.28 | 5.5kW Star/Delta Starter with VFD Space Provision | No. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
1.29 | 7.5kW Star/Delta Starter with VFD Space Provision | No. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
1.3 | 9.3kW Star/Delta Starter with VFD Space Provision | No. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
1.31 | 11kW Star/Delta Starter with VFD Space Provision | No. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
1.32 | 15kW Star/Delta Starter with VFD Space Provision | No. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
C | 4P MCCB BOX wall Mounting type polycarbonate enclosures | [5 empty] | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
| INDOOR TYPE - IP 52 (Ka Rating - 36ka ) | [5 empty] | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
1.33 | 100A | No. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
1.34 | 125A to 160A | No. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
1.35 | 200A to 250A | No. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
1.36 | 400A to 630A(Floor Mounted type) | No. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
1.37 | 800A | No. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
| OUTDOOR TYPE - IP 55 (Ka Rating - 36ka ) | [5 empty] | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
1.38 | 25A to 100A | No. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
1.39 | 125A to 160A | No. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
1.4 | 200A to 250A | No. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
1.41 | 400A to 630A | No. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
1.42 | 800A | No. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
II | LT CABLES & ENDTERMINATIONS | [5 empty] | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
| Supply, Laying, Testing and Commissioning of stranded FRLS XLPE/PVC insulated, Armoured/Unarmoured/Flexible, Aluminum / Copper conductor, laid in tray / hume pipe / in ready made trenches, with nylon cable ties. The cost of the nylon tie shall be included in the cost of installation. | [5 empty] | 0 | 0 | 0
| Cable identification labels at both ends clearly mentioning the cable specs & also at appropriate intervals along the cable route should be provided. The labels shall be engraved / anodized aluminium with white letters on black background. The cost of the Cable identification labels shall be included in the cost of installation & Only heavy duty cable ties should be used for cable dressing. | [5 empty] | 0 | 0 | 0
| Supply, Installation, Testing and Commissioning of double Compression type cable gland, aluminum lugs for aluminum cables / copper lugs for copper cables, insulation tape, anti corrosive paste, brass clamps for gland earthing with 14 SWG copper wire to connect to nearest earth flat. | [5 empty] | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
| Inner sheath: Extruded PVC only for Multicore | [5 empty] | 0 | 0 | 0
| Outer sheath: Extruded Type ST2 PVC with FLAME RETARDANT LESS SMOKE | [5 empty] | 0 | 0 | 0
| Voltage grade:1100Volts | [5 empty] | 0 | 0 | 0
| Armoure: Galvanized Steel strip/Wire for multicore | [5 empty] | 0 | 0 | 0
| Non Magnetic Aluminum Wire/Strip for Single core | [5 empty] | 0 | 0 | 0
| Gland type : Brass with nickel plated | [5 empty] | 0 | 0 | 0
| All Glands used should be of double compression for 35 Sq.mm & Above | [5 empty] | 0 | 0 | 0
| PG glands should be used for copper flexible cables. | [5 empty] | 0 | 0 | 0
| Sealing Ring : Natural rubber for indoor, Neoprene for Outdoor | [5 empty] | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
A | FRLS XLPE Insulated & Steel Armoured Aluminium Conductor Cables | [5 empty] | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
2.1 | 3.5 Core X 400 Sqmm | Mts | RO | RO |  |  | 0 | 0 | 0
2.2 | Endterminations | Nos. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
2.3 | 3.5 Core X 300 Sqmm | Mts | RO | RO |  |  | 0 | 0 | 0
2.4 | Endterminations | Nos. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
2.5 | 3.5 Core X 240 Sqmm | Mts | RO | RO |  |  | 0 | 0 | 0
2.6 | Endterminations | Nos. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
2.7 | 3.5 Core X 185 Sqmm | Mts | RO | RO |  |  | 0 | 0 | 0
2.8 | Endterminations | Nos. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
2.9 | 3.5 Core X 150 Sqmm | Mts | RO | RO |  |  | 0 | 0 | 0
2.1 | Endterminations | Nos. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
2.11 | 3.5 Core X 120 Sqmm | Mts | 160 | 160 | 744 | 89 | 119040 | 14240 | 133280
2.12 | Endterminations | Nos. | 4 | 4 | 1249 | 318 | 4996 | 1272 | 6268
[7 empty] | 0 | 0 | 0
2.13 | 3.5 Core X 95 Sqmm | Mts | RO | RO |  |  | 0 | 0 | 0
2.14 | Endterminations | Nos. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
2.15 | 3.5 Core X 70 Sqmm | Mts | RO | RO |  |  | 0 | 0 | 0
2.16 | Endterminations | Nos. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
2.17 | 3.5 Core X 50 Sqmm | Mts | RO | RO |  |  | 0 | 0 | 0
2.18 | Endterminations | Nos. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
2.19 | 3.5 Core X 35 Sqmm | Mts | RO | RO |  |  | 0 | 0 | 0
2.2 | Endterminations | Nos. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
2.21 | 4 Core X 25 Sqmm | Mts | RO | RO |  |  | 0 | 0 | 0
2.22 | Endterminations | Nos. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
2.23 | 4 Core X 16 Sqmm | Mts | 250 | 250 | 177 | 37 | 44250 | 9250 | 53500
2.24 | Endterminations | Nos. | 10 | 10 | 116 | 37 | 1160 | 370 | 1530
[7 empty] | 0 | 0 | 0
2.25 | 4 Core X 10 Sqmm | Mts | RO | RO |  |  | 0 | 0 | 0
2.26 | Endterminations | Nos. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
2.27 | 4 Core X 6 Sqmm | Mts | RO | RO |  |  | 0 | 0 | 0
2.28 | Endterminations | Nos. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
2.29 | 4 Core X 4 Sqmm | Mts | RO | RO |  |  | 0 | 0 | 0
2.3 | Endterminations | Nos. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
2.31 | 4 Core X 2.5 Sqmm | Mts | RO | RO |  |  | 0 | 0 | 0
2.32 | Endterminations | Nos. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
2.33 | 4 Core X 1.5 Sqmm | Mts | RO | RO |  |  | 0 | 0 | 0
2.34 | Endterminations | Nos. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
2.35 | 3 Core X 10 Sqmm | Mts | RO | RO |  |  | 0 | 0 | 0
2.36 | Endterminations | Nos. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
2.37 | 3 Core X 6 Sqmm | Mts | RO | RO |  |  | 0 | 0 | 0
2.38 | Endterminations | Nos. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
2.39 | 3 Core X 4 Sqmm | Mts | RO | RO |  |  | 0 | 0 | 0
2.4 | Endterminations | Nos. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
2.41 | 3 Core X 2.5 Sqmm | Mts | RO | RO |  |  | 0 | 0 | 0
2.42 | Endterminations | Nos. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
2.43 | 3 Core X 1.5 Sqmm | Mts | RO | RO |  |  | 0 | 0 | 0
2.44 | Endterminations | Nos. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
B | FRLS PVC Insulated & Un Armoured Copper Conductor cables (YY Type) - IS 694 | [5 empty] | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
2.45 | 1 Core x 400 Sq. mm | Mts | RO | RO |  |  | 0 | 0 | 0
2.46 | Endterminations | Nos. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
2.47 | 1 Core x 300 Sq. mm | Mts | RO | RO |  |  | 0 | 0 | 0
2.48 | Endterminations | Nos. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
2.49 | 1 Core x 240 Sq. mm | Mts | RO | RO |  |  | 0 | 0 | 0
2.5 | Endterminations | Nos. |  |  |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
2.51 | 1 Core x 185 Sq. mm | Mts | RO | RO |  |  | 0 | 0 | 0
2.52 | Endterminations | Nos. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
2.53 | 1 Core x 150 Sq. mm | Mts | RO | RO |  |  | 0 | 0 | 0
2.54 | Endterminations | Nos. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
2.55 | 1 Core x 120 Sq. mm | Mts | RO | RO |  |  | 0 | 0 | 0
2.56 | Endterminations | Nos. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
2.57 | 1 Core x 95 Sq. mm | Mts | RO | RO |  |  | 0 | 0 | 0
2.58 | Endterminations | Nos. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
2.59 | 1 Core x 70 Sq. mm | Mts | RO | RO |  |  | 0 | 0 | 0
2.6 | Endterminations | Nos. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
2.61 | 1 Core x 50 Sq. mm | Mts | RO | RO |  |  | 0 | 0 | 0
2.62 | Endterminations | Nos. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
2.63 | 1 Core x 35 Sq. mm | Mts | RO | RO |  |  | 0 | 0 | 0
2.64 | Endterminations | Nos. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
2.65 | 1 Core x 25 Sq. mm | Mts | RO | RO |  |  | 0 | 0 | 0
2.66 | Endterminations | Nos. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
2.67 | 1 Core x 16 Sq. mm | Mts | 225 | 225 | 283 | 29 | 63675 | 6525 | 70200
2.68 | Endterminations | Nos. | 18 | 18 | 73 | 19 | 1314 | 342 | 1656
[7 empty] | 0 | 0 | 0
2.69 | 1 Core x 10 Sq. mm | Mts | 225 | 225 | 187 | 29 | 42075 | 6525 | 48600
2.7 | Endterminations | Nos. | 18 | 18 | 73 | 19 | 1314 | 342 | 1656
[7 empty] | 0 | 0 | 0
2.71 | 1 Core x 6 Sq. mm | Mts | RO | RO |  |  | 0 | 0 | 0
2.72 | Endterminations | Nos. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
2.73 | 1 Core x 4 Sq. mm | Mts | 150 | 150 | 73 | 19 | 10950 | 2850 | 13800
2.74 | Endterminations | Nos. | 12 | 12 | 63 | 19 | 756 | 228 | 984
[7 empty] | 0 | 0 | 0
2.75 | 1 Core x 2.5 Sq. mm | Mts | RO | RO |  |  | 0 | 0 | 0
2.76 | Endterminations | Nos. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
2.77 | 1 Core x 1.5 Sq. mm | Mts | RO | RO |  |  | 0 | 0 | 0
2.78 | Endterminations | Nos. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
2.79 | 3 Core x 10Sq. mm | Mts | RO | RO |  |  | 0 | 0 | 0
2.8 | Endterminations | Nos. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
2.81 | 3 Core x 6 Sq. mm | Mts | RO | RO |  |  | 0 | 0 | 0
2.82 | Endterminations | Nos. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
2.83 | 3 Core x 4 Sq. mm | Mts | RO | RO |  |  | 0 | 0 | 0
2.84 | Endterminations | Nos. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
2.85 | 3 Core x 2.5 Sq. mm | Mts | RO | RO |  |  | 0 | 0 | 0
2.86 | Endterminations | Nos. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
2.87 | 3 Core x 1.5 Sq. mm | Mts | RO | RO |  |  | 0 | 0 | 0
2.88 | Endterminations | Nos. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
2.89 | 4 Core x 10 Sq. mm | Mts | RO | RO |  |  | 0 | 0 | 0
2.9 | Endterminations | Nos. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
2.91 | 4 Core x 6 Sq. mm | Mts | RO | RO |  |  | 0 | 0 | 0
2.92 | Endterminations | Nos. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
2.93 | 5 Core x 6 Sq. mm | Mts | RO | RO |  |  | 0 | 0 | 0
2.94 | Endterminations | Nos. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
2.95 | 5 Core x 10 Sq. mm | Mts | RO | RO |  |  | 0 | 0 | 0
2.96 | Endterminations | Nos. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
2.97 | 5 Core x 25 Sq. mm | Mts | RO | RO |  |  | 0 | 0 | 0
2.98 | Endterminations | Nos. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
2.99 | 5 Core x 16 Sq. mm | Mts | RO | RO |  |  | 0 | 0 | 0
2.1 | Endterminations | Nos. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
C | FRLS PVC Insulated & Steel Armoured Copper Conductor cables (YFY Type) | [5 empty] | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
2.101 | 3 Core x 10 Sq. mm | Mts | RO | RO |  |  | 0 | 0 | 0
2.102 | Endterminations | Nos. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
2.103 | 3 Core x 6 Sq. mm | Mts | 160 | 160 | 349 | 29 | 55840 | 4640 | 60480
2.104 | Endterminations | Nos. | 8 | 8 | 73 | 19 | 584 | 152 | 736
[7 empty] | 0 | 0 | 0
2.105 | 3 Core x 4 Sq. mm | Mts | 30 | 30 | 244 | 29 | 7320 | 870 | 8190
2.106 | Endterminations | Nos. | 2 | 2 | 63 | 19 | 126 | 38 | 164
[7 empty] | 0 | 0 | 0
2.107 | 3 Core x 2.5 Sq. mm | Mts | RO | RO |  |  | 0 | 0 | 0
2.108 | Endterminations | Nos. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
2.109 | 3 Core x 1.5 Sq. mm | Mts | RO | RO |  |  | 0 | 0 | 0
2.11 | Endterminations | Nos. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
2.111 | 4 Core x 25 Sq. mm | Mts | RO | RO |  |  | 0 | 0 | 0
2.112 | Endterminations | Nos. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
2.113 | 4 Core x 16 Sq. mm | Mts | 70 | 70 | 1090 | 37 | 76300 | 2590 | 78890
2.114 | Endterminations | Nos. | 6 | 6 | 125 | 37 | 750 | 222 | 972
[7 empty] | 0 | 0 | 0
2.115 | 4 Core x 10 Sq. mm | Mts | 40 | 40 | 739 | 29 | 29560 | 1160 | 30720
2.116 | Endterminations | Nos. | 4 | 4 | 89 | 29 | 356 | 116 | 472
[7 empty] | 0 | 0 | 0
2.117 | 4 Core x 6 Sq. mm | Mts | RO | RO |  |  | 0 | 0 | 0
2.118 | Endterminations | Nos. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
2.119 | 4 Core x 4 Sq. mm | Mts | RO | RO |  |  | 0 | 0 | 0
2.12 | Endterminations | Nos. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
2.121 | 4 Core x 2.5 Sq. mm | Mts | RO | RO |  |  | 0 | 0 | 0
2.122 | Endterminations | Nos. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
| TOTAL FOR LT CABLES & ENDTERMINATIONS | [5 empty] | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
III | MCB DISTRIBUTION BOARDS (DB) | [5 empty] | 0 | 0 | 0
| Supply, Installation, Testing and Commissioning of MCB Distribution board as per approved installation drawings. | [5 empty] | 0 | 0 | 0
| Wall mounted MCB DBs with MS wire way box on top / bottom & on sides. MCBs shall be rated for 10kA with current limiting feature. Dummy ways to be covered with blank plates. All out going ways shall be labeled & laminated. | [5 empty] | 0 | 0 | 0
| Enclosure:1.2mm CRCA Sheet Steel, Powder Coated | [5 empty] | 0 | 0 | 0
| Door : Double Door | [5 empty] | 0 | 0 | 0
| Protection : IP 43 | [5 empty] | 0 | 0 | 0
| Cable Entry : Top & Bottom | [5 empty] | 0 | 0 | 0
| For UPS distribution RCCB's shall be harmonic resistant (HI/SI Series) | [5 empty] | 0 | 0 | 0
| Bus bar : Shall be tinned Copper and 200% rating for UPS DB Neutral Link | [5 empty] | 0 | 0 | 0
| MCB's : C Curve for Lighting & Raw power, 'D' Curve for UPS Distribution | [5 empty] | 0 | 0 | 0
| Note: | [5 empty] | 0 | 0 | 0
| 1) Separate Earth bus/Neutral bus for each phase | [5 empty] | 0 | 0 | 0
| 2) Each Circuit shall have yellow ferrules with circuit number on both sides | [5 empty] | 0 | 0 | 0
| 3) Accessories required for installation of DB's on Wall/Column/Gyp Board shall be considered | [5 empty] | 0 | 0 | 0
| 4) DB's shall be covered with powder coated (paint should match with DB Color) wire ways all around and up to ceiling to receive incoming circuits. Refer DB frame details. | [5 empty] | 0 | 0 | 0
| 5) Laminated A3 OR A4 size SLD shall be pasted inside DB door | [5 empty] | 0 | 0 | 0
| 6) Safe shroud for Neutral link shall be provided | [5 empty] | 0 | 0 | 0
| 7. All DBs shall be of 7 segment type ( Single Phase DB discription to be added seperately ) & Consider flexitier DB wherever 7 segment type is not matching | [5 empty] | 0 | 0 | 0
| 8) In All DBs Incomer TVSS /Surge protection of 2.5Kv to be Provided | [5 empty] | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
A | HUB Room UDB's : | [5 empty] | 0 | 0 | 0
3.1 | 4 Way SPN MCB DB | [5 empty] | 0 | 0 | 0
| Incomer : 1Nos 40 A DP RCCB with 100mA | [5 empty] | 0 | 0 | 0
| Outgoing : 4 Nos. 32A SP MCB of 'D' curve | No. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
3.2 | 4 Way TPN MCB DB | [5 empty] | 0 | 0 | 0
| 'Incomer : 1No. 63A 4P, MCB | [5 empty] | 0 | 0 | 0
| Subincomer : 3Nos 63 A DP RCCB with 100mA | [5 empty] | 0 | 0 | 0
| Outgoing : 12 Nos. 40A SP MCB of 'D' curve | No. | 2 | 2 | 14116 | 1122 | 28232 | 2244 | 30476
[7 empty] | 0 | 0 | 0
3.3 | 6 Way TPN MCB DB | [5 empty] | 0 | 0 | 0
| 'Incomer : 1No. 63A 4P, MCB | [5 empty] | 0 | 0 | 0
| Subincomer : 3Nos 63 A DP RCCB with 100mA | [5 empty] | 0 | 0 | 0
| Outgoing : 18 Nos. 32A SP MCB of 'D' curve | No. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
3.4 | 8 Way TPN MCB DB | [5 empty] | 0 | 0 | 0
| 'Incomer : 1No. 63A 4P, MCB | [5 empty] | 0 | 0 | 0
| Subincomer : 3Nos 63 A DP RCCB with 100mA | [5 empty] | 0 | 0 | 0
| Outgoing : 24 Nos. 32A SP MCB of 'D' curve | No. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
3.5 | 12 Way TPN MCB DB | [5 empty] | 0 | 0 | 0
| 'Incomer : 1No. 63A 4P, MCB | [5 empty] | 0 | 0 | 0
| Subincomer : 3Nos 63 A DP RCCB with 100mA | [5 empty] | 0 | 0 | 0
| Outgoing : 36 Nos. 32A SP MCB of 'D' curve | No. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
B | LDB | [5 empty] | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
3.6 | 8 Way SPN MCB DB | [5 empty] | 0 | 0 | 0
| Incomer : 1Nos 40A DP 30mA RCCB | [5 empty] | 0 | 0 | 0
| Outgoing : 8 Nos. 10A SP MCB of 'C' curve | No. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
3.7 | 6 Way TPN MCB DB | [5 empty] | 0 | 0 | 0
| Incomer : 1No. 63A, 4P, MCB | [5 empty] | 0 | 0 | 0
| Sub incomer :3Nos 40A DP 30mA RCCB | [5 empty] | 0 | 0 | 0
| Outgoing : 18 Nos. 10A SP MCB of 'C' curve | No. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
3.8 | 8 Way TPN MCB DB | [5 empty] | 0 | 0 | 0
| Incomer : 1No. 63A, 4P, MCB | [5 empty] | 0 | 0 | 0
| Sub incomer :3Nos 40A DP 30mA RCCB | [5 empty] | 0 | 0 | 0
| Outgoing : 24 Nos. 10A SP MCB of 'C' curve | No. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
3.9 | 12 Way TPN MCB DB | [5 empty] | 0 | 0 | 0
| Incomer : 1No. 63A, 4P, MCB | [5 empty] | 0 | 0 | 0
| Sub incomer :3Nos 40A DP 30mA RCCB | [5 empty] | 0 | 0 | 0
| Outgoing : 36 Nos. 10A SP MCB of 'C' curve | No. | 1 | 1 | 19386 | 1319 | 19386 | 1319 | 20705
[7 empty] | 0 | 0 | 0
C | ELDB's : | [5 empty] | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
3.1 | 6 Way SPN MCB DB | [5 empty] | 0 | 0 | 0
| Incomer : 1No. 40A DP 30mA RCCB | [5 empty] | 0 | 0 | 0
| Outgoing : 6 Nos. 10A SP MCB of 'D' curve | No. | 1 | 1 | 4649 | 660 | 4649 | 660 | 5309
[7 empty] | 0 | 0 | 0
3.11 | 8 Way SPN MCB DB | [5 empty] | 0 | 0 | 0
| Incomer : 1No. 40A DP 30mA RCCB | [5 empty] | 0 | 0 | 0
| Outgoing : 8 Nos. 10A SP MCB of 'D' curve | No. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
3.12 | 12 Way SPN MCB DB | [5 empty] | 0 | 0 | 0
| Sub Incomer : 1No. 40A DP 30mA RCCB | [5 empty] | 0 | 0 | 0
| Outgoing : 12 Nos. 10A SP MCB of 'D' curve | No. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
3.13 | 4Way TPN MCB DB | [5 empty] | 0 | 0 | 0
| Incomer : 1No. 32A, 4P, MCB | [5 empty] | 0 | 0 | 0
| Sub Incomer : 1No. 25A DP 30mA RCCB | [5 empty] | 0 | 0 | 0
| Outgoing : 12 Nos. 10A SP MCB of 'D' curve | No. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
3.14 | 6Way TPN MCB DB | [5 empty] | 0 | 0 | 0
| Incomer : 1No. 40A, 4P, MCB | [5 empty] | 0 | 0 | 0
| Sub Incomer : 1No. 32A DP 30mA RCCB | [5 empty] | 0 | 0 | 0
| Outgoing : 18 Nos. 10A SP MCB of 'D' curve | No. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
3.15 | 8Way TPN MCB DB | [5 empty] | 0 | 0 | 0
| Incomer : 1No. 63A, 4P, MCB | [5 empty] | 0 | 0 | 0
| Sub Incomer : 1No. 40A DP 30mA RCCB | [5 empty] | 0 | 0 | 0
| Outgoing : 24 Nos. 10A SP MCB of 'D' curve | No. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
3.16 | 12Way TPN MCB DB | [5 empty] | 0 | 0 | 0
| Incomer : 1No. 40A, 4P, MCB | [5 empty] | 0 | 0 | 0
| Sub incomer : 3Nos 32A DP 30mA RCCB | [5 empty] | 0 | 0 | 0
| Outgoing : 36 Nos. 10A SP MCB of 'D' curve | No. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
D | UDB's : | [5 empty] | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
3.17 | 4Way TPN MCB DB | [5 empty] | 0 | 0 | 0
| Incomer : 1No. 63A 4P, MCB | [5 empty] | 0 | 0 | 0
| Sub incomer 3Nos 40 A DP RCCB with 100mA | [5 empty] | 0 | 0 | 0
| Outgoing :12. Nos. 16A SP MCB of 'D' curve | No. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
3.18 | 6 Way TPN MCB DB | [5 empty] | 0 | 0 | 0
| Incomer : 1No. 63A 4P, MCB | [5 empty] | 0 | 0 | 0
| Sub incomer 3Nos 40 A DP RCCB with 100mA | [5 empty] | 0 | 0 | 0
| Outgoing : 18. Nos. 16A SP MCB of 'D' curve | No. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
3.19 | 8 Way TPN MCB DB | [5 empty] | 0 | 0 | 0
| Incomer : 1No. 63A 4P, MCB | [5 empty] | 0 | 0 | 0
| Sub incomer 3Nos 40 A DP RCCB with 100mA | [5 empty] | 0 | 0 | 0
| Outgoing : 24. Nos. 16A SP MCB of 'D' curve | No. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
3.2 | 12 Way TPN MCB DB | [5 empty] | 0 | 0 | 0
| Incomer : 1No. 63A 4P, MCB | [5 empty] | 0 | 0 | 0
| Sub incomer 3Nos 63 A DP RCCB with 100mA | [5 empty] | 0 | 0 | 0
| Outgoing : 36 Nos. 16A SP MCB of 'D' curve | No. | 2 | 2 | 23400 | 1319 | 46800 | 2638 | 49438
[7 empty] | 0 | 0 | 0
E | RDB's : | [5 empty] | 0 | 0 | 0
3.21 | 12Way SPN MCB DB | [5 empty] | 0 | 0 | 0
| Incomer : 1No. 40 A DP RCCB with 100mA | [5 empty] | 0 | 0 | 0
| Outgoing : 12 Nos. 16A SP MCB of 'C' curve | No. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
3.22 | 4Way TPN MCB DB | [5 empty] | 0 | 0 | 0
| Incomer : 1No. 63A 4P, MCB | [5 empty] | 0 | 0 | 0
| Sub incomer 3Nos 40 A DP RCCB with 100mA | [5 empty] | 0 | 0 | 0
| Outgoing : 12 Nos. 16A SP MCB of 'C' curve | No. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
3.23 | 6 Way TPN MCB DB | [5 empty] | 0 | 0 | 0
| Incomer : 1No. 63A 4P, MCB | [5 empty] | 0 | 0 | 0
| Sub incomer 3Nos 40 A DP RCCB with 100mA | [5 empty] | 0 | 0 | 0
| Outgoing : 18 Nos. 16A SP MCB of 'C' curve | No. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
3.24 | 8 Way TPN MCB DB | [5 empty] | 0 | 0 | 0
| Incomer : 1No. 63A 4P, MCB | [5 empty] | 0 | 0 | 0
| Sub incomer 3Nos 63 A DP RCCB with 100mA | [5 empty] | 0 | 0 | 0
| Outgoing : 24 Nos. 16A SP MCB of 'C' curve | No. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
3.25 | 12 Way TPN MCB DB | [5 empty] | 0 | 0 | 0
| Incomer : 1No. 63A 4P, MCB | [5 empty] | 0 | 0 | 0
| Sub incomer 3Nos 63 A DP RCCB with 100mA | [5 empty] | 0 | 0 | 0
| Outgoing : 36 Nos. 16A SP MCB of 'C' curve | No. | 2 | 2 | 21187 | 1319 | 42374 | 2638 | 45012
[7 empty] | 0 | 0 | 0
F | VAV , FD & HVAC DB's : | [5 empty] | 0 | 0 | 0
3.26 | 8 Way SPN MCB DB | [5 empty] | 0 | 0 | 0
| Incomer : 1Nos 40 A DP RCCB with 100mA | [5 empty] | 0 | 0 | 0
| Outgoing : 8 Nos. 16A SP MCB of 'D' curve | No. | 1 | 1 | 5457 | 660 | 5457 | 660 | 6117
[7 empty] | 0 | 0 | 0
3.26 | 8 Way TPN MCB DB (VAV & FIRE DAMPER ) | [5 empty] | 0 | 0 | 0
| Incomer : 1No. 32A 4P, MCB | [5 empty] | 0 | 0 | 0
| Sub incomer 3Nos 25 A DP RCCB with 100mA | [5 empty] | 0 | 0 | 0
| Outgoing : 24 Nos. 16A SP MCB of 'D' curve | No. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
3.27 | 12 Way TPN MCB DB (VAV & FIRE DAMPER ) | [5 empty] | 0 | 0 | 0
| Incomer : 1No. 40A 4P, MCB | [5 empty] | 0 | 0 | 0
| Sub incomer 3Nos 40 A DP RCCB with 100mA | [5 empty] | 0 | 0 | 0
| Outgoing : 36 Nos. 16A SP MCB of 'D' curve | No. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
G | 4P MCB BOX with Polycarbonate enclosures (Indoor - IP 52) | [5 empty] | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
3.28 | 6A to 32A | No. | 4 | 4 | 1583 | 239 | 6332 | 956 | 7288
[7 empty] | 0 | 0 | 0
3.29 | 40A to 63A | No. | 2 | 2 | 2084 | 318 | 4168 | 636 | 4804
[7 empty] | 0 | 0 | 0
| 4P MCB BOX with Polycarbonate enclosures (Outdoor - IP 55) | [5 empty] | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
3.3 | 6A to 32A | No. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
3.31 | 40A to 63A | No. | 1 | 1 | 2084 | 318 | 2084 | 318 | 2402
[7 empty] | 0 | 0 | 0
| 4P RCBO - AC Series 100ma - with Polycarbonate enclosures (Indoor - IP 52) | [5 empty] | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
3.32 | 6A to 32A | No. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
3.33 | 40A to 63A | No. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
| 4P RCBO - AC Series 100ma - with Polycarbonate enclosures (Indoor - IP 55) | [5 empty] | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
3.34 | 6A to 32A | No. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
3.35 | 40A to 63A | No. | 2 | 2 | 4762 | 722 | 9524 | 1444 | 10968
[7 empty] | 0 | 0 | 0
3.36 | Providing 2 MODULE Metal back box for Data socket outlets in the WALL/floor. | Nos. | 10 | 10 | 46 | 10 | 460 | 100 | 560
[7 empty] | 0 | 0 | 0
3.37 | Providing 3 MODULE Metal back box for Data socket outlets in the WALL/floor. | Nos. | 5 | 5 | 55 | 19 | 275 | 95 | 370
[7 empty] | 0 | 0 | 0
3.38 | Providing 2 MODULE PVC back box for Data socket outlets in the WALL/floor. | Nos. | 10 | 10 | 46 | 10 | 460 | 100 | 560
[7 empty] | 0 | 0 | 0
3.39 | Providing 3 MODULE PVC back box for Data socket outlets in the WALL/floor. | Nos. | 2 | 2 | 55 | 19 | 110 | 38 | 148
[7 empty] | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
IV | CIRCUIT MAINS FOR POWER CIRCUITS | [5 empty] | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
| Supply, Installation, Testing and Commissioning of Circuit mains using 1.1kV grade FRLS PVC insulated PVC round sheathed single/multicore core flexible cables drawn in existing conduit or raceway. Circuit mains shall be measured from respective DB to the nearest socket board & looping circuit also be measured in running Mtr. All circuit terminations shall be provided with solder less crimping type copper sockets / lugs, ferrules indicating source code on load side & load code on source side. There shall not be any joints in the circuits, only looping is allowed in terminal blocks/connectors costing shall include terminal blocks/connectors if any & in switches / Sensors/ socket outlets. Kindly refer IS 694:1990. | [5 empty] | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
| Colour codes to be followed as below | [5 empty] | 0 | 0 | 0
| Raw power Circuits - BLACK | [5 empty] | 0 | 0 | 0
| UPS power circuits - WHITE | [5 empty] | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
4.1 | UPS / RP/AV&TV Circuit: | [5 empty] | 0 | 0 | 0
| Supply, Installation, Testing and Commissioning of 3 C x 2.5 Sqmm FRLS 1100V PVC double insulated flexible multicore cable in existing conduits/raceways. | Mts. | 3050 | 3050 | 140 | 29 | 427000 | 88450 | 515450
[7 empty] | 0 | 0 | 0
4.2 | UPS / RP/AV&TV looping: | [5 empty] | 0 | 0 | 0
| Supply, Installation, Testing and Commissioning of 3 C x 2.5 Sqmm FRLS 1100V PVC double insulated flexible multicore cable in existing conduits/raceways. | Mts. | 2600 | 2600 | 140 | 29 | 364000 | 75400 | 439400
[7 empty] | 0 | 0 | 0
4.3 | SERVER POWER CIRCUIT | [5 empty] | 0 | 0 | 0
| Supply, Installation, Testing and Commissioning of 3 C x 4 Sqmm FRLS 1100V PVC double insulated flexible multicore cable in existing conduits/raceways. | Mts. | 100 | 100 | 217 | 29 | 21700 | 2900 | 24600
[7 empty] | 0 | 0 | 0
4.4 | RAW POWER CIRCUIT :Pantry/Micro kitchen | [5 empty] | 0 | 0 | 0
| Supply, Installation, Testing and Commissioning of 3 C x 6 Sqmm FRLS 1100V PVC double insulated flexible multicore cable in existing conduits/raceways. | Mts. | 100 | 100 | 318 | 29 | 31800 | 2900 | 34700
[7 empty] | 0 | 0 | 0
4.5 | VAV & FIRE EXIT SINAGES Circuit & looping: | [5 empty] | 0 | 0 | 0
| Supply, Installation, Testing and Commissioning of 3Cx1.5sqmm FRLS 1100V PVC double insulated flexible multicore cable in in existing conduits/raceways. | Mts. | 620 | 620 | 89 | 19 | 55180 | 11780 | 66960
[7 empty] | 0 | 0 | 0
4.6 | Supply & Installation , Testing and Commissioning of male connector of weiland make or equivalent make | Nos. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
4.7 | Supply & Installation , Testing and Commissioning of female connector of weiland make or equivalent make | Nos. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
4.8 | Supply & Installation , Testing and Commissioning of 1 in 2 out connector of weiland make or equivalent make | Nos. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
4.9 | Supply & Installation , Testing and Commissioning of 1 in 3 out connector of weiland make or equivalent make | Nos. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
4.1 | Supply & Installation , Testing and Commissioning of 1 in 5 out connector of weiland make or equivalent make | Nos. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
V | CIRCUIT MAINS & POINT WIRING FOR LIGHT FIXTURES | [5 empty] | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
A | POINT WIRING - Switch controls | [5 empty] | 0 | 0 | 0
| Supply, Installation, Testing and Commissioning of 3 C x 1.5 Sqmm FRLS 1100V PVC double insulated flexible multicore cable in multicore cable in Existing conduits/Raceways. The wiring shall be complete with ceiling roses, switches ,Modular Boxes and all consumables.All circuit terminations shall be provided with solder less crimping type copper sockets / lugs, ferrules indicating source code on load side & load code on source side. There shall not be any joints in the circuits, only looping is allowed in terminal blocks & in switches / Sensors/ socket outlets. Kindly refer IS 694:1990. | [5 empty] | 0 | 0 | 0
| Colour codes to be followed as below | [5 empty] | 0 | 0 | 0
| Lighting Circuits - Grey | [5 empty] | 0 | 0 | 0
| Emergency Lighting Circuits - Black | [5 empty] | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
5.1 | PRIMARY LIGHT POINT- Vendor to calculate the length based on the lighting layout & quote accordingly | [5 empty] | 0 | 0 | 0
| Primary light point means wiring from DB to first switch Point/Sensors & first switch point/Sensors to the first light fixture . The switch and all necessary accessories would be part of primary point & The cost shall also include sub-circuit if it is drawn from adjacent switch box/sensors | Nos. | 5 | 5 | 2680 | 538 | 13400 | 2690 | 16090
[7 empty] | 0 | 0 | 0
5.2 | SECONDARY LIGHT POINT - Vendor to calculate the length based on the lighting layout & quote accordingly | [5 empty] | 0 | 0 | 0
| Secondary light point means extention of light outlet from existing primary point. Same to be controlled by the existing switch/Sensors of primary point & the cost shall include Ceiling flexible conduit shall be included at the drop of light fixture. | Nos. | 60 | 60 | 424 | 89 | 25440 | 5340 | 30780
[7 empty] | 0 | 0 | 0
B | POINT WIRING - MCB Control | [5 empty] | 0 | 0 | 0
| Supply, Installation, Testing and Commissioning of 3 C x 1.5 Sqmm FRLS 1100V PVC double insulated flexible multicore cable in Existing conduits/Raceways. The wiring shall be complete with ceiling roses, switches ,Modular Boxes and all consumables.All circuit terminations shall be provided with solder less crimping type copper sockets / lugs, ferrules indicating source code on load side & load code on source side. There shall not be any joints in the circuits, only looping is allowed in terminal blocks & in switches / Sensors/ socket outlets. Kindly refer IS 694:1990. | [5 empty] | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
5.3 | PRIMARY LIGHT POINT - Vendor to calculate the length based on the lighting layout & quote accordingly | [5 empty] | 0 | 0 | 0
| Primary light point means wiring from DB to first light point. The cost shall include Ceiling flexible conduit at the drop of light fixture. | Nos. | 8 | 8 | 1688 | 344 | 13504 | 2752 | 16256
[7 empty] | 0 | 0 | 0
5.4 | SECONDARY LIGHT POINT - Vendor to calculate the length based on the lighting layout & quote accordingly | [5 empty] | 0 | 0 | 0
| Secondary light point means extention of light outlet from existing primary point. The cost shall include Ceiling flexible conduit at the drop of light fixture. | Nos. | 90 | 90 | 424 | 89 | 38160 | 8010 | 46170
[7 empty] | 0 | 0 | 0
C | POINT WIRING - Sensor Control | [5 empty] | 0 | 0 | 0
| Supply, Installation, Testing and Commissioning of 3 C x 1.5 Sqmm FRLS 1100V PVC double insulated flexible multicore cable in multicore cable in Existing conduits/Raceways. The wiring shall be complete with ceiling roses, switches ,Modular Boxes and all consumables.All circuit terminations shall be provided with solder less crimping type copper sockets / lugs, ferrules indicating source code on load side & load code on source side. There shall not be any joints in the circuits, only looping is allowed in terminal blocks & in switches / Sensors/ socket outlets. Kindly refer IS 694:1990. | [5 empty] | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
5.5 | PRIMARY LIGHT POINT - Vendor to calculate the length based on the lighting layout & quote accordingly | [5 empty] | 0 | 0 | 0
| Primary light point means wiring from DB to first light point. The cost shall include Ceiling flexible conduit at the drop of light fixture. | Nos. | 22 | 22 | 2680 | 538 | 58960 | 11836 | 70796
[7 empty] | 0 | 0 | 0
5.6 | SECONDARY LIGHT POINT- Vendor to calculate the length based on the lighting layout & quote accordingly | [5 empty] | 0 | 0 | 0
| Secondary light point means extention of light outlet from existing primary point. The cost shall include Ceiling flexible conduit at the drop of light fixture. | Nos. | 250 | 250 | 424 | 89 | 106000 | 22250 | 128250
[7 empty] | 0 | 0 | 0
D | Supply, Installation, Testing and Commissioning of of following size 2mm thick rigid GI conduits & accessories fixing in ceiling/wall/Parition etc | [5 empty] | 0 | 0 | 0
5.7 | 32mm dia | Mts. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
5.8 | 25mm dia | Mts. | 1400 | 1400 | 120 | 24 | 168000 | 33600 | 201600
[7 empty] | 0 | 0 | 0
5.9 | 20mm dia | Mts. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
5.1 | Supply , Installation, Testing and Commissioning of recess mounted Occupancy Sensor having coverage area of 400Sq.ft for a mounting height of 2.8Mtr & PIR Technology. | Nos. | 30 | 30 | 2637 | 441 | 79110 | 13230 | 92340
[7 empty] | 0 | 0 | 0
5.11 | Supply , Installation, Testing and Commissioning of recess mounted dimmable/ Day light Occupancy Sensor having coverage area of 400Sq.ft for a mounting height of 2.8Mtr & PIR Technology. | Nos. | 12 | 12 | 2637 | 441 | 31644 | 5292 | 36936
[7 empty] | 0 | 0 | 0
5.12 | Supply & Installation of supports for sensors . Costig shall include all necessary supports to complete the same. Sample approval to be taken before installation & colour of the supports should match architect intent .. Costing shall include painting works & height adjustable for the supports as per the site requirement | Nos. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
5.13 | Supply, Installation, Testing and Commissioning of 2 channel DALI module The module is DIN rail or direct mountable. Each channel should be capable of handling 64 adre4sses and 16 zones. (Board Room) | Nos. | 1 | 1 | 60385 | 13176 | 60385 | 13176 | 73561
[7 empty] | 0 | 0 | 0
5.14 | Supply, Installation, Testing and Commissioning of QS sensor module to communicate with wireless occupancy sensor and wireless keypads. This module is mounted in the ceiling. This is connected to 0-10V module using 4C X 1.5 sqmm wire. (Board Room) | Nos. | 1 | 1 | 6040 | 441 | 6040 | 441 | 6481
[7 empty] | 0 | 0 | 0
5.15 | Supply, Installation, Testing and Commissioning of 6 button with raise & lower wall mounted wired / wireless keypad with white finish. No back box should be required for the same and should be mountable on any surface. No sperate power 230V power supply should be required for this keypad. (Board Room) | Nos. | 2 | 2 | 10432 | 2198 | 20864 | 4396 | 25260
[7 empty] | 0 | 0 | 0
5.16 | Supply, Installation, Testing and Commissioning of Wireless Ceiling mounted Occupancy dimmable Sensor with radio frequency and connect with relay or 0-10v module wirelessly. The sensors should not interfere with any other wireless devices. (Board Room) | Nos. | 4 | 4 | 6040 | 441 | 24160 | 1764 | 25924
[7 empty] | 0 | 0 | 0
5.17 | Supply, Installation, Testing and Commissioning of Network interface versatile integration access point for Lutron’s QS-based systems. Through either RS232 or TCP/IP over Ethernet, third-party devices can control and/or monitor a QS system. Easily integrate with touchscreens, PCs, A/V systems, or other digital systems and devices. | Nos. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
5.18 | QS cable for power and data simialr to Lutron QS-CBL-LSZH Cable Adheres to CE standards for Low Smoke Generation (EN 60332-1-2), Halogen Gas Emission (EN 61034-2), and Flame Retardation (EN 60754-1&2). • Five Conductors: Common – 0.75 mm2 (18 AWG) Power – 0.75 mm2 (18 AWG) MUX Data – 0.25 mm2 (22 AWG) _ Data – 0.25 mm2 (22 AWG) Drain Wire – 0.2 mm2 (24 AWG) (Board Room) | Mtrs | 100 | 100 | 449 | 55 | 44900 | 5500 | 50400
[7 empty] | 0 | 0 | 0
5.19 | Supply, Installation, Testing and Commissioning of 2Cx1.5sqmm FRLS 1100V PVC double insulated flexible multicore cable drawn in existing conduit of approved make. (Board Room) | Mtrs | 120 | 120 | 94 | 32 | 11280 | 3840 | 15120
[7 empty] | 0 | 0 | 0
5.2 | Supply, Installation, Testing and Commissioning of Power supply unit (Board Room) | Nos. | 1 | 1 | 3955 | 441 | 3955 | 441 | 4396
[7 empty] | 0 | 0 | 0
5.21 | Supply, Installation, Testing and Commissioning of LMS System (Board Room) | Nos. | 1 | 1 | 0 | 30742 | 0 | 30742 | 30742
[7 empty] | 0 | 0 | 0
5.22 | Supply, Installation, Testing and Commissioning of Wireless Daylight Sensors (Lutron), 4-channel Switching modules. - in all meeting rooms | Set | 4 | 4 | 16469 | 4393 | 65876 | 17572 | 83448
[7 empty] | 0 | 0 | 0
VI | POWER RECEPTACLES. | [5 empty] | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
| Supply, Installation, Testing and Commissioning of the following Modular/Industrial Switch, sockets with modular front plate, and accessories as per the site conditions. | [5 empty] | 0 | 0 | 0
| The quoted rate for power socket outlets shall include a. Socket outlets - As specified b. Switches c. 20SWG metal boxes with knockout on all sides d. Front plate of required colours(As per architect Approval) with accessories | [5 empty] | 0 | 0 | 0
| Industrial type sockets shall be of Polycarbonate body with plug top & locking facility. All switch / sockets shall be provided with printed labels / stickers indicating source code. Colour code for UPS socket plates : White/ as per architect. Colour code for RP socket plates : Black/Grey/ as per architect. All switch / sockets including front plate & frame which will be mounted on the metal boxes shall have removable film coat to protect from scratches & paint during installation.Prior Approval to be taken from Architect/Consultants before Procurement | [5 empty] | 0 | 0 | 0
| Note: Safety shutters to prevent accidental contact with live parts shall be provided & 4 mm Acrylic sheet to be provided for sockets face plate whichever is connected with box | [5 empty] | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
| Colour codes for HUB/server Industrial Sockets to be followed as below | [5 empty] | 0 | 0 | 0
| Source #1 - Blue | [5 empty] | 0 | 0 | 0
| Source #2 - Orange | [5 empty] | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
| Colour codes for kictehen Industrial Sockets to be followed as per architect .Socket type shall be round pin type as per the availibility/Norms . Same will be decided at the time of approval .. Costing shall include selection of any time of sockets | [5 empty] | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
| Colour codes for workstation Sockets to be followed as below as per architect | [5 empty] | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
A | Without box | [5 empty] | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
6.1 | 1x6/13A intel socket controlled by 16A switch | Nos. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
6.2 | 2x6/13A intel socket controlled by 16A switch | Nos. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
6.3 | 3x6/13A intel socket controlled by 16A switch | Nos. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
6.4 | 4x6/13A intel socket controlled by 16A switch | Nos. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
6.5 | 1x6/16A Round pin socket controlled by 16A switch | Nos. | 170 | 170 | 283 | 63 | 48110 | 10710 | 58820
[7 empty] | 0 | 0 | 0
6.6 | 2x6/16A Round pin socket controlled by 16A switch | Nos. | 170 | 170 | 458 | 98 | 77860 | 16660 | 94520
[7 empty] | 0 | 0 | 0
6.7 | 3x6/16A Round pin socket controlled by 16A switch | Nos. | 25 | 25 | 616 | 125 | 15400 | 3125 | 18525
[7 empty] | 0 | 0 | 0
6.8 | 4x6/16A Round pin socket controlled by 16A switch | Nos. | 2 | 2 | 845 | 177 | 1690 | 354 | 2044
[7 empty] | 0 | 0 | 0
B | With box | [5 empty] | 0 | 0 | 0
6.9 | 1x6/13A intel socket controlled by 16A switch | Nos. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
6.1 | 2x6/13A intel socket controlled by 16A switch | Nos. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
6.11 | 3x6/13A intel socket controlled by 16A switch | Nos. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
6.12 | 4x6/13A intel socket controlled by 16A switch | Nos. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
6.13 | 1x6/16A intel socket controlled by 16A switch | Nos. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
6.14 | 1x6/16A Round pin socket controlled by 16A switch | Nos. | 65 | 65 | 327 | 73 | 21255 | 4745 | 26000
[7 empty] | 0 | 0 | 0
6.15 | 2x6/16A Round pin socket controlled by 16A switch | Nos. | 20 | 20 | 538 | 116 | 10760 | 2320 | 13080
[7 empty] | 0 | 0 | 0
6.16 | 3x6/16A Round pin socket controlled by 16A switch | Nos. | 10 | 10 | 714 | 150 | 7140 | 1500 | 8640
[7 empty] | 0 | 0 | 0
6.17 | 4x6/16A Round pin socket controlled by 16A switch | Nos. | 2 | 2 | 968 | 196 | 1936 | 392 | 2328
[7 empty] | 0 | 0 | 0
6.18 | Supply, Installation, Testing and Commissioning of USB port (Output Current 0 to 2Amp) - Type C | Nos. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
6.19 | Supply, Installation, Testing and Commissioning of USB port (Output Current 0 to 2Amp) - Type A | Nos. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
C | Industrial Sockets | [5 empty] | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
6.2 | 1No. 32A 3 pin 1phase Industrial type socket with plug top controlled by 32A DP MCB (D CURVE) & Same shall be mounted on Existing powder coated ceiling raceways as per approved sample. ( IP 44) | Nos. | 6 | 6 | 2812 | 660 | 16872 | 3960 | 20832
[7 empty] | 0 | 0 | 0
6.21 | 1No. 63A 5 pin 3phase Industrial type socket with plug top controlled by 63A 4P MCB (D CURVE) & Same shall be mounted on Existing powder coated ceiling raceways as per approved sample. ( IP 44) | Nos. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
6.22 | 1No. 16 A 3 pin round pin Socket with 16A Switch (IP65) | Nos. | 5 | 5 | 327 | 73 | 1635 | 365 | 2000
[7 empty] | 0 | 0 | 0
6.23 | 1No. 40A 5pin 1phase Industrial type socket with plug top controlled by 40A 4P MCB (D CURVE) & Same shall be mounted on Existing powder coated ceiling raceways as per approved sample. ( IP 44) | Nos. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
6.24 | 1No. 20A 3 pin 1phase Industrial type socket with plug top controlled by 20A DP MCB. ( IP 65 FOR KITCHEN ) | Nos. | 1 | 1 | 2812 | 660 | 2812 | 660 | 3472
[7 empty] | 0 | 0 | 0
6.25 | 1No. 32A 3 pin 1phase Industrial type socket with plug top controlled by 32A DP MCB. ( IP 65 FOR MICRO KITCHEN ) | Nos. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
6.26 | 1No. 40A 3 pin 1phase Industrial type socket with plug top controlled by 40A DP MCB. ( IP 65 FOR KITCHEN ) | Nos. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
6.27 | 1No. 63A 3 pin 1phase Industrial type socket with plug top controlled by 63A DP MCB. | Nos. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
6.28 | 1No. 16A 5 pin 3 phase Industrial type socket with plug top controlled by 16A 4P MCB ( IP 65 FOR KITCHEN ) | Nos. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
6.29 | 1No. 20A 5 pin 3 phase Industrial type socket with plug top controlled by 20A 4P MCB .( IP 65 FOR KITCHEN ) | Nos. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
6.3 | 1No. 32A 5 pin 3 phase Industrial type socket with plug top controlled by 32A 4P MCB ( IP 65 FOR KITCHEN ) | Nos. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
6.31 | 1No. 40A 5 pin 3 phase Industrial type socket with plug top controlled by 40A 4P MCB ( ( IP 65 FOR KITCHEN ) | Nos. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
6.32 | 1No. 63A 5 pin 3 phase Industrial type socket with plug top controlled by 63A 4P MCB ( IP 65 FOR KITCHEN ) | Nos. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
D | FLOOR SERVICE BOXES | [5 empty] | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
6.33 | Supply & Installation of Floor service box suitable for fixing 1 Set of 2x6/13A round socket controlled by 16A switch in one compartment & in other compartment place provision for mounting 1 Data / 1 Voice points/1 HDMI (The rate to include cost of sockets) Finish:SS Type | Nos. | 3 | 3 | 8345 | 1319 | 25035 | 3957 | 28992
[7 empty] | 0 | 0 | 0
6.34 | Supply & Installation of Floor service box suitable for fixing 2 Set of 2x6/13A round socket controlled by 16A switch in one compartment & in other compartment place provision for mounting 2 Data / 2 Voice points/1 HDMI (The rate to include cost of sockets) Finish:SS Type | Nos. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
6.35 | Supply & Installation of Floor service box suitable for fixing 1 Set of 3x6/13A round socket controlled by 16A switch in one compartment & in other compartment place provision for mounting 1 Data / 1 Voice points/1 HDMI (The rate to include cost of sockets) Finish:SS Type | Nos. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
6.36 | Supply & Installation of Floor service box suitable for fixing 2 Set of 3 x6/13A round socket controlled by 16A switch in one compartment & in other compartment place provision for mounting 1 Data / 1 Voice points/1 HDMI (The rate to include cost of sockets) Finish:SS Type | Nos. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
6.37 | Supply & Installation of Floor service box suitable for fixing1 Set of 4x6/13A round socket controlled by 16A switch in one compartment & in other compartment place provision for mounting 1 Data / 1 Voice points/1 HDMI (The rate to include cost of sockets) Finish:SS Type | Nos. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
6.38 | Supply & Installation of Floor service box suitable for fixing 2 Set of 4 x6/13A round socket controlled by 16A switch in one compartment & in other compartment place provision for mounting 1 Data / 1 Voice points/1 HDMI (The rate to include cost of sockets) Finish:SS Type | Nos. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
| Factory made Standard accessories only to be used for bends, curve, tees etc., | [5 empty] | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
6.39 | Supply & Installation of 12M Modular boxes (Pop Up) (with Data, Voice,USB, C-Type, HDMI) MEETING ROOMS | Nos. | 7 | 7 | 11859 | 1319 | 83013 | 9233 | 92246
[7 empty] | 0 | 0 | 0
6.4 | Supply & Installation of 16M Modular boxes (Pop Up) (with Data, Voice,USB, C-Type, HDMI), BOARD ROOM | Nos. | 4 | 4 | 15372 | 1319 | 61488 | 5276 | 66764
[7 empty] | 0 | 0 | 0
A | Ladder Type Cable Tray : | [5 empty] | 0 | 0 | 0
| Supply and Erection of Heavy duty GI ladder type 2mm thick hot dipped galvanized by 610gms/sqm (87 microns) in line with IS: 4759. The tray and accessories includes cleat angle, rungs, side runner, coupler plate, Elbows, Bends, Tees and Reducers and Hardware .The fixing of cable trays include necessary ceiling suspended / wall mounted supports fixed in ceiling with Fabricated Ms Angle supports,Ms C channel,Base plate etc, The rate shall include bends, angles, Ts, HITECH ROD and all accessories complete Supports Shall be provided at every 1200mm. The cost of supports to be included. Supports must be welded to a square true ceiling base plate with arc welding, the base plate must be fixed to the true ceiling with 04 nos. of HILTI anchor fasteners. The cost of 2runs of 25x3mm GI Strip to be included in the cost of the cable tray. Supports must be made out of MS L angle type for cable tray width of 450mm and above. For Less than 450mm width tray support with hi-tech threaded rods & anchor fasteners. | [5 empty] | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
7.1 | 1200 x 100 mm Size | Mts. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
7.2 | 1000 x 100 mm Size | Mts. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
7.3 | 750 x 75mm Size | Mts. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
7.4 | 600 x 75mm Size | Mts. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
7.5 | 450 x 50mm Size | Mts. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
7.6 | 300 x 50mm Size | Mts. | 50 | 50 | 660 | 192 | 33000 | 9600 | 42600
[7 empty] | 0 | 0 | 0
7.7 | 250 x 50mm Size | Mts. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
7.8 | 200 x 50mm Size | Mts. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
7.9 | 150 x 50mm Size | Mts. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
7.1 | 100 x 50mm Size | Mts. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
B | Perforated type cable tray with top cover ( POWER ) | [5 empty] | 0 | 0 | 0
| Supply and installation of following sizes of perforated cable trays of 2mm thickness and height as per below description for supporting cables including bends, tees & reducers and including all labour and materials, as per approved drawings, specifications of this tender and directions of Engineer-in-charge. Supports Shall be provided at every 1200mm. The cost of supports to be included. Supports must be welded to a square true ceiling base plate with arc welding, the base plate must be fixed to the true ceiling with 04 nos. of HILTI anchor fasteners. Supports must be made out of MS L angle type for cable tray width of 450mm and above. For Less than 450mm width tray support with hi-tech threaded rods & anchor fasteners. Note: * Factory fabricated bends to be used for all ceiling raceways & trays | [5 empty] | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
7.11 | 1200 x 100 mm Size | Mts. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
7.12 | 1000 x 100 mm Size | Mts. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
7.13 | 750x 75 mm Size | Mts. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
7.14 | 600 x 75mm Size | Mts. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
7.15 | 450 x 60mm Size | Mts. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
7.16 | 300 x 60mm Size | Mts. | 80 | 80 | 1127 | 147 | 90160 | 11760 | 101920
[7 empty] | 0 | 0 | 0
7.17 | 250 x 60mm Size | Mts. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
7.18 | 200 x 60mm Size | Mts. | 30 | 30 | 854 | 107 | 25620 | 3210 | 28830
[7 empty] | 0 | 0 | 0
7.19 | 150 x 60mm Size | Mts. | 20 | 20 | 722 | 94 | 14440 | 1880 | 16320
[7 empty] | 0 | 0 | 0
7.2 | 100 x 60mm Size | Mts. | 80 | 80 | 582 | 81 | 46560 | 6480 | 53040
[7 empty] | 0 | 0 | 0
7.21 | 80 x 60mm Size | Mts. | 50 | 50 | 564 | 81 | 28200 | 4050 | 32250
[7 empty] | 0 | 0 | 0
C | Perforated type cable tray with top cover for (LIGHTING) | [5 empty] | 0 | 0 | 0
| Supply and installation of following sizes of perforated cable trays of 2mm thickness and height as per below description for supporting cables including bends, tees & reducers and including all labour and materials, as per approved drawings, specifications of this tender and directions of Engineer-in-charge. Supports Shall be provided at every 1200mm. The cost of supports to be included. Supports must be welded to a square true ceiling base plate with arc welding, the base plate must be fixed to the true ceiling with 04 nos. of HILTI anchor fasteners. Supports must be made out of MS L angle type for cable tray width of 450mm and above. For Less than 450mm width tray support with hi-tech threaded rods & anchor fasteners. Note: * Factory fabricated bends to be used for all ceiling raceways & trays | [5 empty] | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
7.22 | 450 x 60mm Size | Mts. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
7.23 | 300 x 60mm Size | Mts. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
7.24 | 250 x 60mm Size | Mts. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
7.25 | 200 x 60mm Size | Mts. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
7.26 | 150 x 60mm Size | Mts. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
7.27 | 100 x 60mm Size | Mts. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
7.28 | 80 x 60mm Size | Mts. | 100 | 100 | 564 | 81 | 56400 | 8100 | 64500
[7 empty] | 0 | 0 | 0
7.29 | 60 x 60mm Size | Mts. | 200 | 200 | 546 | 81 | 109200 | 16200 | 125400
[7 empty] | 0 | 0 | 0
D | Perforated type cable tray with top cover for (HVAC) | [5 empty] | 0 | 0 | 0
| Supply and installation of following sizes of perforated cable trays of 2mm thickness and height as per below description for supporting cables including bends, tees & reducers and including all labour and materials, as per approved drawings, specifications of this tender and directions of Engineer-in-charge. Supports Shall be provided at every 1200mm. The cost of supports to be included. Supports must be welded to a square true ceiling base plate with arc welding, the base plate must be fixed to the true ceiling with 04 nos. of HILTI anchor fasteners. Supports must be made out of MS L angle type for cable tray width of 450mm and above. For Less than 450mm width tray support with hi-tech threaded rods & anchor fasteners. Note: * Factory fabricated bends and accessories to be used for all ceiling raceways & trays | [5 empty] | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
7.3 | 450 x 60mm Size | Mts. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
7.31 | 300 x 60mm Size | Mts. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
7.32 | 250 x 60mm Size | Mts. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
7.33 | 200 x 60mm Size | Mts. | 50 | 50 | 854 | 107 | 42700 | 5350 | 48050
[7 empty] | 0 | 0 | 0
7.34 | 150 x 60mm Size | Mts. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
7.35 | 100 x 60mm Size | Mts. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
7.36 | 80 x 60mm Size | Mts. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
7.37 | 60 x 60mm Size | Mts. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
D | Raceways | [5 empty] | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
| Supply & Installation of following size GI raceway / wire way with cover, made out of 16 SWG GI for body and 14 SWG GI for cover. Junction boxes to be provided with enough supports inside the box. Raceway installed above false ceiling/floor shall include necessary mounting supports, junction boxes and accessories to fix it firmly to the ground/ ceiling. The rate quote shall include providing earthing for the Wireway trunking. All edges, cut faces shall be free of burrs & shall be smooth. The channels shall be earthed at the boxes and at the joints with 4sq.mm copper Wire with end terminations screws so that earth is continuous. Jointing of the race ways to be done with welding. Colour code should be followed for cover as per project incharge. The costing shall include chipping works, disposal of debris, Proper cleaning & Packing of junction boxes/Raceways & filling the Cement concrete with chicken mesh, making it for floor finishing level as per site Incharge. Note: * Factory fabricated bends and accessories to be used for all ceiling raceways & trays | [5 empty] | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
1 | Floor raceways with respective Junction Box | [5 empty] | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
7.38 | 450 x 40mm Size | Mts. | RO | RO |  |  | 0 | 0 | 0
7.39 | 460 x 460 x 50mm Size | Nos. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
7.4 | 300 x 40mm Size | Mts. | RO | RO |  |  | 0 | 0 | 0
7.41 | 310 x 310 x 50mm Size | Nos. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
7.42 | 250 x 40mm Size | Mts. | 30 | 30 | 784 | 120 | 23520 | 3600 | 27120
7.43 | 260 x 260 x 50mm Size | Nos. | 4 | 4 | 511 | 107 | 2044 | 428 | 2472
[7 empty] | 0 | 0 | 0
7.44 | 200 x 40mm Size | Mts. | 45 | 45 | 660 | 107 | 29700 | 4815 | 34515
7.45 | 210 x 210 x 50mm Size | Nos. | 5 | 5 | 458 | 98 | 2290 | 490 | 2780
[7 empty] | 0 | 0 | 0
7.46 | 150 x 40mm Size | Mts. | 40 | 40 | 538 | 94 | 21520 | 3760 | 25280
7.47 | 160 x 160 x 50mm Size | Nos. | 5 | 5 | 370 | 81 | 1850 | 405 | 2255
[7 empty] | 0 | 0 | 0
7.48 | 100 x 40mm Size | Mts. | 70 | 70 | 415 | 81 | 29050 | 5670 | 34720
7.49 | 110 x 110 x 50mm Size | Nos. | 10 | 10 | 308 | 63 | 3080 | 630 | 3710
[7 empty] | 0 | 0 | 0
7.5 | 80 x 40mm Size | Mts. | 100 | 100 | 396 | 81 | 39600 | 8100 | 47700
7.51 | 90 x 90 x 50mm Size | Nos. | 40 | 40 | 308 | 63 | 12320 | 2520 | 14840
[7 empty] | 0 | 0 | 0
1 | Floor raceways with respective Junction Box(In False floor area) | [5 empty] | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
7.52 | 450 x 40mm Size | Mts. | RO | RO |  |  | 0 | 0 | 0
7.53 | 460 x 460 x 50mm Size | Nos. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
7.54 | 300 x 40mm Size | Mts. | RO | RO |  |  | 0 | 0 | 0
7.55 | 310 x 310 x 50mm Size | Nos. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
7.56 | 250 x 40mm Size | Mts. | RO | RO |  |  | 0 | 0 | 0
7.57 | 260 x 260 x 50mm Size | Nos. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
7.58 | 200 x 40mm Size | Mts. | RO | RO |  |  | 0 | 0 | 0
7.59 | 210 x 210 x 50mm Size | Nos. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
7.6 | 150 x 40mm Size | Mts. | RO | RO |  |  | 0 | 0 | 0
7.61 | 160 x 160 x 50mm Size | Nos. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
7.62 | 100 x 40mm Size | Mts. | RO | RO |  |  | 0 | 0 | 0
7.63 | 110 x 110 x 50mm Size | Nos. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
7.64 | 80 x 40mm Size | Mts. | RO | RO |  |  | 0 | 0 | 0
7.65 | 90 x 90 x 50mm Size | Nos. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
F | Ceiling Raceways | [5 empty] | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
7.66 | 600 x 60mm Size | Mts. | RO | RO |  |  | 0 | 0 | 0
7.67 | 610 x 610 x 60mm Size | Nos. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
7.68 | 450 x 60mm Size | Mts. | RO | RO |  |  | 0 | 0 | 0
7.69 | 460 x 460 x 60mm Size | Nos. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
7.7 | 300 x 60mm Size | Mts. | RO | RO |  |  | 0 | 0 | 0
7.71 | 310 x 310 x 60mm Size | Nos. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
7.72 | 250 x 60mm Size | Mts. | RO | RO |  |  | 0 | 0 | 0
7.73 | 260 x 260 x 60mm Size | Nos. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
7.74 | 200 x 60mm Size | Mts. | RO | RO |  |  | 0 | 0 | 0
7.75 | 210 x 210 x 60mm Size | Nos. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
7.76 | 150 x 60mm Size | Mts. | RO | RO |  |  | 0 | 0 | 0
7.77 | 160 x 160 x 60mm Size | Nos. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
7.78 | 100 x 60mm Size | Mts. | RO | RO |  |  | 0 | 0 | 0
7.79 | 110 x 110 x 60mm Size | Nos. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
7.8 | 80 x 60mm Size | Mts. | RO | RO |  |  | 0 | 0 | 0
7.81 | 90 x 90 x 60mm Size | Nos. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
F | Supply & Laying of following size 2mm thick rigid FRLS PVC conduits & accessories fixing in ceiling | [5 empty] | 0 | 0 | 0
7.82 | 32mm dia | Mts. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
7.83 | 25mm dia | Mts. | 200 | 200 | 55 | 19 | 11000 | 3800 | 14800
[7 empty] | 0 | 0 | 0
7.84 | 20mm dia | Mts. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
G | Supply & Laying of following size 2mm thick rigid FRLS PVC conduits & accessories fixing in wall/ floor/false floor | [5 empty] | 0 | 0 | 0
7.85 | 32mm dia | Mts. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
7.86 | 25mm dia | Mts. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
7.87 | 20mm dia | Mts. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
F | Supply & Laying of following size 1.6mm thick rigid MS conduits & accessories fixing in ceiling | [5 empty] | 0 | 0 | 0
7.88 | 32mm dia | Mts. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
7.89 | 25mm dia | Mts. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
7.9 | 20mm dia | Mts. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
G | Supply & Laying of following size 1.6mm thick rigid MS conduits & accessories fixing in wall/ floor/false floor | [5 empty] | 0 | 0 | 0
7.91 | 32mm dia | Mts. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
7.92 | 25mm dia | Mts. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
7.93 | 20mm dia | Mts. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
F | Supply & Laying of following size 1.6mm thick rigid GI conduits & accessories fixing in ceiling | [5 empty] | 0 | 0 | 0
7.94 | 32mm dia | Mts. | 100 | 100 | 143 | 24 | 14300 | 2400 | 16700
[7 empty] | 0 | 0 | 0
7.95 | 25mm dia | Mts. | 250 | 250 | 112 | 24 | 28000 | 6000 | 34000
[7 empty] | 0 | 0 | 0
7.96 | 20mm dia | Mts. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
G | Supply & Laying of following size 1.6mm thick rigid FRLS GI conduits & accessories fixing in wall/ floor/false floor | [5 empty] | 0 | 0 | 0
7.97 | 32mm dia | Mts. | 50 | 50 | 150 | 24 | 7500 | 1200 | 8700
[7 empty] | 0 | 0 | 0
7.98 | 25mm dia | Mts. | 30 | 30 | 120 | 24 | 3600 | 720 | 4320
[7 empty] | 0 | 0 | 0
7.99 | 20mm dia | Mts. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
H | Supply & Installation of following size Powder coated raceway / wire way with cover, made out of 2mm thick steel sheet factory fabricated post galvanized raceways to be laid in the ceiling / Floor for Server/ HUB room area with cutouts for installation of MCB and Industrial socket outlets. The rate to include providing 2 mm thick GI cover fixing accessories, Earthing with 8SWG copper wire, complete with necessary supports, bends, access boxes, Tap off boxes & Cross over as per specification and site requirement. The shade shall be as per site approval.Colour code should be followed for as per project incharge. | [5 empty] | 0 | 0 | 0
| Supply & Installation of following size Powder coated junction boxes , made out of 16 SWG GI/MS for body and 14 SWG GI/MS for cover. - The shade shall be as per site approval.Colour code should be followed for cover as per project incharge. | [5 empty] | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
8.1 | 150 x 200mm Size | Mts. | RO | RO |  |  | 0 | 0 | 0
8.101 | 460 x 460 x 400mm Size | Nos. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
8.102 | 150 x 150mm Size | Mts. | 20 | 20 | 731 | 94 | 14620 | 1880 | 16500
8.103 | 160 x 160 x 100mm Size | Nos. | 2 | 2 | 370 | 81 | 740 | 162 | 902
[7 empty] | 0 | 0 | 0
8.104 | 100 x100mm Size | Mts. | RO | RO |  |  | 0 | 0 | 0
8.105 | 110 x 110 x 100mm Size | Nos. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
8.106 | Supply and installation of 450mm X 100mm Electroinc type SS Basket type cable tray/Cablofil type and include all necessary supporting rods, C channel complete as required at distance of 1200mm. | Mts. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
8.107 | Supply and installation of 300mm X 100mm Electroinc type Basket type cable tray/Cablofil type and include all necessary supporting rods, C channel complete as required at distance of 1200mm. | Mts. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
VIII | CABLE TRAYS & RACEWAYS FOR NETWORK | [5 empty] | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
| Factory made Standard accessories only to be used for bends, curve, tees etc., | [5 empty] | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
A | Ladder Type Cable Tray : | [5 empty] | 0 | 0 | 0
| Supply and Erection of Heavy duty GI ladder type 2mm thick hot dipped galvanized by 610gms/sqm (87 microns) in line with IS: 4759. The tray and accessories includes cleat angle, rungs, side runner, coupler plate, Elbows, Bends, Tees and Reducers and Hardware .The fixing of cable trays include necessary ceiling suspended / wall mounted supports fixed in ceiling with Fabricated Ms Angle supports,Ms C channel,Base plate etc, The rate shall include bends, angles, Ts, HITECH ROD and all accessories complete Supports Shall be provided at every 1200mm. The cost of supports to be included. Supports must be welded to a square true ceiling base plate with arc welding, the base plate must be fixed to the true ceiling with 04 nos. of HILTI anchor fasteners. The cost of 2runs of 25x3mm GI Strip to be included in the cost of the cable tray. Supports must be made out of MS L angle type for cable tray width of 450mm and above. For Less than 450mm width tray support with hi-tech threaded rods & anchor fasteners. | [5 empty] | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
8.1 | 1200 x 100 mm Size | Mts. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
8.2 | 1000 x 100 mm Size | Mts. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
8.3 | 750 x 75mm Size | Mts. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
8.4 | 600 x 75mm Size | Mts. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
8.5 | 450 x 50mm Size | Mts. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
8.6 | 300 x 50mm Size | Mts. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
8.7 | 250 x 50mm Size | Mts. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
8.8 | 200 x 50mm Size | Mts. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
8.9 | 150 x 50mm Size | Mts. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
8.1 | 100 x 50mm Size | Mts. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
B | Raceways | [5 empty] | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
| Supply & Installation of following size GI raceway / wire way with cover, made out of 16 SWG GI for body and 14 SWG GI for cover. Junction boxes to be provided with enough supports inside the box. Raceway installed above false ceiling/floor shall include necessary mounting supports, junction boxes and accessories to fix it firmly to the ground/ ceiling. The rate quote shall include providing earthing for the Wireway trunking. All edges, cut faces shall be free of burrs & shall be smooth. The channels shall be earthed at the boxes and at the joints with 4sq.mm copper Wire with end terminations screws so that earth is continuous. Jointing of the race ways to be done with welding. Colour code should be followed for cover as per project incharge. The costing shall include chipping works, disposal of debris, Proper cleaning & Packing of junction boxes/Raceways & filling the Cement concrete with chicken mesh, making it for floor finishing level as per site Incharge. | [5 empty] | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
1 | Floor raceways with respective Junction Box | [5 empty] | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
8.11 | 450 x 40mm Size | Mts. | RO | RO |  |  | 0 | 0 | 0
8.12 | 460 x 460 x 50mm Size | Nos. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
8.13 | 300 x 40mm Size | Mts. | 20 | 20 | 907 | 147 | 18140 | 2940 | 21080
8.14 | 310 x 310 x 50mm Size | Nos. | 5 | 5 | 784 | 160 | 3920 | 800 | 4720
[7 empty] | 0 | 0 | 0
8.15 | 250 x 40mm Size | Mts. | RO | RO |  |  | 0 | 0 | 0
8.16 | 260 x 260 x 50mm Size | Nos. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
8.17 | 200 x 40mm Size | Mts. | 20 | 20 | 660 | 107 | 13200 | 2140 | 15340
8.18 | 210 x 210 x 50mm Size | Nos. | 5 | 5 | 458 | 98 | 2290 | 490 | 2780
[7 empty] | 0 | 0 | 0
8.19 | 150 x 40mm Size | Mts. | 40 | 40 | 538 | 94 | 21520 | 3760 | 25280
8.2 | 160 x 160 x 50mm Size | Nos. | 5 | 5 | 370 | 81 | 1850 | 405 | 2255
[7 empty] | 0 | 0 | 0
8.21 | 100 x 40mm Size | Mts. | 10 | 10 | 415 | 81 | 4150 | 810 | 4960
8.22 | 110 x 110 x 50mm Size | Nos. | 5 | 5 | 308 | 63 | 1540 | 315 | 1855
[7 empty] | 0 | 0 | 0
8.23 | 80 x 40mm Size | Mts. | 100 | 100 | 396 | 81 | 39600 | 8100 | 47700
8.24 | 90 x 90 x 50mm Size | Nos. | 60 | 60 | 308 | 63 | 18480 | 3780 | 22260
[7 empty] | 0 | 0 | 0
| Floor raceways with respective Junction Box (In Flase floor area) | [5 empty] | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
8.25 | 450 x 40mm Size | Mts. | RO | RO |  |  | 0 | 0 | 0
8.26 | 460 x 460 x 50mm Size | Nos. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
8.27 | 300 x 40mm Size | Mts. | RO | RO |  |  | 0 | 0 | 0
8.28 | 310 x 310 x 50mm Size | Nos. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
8.29 | 250 x 40mm Size | Mts. | RO | RO |  |  | 0 | 0 | 0
8.3 | 260 x 260 x 50mm Size | Nos. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
8.31 | 200 x 40mm Size | Mts. | RO | RO |  |  | 0 | 0 | 0
8.32 | 210 x 210 x 50mm Size | Nos. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
8.33 | 150 x 40mm Size | Mts. | RO | RO |  |  | 0 | 0 | 0
8.34 | 160 x 160 x 50mm Size | Nos. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
8.35 | 100 x 40mm Size | Mts. | RO | RO |  |  | 0 | 0 | 0
8.36 | 110 x 110 x 50mm Size | Nos. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
8.37 | 80 x 40mm Size | Mts. | RO | RO |  |  | 0 | 0 | 0
8.38 | 90 x 90 x 50mm Size | Nos. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
F | Ceiling Raceways ( Network Cables) - GI | [5 empty] | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
8.39 | 450 x 100mm Size | Mts. | RO | RO |  |  | 0 | 0 | 0
8.4 | 610 x 610 x 60mm Size | Nos. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
8.41 | 450 x 60mm Size | Mts. | RO | RO |  |  | 0 | 0 | 0
8.42 | 460 x 460 x 110mm Size | Nos. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
8.43 | 300 x 60mm Size | Mts. | 30 | 30 | 1038 | 147 | 31140 | 4410 | 35550
8.44 | 310 x 310 x 60mm Size | Nos. | 5 | 5 | 784 | 160 | 3920 | 800 | 4720
[7 empty] | 0 | 0 | 0
8.45 | 250 x 60mm Size | Mts. | RO | RO |  |  | 0 | 0 | 0
8.46 | 260 x 260 x 60mm Size | Nos. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
8.47 | 200 x 60mm Size | Mts. | 10 | 10 | 792 | 107 | 7920 | 1070 | 8990
8.48 | 210 x 210 x 60mm Size | Nos. | 5 | 5 | 458 | 98 | 2290 | 490 | 2780
[7 empty] | 0 | 0 | 0
8.49 | 150 x 60mm Size | Mts. | 20 | 20 | 669 | 94 | 13380 | 1880 | 15260
8.5 | 160 x 160 x 60mm Size | Nos. | 5 | 5 | 370 | 81 | 1850 | 405 | 2255
[7 empty] | 0 | 0 | 0
8.51 | 100 x 60mm Size | Mts. | 120 | 120 | 538 | 81 | 64560 | 9720 | 74280
8.52 | 110 x 110 x 60mm Size | Nos. | 5 | 5 | 308 | 63 | 1540 | 315 | 1855
[7 empty] | 0 | 0 | 0
8.53 | 80 x 60mm Size | Mts. | 10 | 10 | 520 | 81 | 5200 | 810 | 6010
8.54 | 90 x 90 x 60mm Size | Nos. | 5 | 5 | 308 | 63 | 1540 | 315 | 1855
[7 empty] | 0 | 0 | 0
F | Ceiling Raceways (ACCESS & CCTV ) GI | [5 empty] | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
8.55 | 600 x 60mm Size | Mts. | RO | RO |  |  | 0 | 0 | 0
8.56 | 610 x 610 x 60mm Size | Nos. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
8.57 | 450 x 60mm Size | Mts. | RO | RO |  |  | 0 | 0 | 0
8.58 | 460 x 460 x 60mm Size | Nos. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
8.59 | 300 x 60mm Size | Mts. | RO | RO |  |  | 0 | 0 | 0
8.6 | 310 x 310 x 60mm Size | Nos. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
8.61 | 250 x 60mm Size | Mts. | RO | RO |  |  | 0 | 0 | 0
8.62 | 260 x 260 x 60mm Size | Nos. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
8.63 | 200 x 60mm Size | Mts. | RO | RO |  |  | 0 | 0 | 0
8.64 | 210 x 210 x 60mm Size | Nos. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
8.65 | 150 x 60mm Size | Mts. | RO | RO |  |  | 0 | 0 | 0
8.66 | 160 x 160 x 110mm Size | Nos. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
8.67 | 100 x 60mm Size | Mts. | RO | RO |  |  | 0 | 0 | 0
8.68 | 110 x 110 x 110mm Size | Nos. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
8.69 | 80 x 60mm Size | Mts. | 100 | 100 | 520 | 81 | 52000 | 8100 | 60100
8.7 | 90 x 90 x 60mm Size | Nos. | 10 | 10 | 308 | 63 | 3080 | 630 | 3710
[7 empty] | 0 | 0 | 0
F | Ceiling Raceways (WIFI ) GI | [5 empty] | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
8.71 | 600 x 60mm Size | Mts. | RO | RO |  |  | 0 | 0 | 0
8.72 | 610 x 610 x 60mm Size | Nos. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
8.73 | 450 x 60mm Size | Mts. | RO | RO |  |  | 0 | 0 | 0
8.74 | 460 x 460 x 60mm Size | Nos. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
8.75 | 300 x 60mm Size | Mts. | RO | RO |  |  | 0 | 0 | 0
8.76 | 310 x 310 x 60mm Size | Nos. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
8.77 | 250 x 60mm Size | Mts. | RO | RO |  |  | 0 | 0 | 0
8.78 | 260 x 260 x 60mm Size | Nos. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
8.79 | 200 x 60mm Size | Mts. | RO | RO |  |  | 0 | 0 | 0
8.8 | 210 x 210 x 60mm Size | Nos. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
8.81 | 150 x 60mm Size | Mts. | RO | RO |  |  | 0 | 0 | 0
8.82 | 160 x 160 x 110mm Size | Nos. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
8.83 | 100 x 60mm Size | Mts. | 15 | 15 | 538 | 81 | 8070 | 1215 | 9285
8.84 | 110 x 110 x 110mm Size | Nos. | 4 | 4 | 308 | 63 | 1232 | 252 | 1484
[7 empty] | 0 | 0 | 0
8.85 | 80 x 60mm Size | Mts. | 100 | 100 | 520 | 81 | 52000 | 8100 | 60100
8.86 | 90 x 90 x 60mm Size | Nos. | 10 | 10 | 308 | 63 | 3080 | 630 | 3710
[7 empty] | 0 | 0 | 0
F | Supply & Laying of following size 2mm thick rigid FRLS PVC conduits & accessories fixing in ceiling | [5 empty] | 0 | 0 | 0
8.87 | 32mm dia | Mts. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
8.88 | 25mm dia | Mts. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
8.89 | 20mm dia | Mts. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
G | Supply & Laying of following size 2mm thick rigid FRLS PVC conduits & accessories fixing in wall/ floor/false floor | [5 empty] | 0 | 0 | 0
8.9 | 32mm dia | Mts. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
8.91 | 25mm dia | Mts. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
8.92 | 20mm dia | Mts. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
F | Supply & Laying of following size 1.6mm thick rigid MS conduits & accessories fixing in ceiling | [5 empty] | 0 | 0 | 0
8.93 | 32mm dia | Mts. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
8.94 | 25mm dia | Mts. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
8.95 | 20mm dia | Mts. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
G | Supply & Laying of following size 1.6mm thick rigid MS conduits & accessories fixing in wall/ floor/false floor | [5 empty] | 0 | 0 | 0
8.96 | 32mm dia | Mts. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
8.97 | 25mm dia | Mts. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
8.98 | 20mm dia | Mts. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
F | Supply & Laying of following size 1.6mm thick rigid GI conduits & accessories fixing in ceiling | [5 empty] | 0 | 0 | 0
8.99 | 32mm dia | Mts. | 50 | 50 | 150 | 24 | 7500 | 1200 | 8700
[7 empty] | 0 | 0 | 0
8.1 | 25mm dia | Mts. | 300 | 300 | 120 | 24 | 36000 | 7200 | 43200
[7 empty] | 0 | 0 | 0
8.101 | 20mm dia | Mts. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
G | Supply & Laying of following size 1.6mm thick rigid FRLS GI conduits & accessories fixing in wall/ floor/false floor | [5 empty] | 0 | 0 | 0
8.102 | 32mm dia | Mts. | 50 | 50 | 150 | 24 | 7500 | 1200 | 8700
[7 empty] | 0 | 0 | 0
8.103 | 25mm dia | Mts. | 50 | 50 | 120 | 24 | 6000 | 1200 | 7200
[7 empty] | 0 | 0 | 0
8.104 | 20mm dia | Mts. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
H | Supply & Installation of following size Powder coated raceway / wire way with cover, made out of 2mm thick steel sheet factory fabricated post galvanized raceways to be laid in the ceiling / Floor for Server/ HUB room area with cutouts for installation of MCB and Industrial socket outlets. The rate to include providing 2 mm thick GI cover fixing accessories, Earthing with 8SWG copper wire, complete with necessary supports, bends, access boxes, Tap off boxes & Cross over as per specification and site requirement. The shade shall be as per site approval.Colour code should be followed for as per project incharge. | [5 empty] | 0 | 0 | 0
| Supply & Installation of following size Powder coated junction boxes , made out of 16 SWG GI/MS for body and 14 SWG GI/MS for cover. - The shade shall be as per site approval.Colour code should be followed for cover as per project incharge. | [5 empty] | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
8.105 | 450 x 200mm Size | Mts. | 10 | 10 | 1750 | 225 | 17500 | 2250 | 19750
8.106 | 210 x 210 x 200mm Size | Nos. | 4 | 4 | 458 | 98 | 1832 | 392 | 2224
[7 empty] | 0 | 0 | 0
8.107 | 300 x 100mm Size | Mts. | 10 | 10 | 1275 | 147 | 12750 | 1470 | 14220
8.108 | 160 x 160 x 100mm Size | Nos. | 4 | 4 | 370 | 81 | 1480 | 324 | 1804
[7 empty] | 0 | 0 | 0
8.109 | 100 x100mm Size | Mts. | RO | RO | 740 | 90 | 0 | 0 | 0
8.11 | 110 x 110 x 100mm Size | Nos. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
8.111 | Supply and installation of 450mm X 100mm Electroinc type Basket type cable tray/Cablofil type and include all necessary supporting rods, C channel complete as required at distance of 1200mm. | Mts. | 6 | 6 | 1438 | 230 | 8628 | 1380 | 10008
[7 empty] | 0 | 0 | 0
8.112 | Supply and installation of 300mm X 100mm Electroinc type Basket type cable tray/Cablofil type and include all necessary supporting rods, C channel complete as required at distance of 1200mm. | Mts. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
IX | EARTHING | [5 empty] | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
A | Supplier shall provide installation methodology for the installation of earth electrodes | [5 empty] | 0 | 0 | 0
| Supplier shall be present during the installation of earth electrode | [5 empty] | 0 | 0 | 0
| All the testing at site shall be conducted in presence of consultants | [5 empty] | 0 | 0 | 0
| Rate shall include all civil works including construction of chamber with PCC cover alongwith Name plate details as per the requirement. Costing shall include soil test report & additional equipments if any to achieve the desired value as mentioned in technical specification | [5 empty] | 0 | 0 | 0
9.1 | Body Earthing: 'Supply, installation, testing & commissioning of MAINTENANCEFREE earthing system with Earthing Electrode dual pipe consist of 3mtr long 47 mm dia outer pipe, 25 mm dia inner pipe, Terminal flat of 30 x 10/ 12 x 12mm, the entire construction processed with Hot Dip Galvanization, outer surface upto 100 microns, and all inner surface 300 microns, all inner annular space filled with highly conductive and non-corrosive nature crystalline material, along with electrode Moisture Booster compound of 2 x 25 Kg bags to fill surround the pipe at the time of installation. (Moisture Booster having its property of moisture retention, conduction and non-corrosive nature). Also include 300mm x 300mm heavy duty GI frame and heavy duty RCC Pre cast cover, 150mm brick masonry chamber etc., complete. ASHLOK T-19 / GALAXY G-503 | Nos. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
9.2 | Neutral Earthing: 'Supply, installation, testing & commissioning of MAINTENANCEFREE earthing system with Earthing Electrode dual pipe consist of 3mtr long 77 mm dia outer pipe, 47 mm dia inner pipe, Terminal flat of 38 x 10 mm, the entire construction processed with Hot Dip Galvanization, outer surface upto 100 microns and all inner surface Upto 300 microns, all inner annular space filled with highly conductive and non-corrosive nature crystalline material, along with electrode Moisture Booster compound of 2 x 25 kg bags to fill surround the pipe at the time of installation. (Moisture Booster having its property of moisture retention, conduction and non – corrosive nature) .Also include 300mm x 300mm heavy duty GI frame and heavy duty RCC Pre cast cover, 150mm brick masonry chamber etc., complete. ASHLOK T-39 / GALAXY G-803 | Nos. | 2 | 2 | 13176 | 2198 | 26352 | 4396 | 30748
[7 empty] | 0 | 0 | 0
B | EARTH STRIPS | [5 empty] | 0 | 0 | 0
| GI/Cu earth strips on cable tray or below ground as per site condition. All Cu. Strips shall be run in pvc heat shrinkable sleeve & mounted on insulation mounts. Cost of civil works shall be included for strips laid below ground. Including connection/ terminating with nut, bolt, spring, washer etc. as required. Jointing shall be done by overlapping and with 2 sets of brass nut bolt & spring washer spaced at 50mm. Joints to be welded for GI and brazing for copper strips. | [5 empty] | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
9.3 | 8 SWG GI Wire | Mts. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
9.4 | 25 x 3mm GI Earth flat | Mts. | 150 | 150 | 81 | 29 | 12150 | 4350 | 16500
[7 empty] | 0 | 0 | 0
9.5 | 25 x 6mm GI Earth flat | Mts. | 200 | 200 | 112 | 32 | 22400 | 6400 | 28800
[7 empty] | 0 | 0 | 0
9.6 | 50 x 6mm GI Earth flat | Mts. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
9.7 | 75 x 10mm GI Earth flat | Mts. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
9.8 | Busbar of 0.5 Mtr length made out of 25 x 6 mm GI strip with drill holes of M8 at 25mm interval mounted on insulators with glass covered box & Naming to be done as per the Requirement. Detailed drawings attached in earthing schematic & construction of earth box to be made as per schematic | Nos. | 2 | 2 | 2746 | 441 | 5492 | 882 | 6374
[7 empty] | 0 | 0 | 0
9.9 | Busbar of 0.5 Mtr length made out of 50 x 6 mm GI strip with drill holes of M8 at 25mm interval mounted on insulators with glass covered box & Naming to be done as per the Requirement. Detailed drawings attached in earthing schematic & construction of earth box to be made as per schematic | Nos. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
9.1 | Busbar of 0.5 Mtr length made out of 75 x10 mm GI strip with drill holes of M8 at 25mm interval mounted on insulators with glass covered box & Naming to be done as per the Requirement.Detailed drawings attached in earthing schematic & construction of earth box to be made as per schematic. | Nos. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
9.11 | Busbar of 0.5 Mtr length made out of 100 x10 mm GI strip with drill holes of M8 at 25mm interval mounted on insulators with glass covered box & Naming to be done as per the Requirement.Detailed drawings attached in earthing schematic & construction of earth box to be made as per schematic | Nos. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
9.12 | 8 SWG Cu Wire | Mts. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
9.13 | 25 x 3mm Cu. Earth flat | Mts. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
9.14 | 25 x 6mm Cu. Earth flat | Mts. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
9.15 | 50 x 6mm Cu. Earth flat | Mts. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
9.16 | 75 x 10mm Cu. Earth flat | Mts. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
C | PVC Insulated Copper Conductor Unarmoured Cables (YY Type) - IS 694 | [5 empty] | 0 | 0 | 0
| Supply, Laying, Testing and Commissioning of 1.1kV grade, copper conductor, PVC insulated, unarmoured, power cables as per IS - 694. The cables shall be laid on tray / hume pipe /in ready made trenches, with nylon cable ties / MS Clamps @ 600mm interval etc., as required. The cost of the nylon tie shall be included in the cost of installation. Rate quoted shall exclude cost of tray / hume pipe | [5 empty] | 0 | 0 | 0
| Cable identification labels at both ends clearly mentioning the cable specs & also at appropriate intervals along the cable route should be provided. The labels shall be engraved / anodized aluminium with white letters on black background. The cost of the Cable identification labels shall be included in the cost of installation. | [5 empty] | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
9.17 | 1 Core x 300 Sq. mm | Mts. | RO | RO |  |  | 0 | 0 | 0
9.18 | Endterminations | Nos. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
9.19 | 1 Core x 240 Sq. mm | Mts. | RO | RO |  |  | 0 | 0 | 0
9.2 | Endterminations | Nos. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
9.21 | 1 Core x 185 Sq. mm | Mts. | RO | RO |  |  | 0 | 0 | 0
9.22 | Endterminations | Nos. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
9.23 | 1 Core x 150 Sq. mm | Mts. | RO | RO |  |  | 0 | 0 | 0
9.24 | Endterminations | Nos. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
9.25 | 1 Core x 120 Sq. mm | Mts. | RO | RO |  |  | 0 | 0 | 0
9.26 | Endterminations | Nos. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
9.27 | 1 Core x 95 Sq. mm | Mts | RO | RO |  |  | 0 | 0 | 0
9.28 | Endterminations | Nos. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
9.29 | 1 Core x 70 Sq. mm | Mts. | RO | RO |  |  | 0 | 0 | 0
9.3 | Endterminations | Nos. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
9.31 | 1 Core x 50 Sq. mm | Mts. | RO | RO |  |  | 0 | 0 | 0
9.32 | Endterminations | Nos. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
9.33 | 1 Core x 35 Sq. mm | Mts. | RO | RO |  |  | 0 | 0 | 0
9.34 | Endterminations | Nos. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
9.35 | 1 Core x 25Sq. mm | Mts. | RO | RO |  |  | 0 | 0 | 0
9.36 | Endterminations | Nos. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
9.37 | 1 Core x 16Sq. mm | Mts. | 300 | 300 | 283 | 29 | 84900 | 8700 | 93600
9.38 | End terminations | Nos. | 10 | 10 | 73 | 19 | 730 | 190 | 920
[7 empty] | 0 | 0 | 0
9.39 | 1 Core x 10Sq. mm | Mts. | 200 | 200 | 187 | 29 | 37400 | 5800 | 43200
9.4 | Endterminations | Nos. | 10 | 10 | 73 | 19 | 730 | 190 | 920
[7 empty] | 0 | 0 | 0
9.41 | 1 Core x 6Sq. mm | Mts. | 150 | 150 | 105 | 19 | 15750 | 2850 | 18600
9.42 | Endterminations | Nos. | 10 | 10 | 73 | 19 | 730 | 190 | 920
[7 empty] | 0 | 0 | 0
9.43 | 1 Core x 4Sq. mm | Mts. | 100 | 100 | 71 | 19 | 7100 | 1900 | 9000
9.44 | Endterminations | Nos. | 20 | 20 | 63 | 19 | 1260 | 380 | 1640
[7 empty] | 0 | 0 | 0
9.45 | 1 Core x 2.5Sq. mm | Mts. | RO | RO |  |  | 0 | 0 | 0
9.46 | Endterminations | Nos. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
9.47 | 1 Core x 1.5Sq. mm | Mts. | RO | RO |  |  | 0 | 0 | 0
9.48 | Endterminations | Nos. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
9.49 | Antistatic floor earthing with 25 x 0.05mm thick copper film | Mts. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
9.5 | PVC insulating tapes of 19mm width in rolls of 10 meters for Neutral taping earth strips | Mtrs | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
9.51 | 600mm long, 25 x 3 Copper, Earth bus suitable for terminating for cables with holes at regular intervals connected to main bus. The same need to be mounted in MS box with transparent cover.Naming to be done as per the requirement.Detailed drawings attached in earthing schematic & construction of earth box to be made as per schematic[For UPS Cables termination] | Nos. | 2 | 2 | 3690 | 441 | 7380 | 882 | 8262
[7 empty] | 0 | 0 | 0
9.52 | 600mm long, 25 x 6 Copper, Earth bus suitable for terminating for cables with holes at regular intervals connected to main bus. The same need to be mounted in MS box with transparent cover.Naming to be done as per the requirement.Detailed drawings attached in earthing schematic & construction of earth box to be made as per schematic[For UPS Cables termination] | Nos. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
9.53 | 600mm long, 50 x 6 Copper, Earth bus suitable for terminating for cables with holes at regular intervals connected to main bus. The same need to be mounted in MS box with transparent cover.Naming to be done as per the Requirement.Detailed drawings attached in earthing schematic & construction of earth box to be made as per schematic [For UPS Cables termination] | Nos. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
X | MISCELLANEOUS ITEMS | [5 empty] | 0 | 0 | 0
| All the items shall be of IS certified | [5 empty] | 0 | 0 | 0
| All the items shall be in line with CEIG requirement | [5 empty] | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
| Providing, Laying and fixing of following dia RCC Pipe NP2 class in ground complete with RCC collars, jointing with cement mortar 1:2 (1 cement : 2 fine sand) including trenching (75 cm deep) & refilling etc. as required for cable laying at the road crossing or wherever necessary as per site condition. Cost to include RCC collar and necessary civil works as required. | [5 empty] | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
10.1 | 200mm dia | Mts. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
10.2 | 300mm dia | Mts. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
10.3 | 100 mm dia HDPE pipe | Mts. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
10.4 | Supply and fixing of 1.1 KV grade nominal 2.0 mm +/- 10% thick insulated Synthetic Mat conforming to IS 15652: 2006 and meeting the requirements of IS 5216 (Part1,2&3), IS 8437, IEC-479 Pub-1, along-with suitable adhesive/ chemibound, Pu resin, waterproofing compound and sealing material as per in service recommendation - 2 m x 1m | Nos. | 3 | 3 | 2812 | 441 | 8436 | 1323 | 9759
[7 empty] | 0 | 0 | 0
10.5 | Supply & fixing of shock treatment chart duly framed with 5mm thick glass required both in Hindi, English & Kannada for treating person suffering due to electric shock suitable to mount on wall. | Nos. | 2 | 2 | 1319 | 441 | 2638 | 882 | 3520
[7 empty] | 0 | 0 | 0
10.6 | Supply & fixing of First Aid box conforming to IS 2217 -1963. | Nos. | 2 | 2 | 1758 | 441 | 3516 | 882 | 4398
[7 empty] | 0 | 0 | 0
10.7 | Providing and fixing L.V. danger notice plate of 200 mm X 150 mm, made of mild steel, 2 mm thick, and vitreous enameled white on both sides, and with inscription in single red Colour on front side as required. | Nos. | 2 | 2 | 1319 | 441 | 2638 | 882 | 3520
[7 empty] | 0 | 0 | 0
10.8 | Fire Bucket with stand suitable for 2 buckets of round shape bottom, painted red marked 'FIRE' and duly filled with river sand. | Nos. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
10.9 | Supply and fixing of self illuminated LAMINATED Single line diagram chart duly framed with 5mm thick glass suitable to mount on wall with studs. (AO size) | Nos. | 2 | 2 | 2198 | 441 | 4396 | 882 | 5278
[7 empty] | 0 | 0 | 0
10.1 | MS support with 2 coats of anti rusting primer & epoxy enamel paint - Approval should be taken before operating the item. | Kgs | 40 | 40 | 147 | 32 | 5880 | 1280 | 7160
[7 empty] | 0 | 0 | 0
10.11 | Supply & installation of 150mm wide x 100mm depth 16G DB cabinet MS Powder coated of DB colour. | Mtr | 40 | 40 | 809 | 94 | 32360 | 3760 | 36120
[7 empty] | 0 | 0 | 0
10.12 | Fire Barrier Sealants (acrylic Latex Caulk) for Metal pipes,cables through Gypsum walls of 50 mm thick with smaller gaps of less than 20 mm. | Sq.Mtr | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
10.13 | Supply of Rubber hand gloves suitable for 1.1KV. | Pairs | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
10.14 | 2 hour fire rated fire retardant material sealing all electrical cutouts/ducts and openings made in the slab / wall / partition to take conduits / cable trays / raceways etc as required complete / as directed by the site incharge. Vertical openings will be closed wit 4.5 mm chequered plate and sealent(3m/Hilti) | Sq.Mtr | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
10.15 | Neccesary wall opening , wall chasing for Electrical /Data /ACS/CCtV/AV services entry and closure with chicken mesh and cement mortar with experience professional for all the civil walls in the project . | Ls | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
10.16 | Emergency power off | [5 empty] | 0 | 0 | 0
| The EPO station button has one double pole, double throw momentary contact push-button switch. One normally opened (NO) contact is connected from the power source (240 V AC) to the shunt trip contactor coil. When actuated, the contact connects the 240V AC power. One normally closed (NC) contact is connected to the BMS or monitoring/alarm system for the raised floor operation such that an alarm point is displayed or recorded to identify the specific EPO station which has been activated. | Nos. | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
10.17 | As built drawings: | [5 empty] | 0 | 0 | 0
| Preparation and Submission of self illuminated A1 size as built drawings of total work executed (5 Sets hard and 1 Sets soft copy in Pen drive/CD's(5 No). | LS | 1 | 1 | 13176 | 4393 | 13176 | 4393 | 17569
[7 empty] | 0 | 0 | 0
10.18 | Supply, Laying, Testing and Commissioning of additional adoptor box for existing tap-off box for Cable termination .. Additional Adoptor box shall be power coated type & finising shall be matched to existing Tap-off boxes | No | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
10.19 | Supply, Laying, Testing and Commissioning of Software user box alongwith glands for access control system(Approxiamte size is 450mm x 300 mm ) .Box shall be MS powder coated type & RAL colour to be provided by IT team | No | RO | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
XI | Temporary Lighting & Power arrangement | [5 empty] | 0 | 0 | 0
A | Providing Temporary Lighting & Power arrangement with sufficient temporary Lighting ( Min 200Lux Ave. ) & power shall be provided to all agencies during execution with the following requirements | Lot | 1 | 1 | 54355 | 10873 | 54355 | 10873 | 65228
| 1. Considering 24/7 lighting for all the equal distance (minimum 15 feet ) . , All the passage with the 4feet (40w)Patti/tube light fittings on equal distance and all the enclosed area to be provided with light fixtures until the project works are completed. | [5 empty] | 0 | 0 | 0
| 2. A main panel built up with all the safety protection features having 10 feeders for the main contractors (HVAC/INTERIOR/ELECTRICAL/FIRE FIGHTING) capacity of feeding 6welding machines /20drilling machines with energy meter ,main incoming feeder with energy meter and 2 Feeders to all the floors PDB and lighting DB with energy meter. | [5 empty] | 0 | 0 | 0
| 3. All the floor office area to be provided with 4PDB distributed in equal distance & each should be equipped with the 8nos industrial socket with all the safety protection features. | [5 empty] | 0 | 0 | 0
| 4. Halogen lights (200w) to be provided wherever necessary as per the project requirement (sufficient numbers to be stocked) | [5 empty] | 0 | 0 | 0
| 5. All the entry/temporary toilets/ path ways ,staircases, vendor store area, material stacking place to be provided with adequate lighting with 4feet Patti fitting on the equal distance | [5 empty] | 0 | 0 | 0
| 6. Cabling from the main Incomer feeder to the main panel and all the floors PDBs and lighting controls and DB to be considered and the cabling to be routed in the ceiling level. | [5 empty] | 0 | 0 | 0
| 7. Temporary earthing to the main panel & DG's to be considered. | [5 empty] | 0 | 0 | 0
| 8. Above installation works to be completed within an given period of time in all the work area. | [5 empty] | 0 | 0 | 0
| 9. A dedicated qualified electrician with tools to be provided 24/7 for maintaining the temporary lighting and DG. | [5 empty] | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
11.1 | Supply, installation, testing & commissioning of 100KVA DG sets along with AMF panel on rental basis. The price shall include temporary arrangement of exhaust system, fuel system and necessary statutory approvals to run the DG set. The price also include maintenance of DG set, removing of DG set & its associated works in all respect once the rental agreement is expired. The price shall be quoted on monthly basis. | Month |  |  |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
11.2 | Supply, installation, testing & commissioning of 62.5KVA DG sets along with AMF panel on rental basis. The price shall include temporary arrangement of exhaust system, fuel system and necessary statutory approvals to run the DG set. The price also include maintenance of DG set, removing of DG set & its associated works in all respect once the rental agreement is expired. The price shall be quoted on monthly basis. | Month |  |  |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
11.3 | Diesel consumption for 100 KVA DG & Price will be paid as per actuals. | Hrs |  |  |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
11.4 | Diesel consumption for 62.5 KVA DG & Price will be paid as per actuals. | Hrs |  |  |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
XII | Professional Charges: | [5 empty] | 0 | 0 | 0
12.1 | Professional charges towards filing application, preparation of drawings in necessary formats for approval, follow up and arranging approval of drawings, scheme by Local electricity authority / Electrical Inspectorate, obtaining clearance from electricity authority / Electrical Inspectorate/ CEIG. All necessary charges shall be part of contractor scope only. client will not pay any charges for the same | LS | 1 | 1 | 0 | 158097 | 0 | 158097 | 158097
12.2 | Inverter O/P DB
12way SPN DB
Incommer 40A DP RCBO- 1no
| Outgoing : 20/25/32A 'C' Curve SP MCB's 10kA -6 Nos. | Nos | 1 | 1 | 5518 | 660 | 5518 | 660 | 6178
12.3 | UPS O/P (VTPNDB MCCB INCOMER)
8WAY VTPN DB
Incommer
1 No.125A TP+2N TMD MCCB 16kA
Outgoings
40A TP MCB 10kA D curve - 4Nos UPSDB
63A TP MCB 10kA D curve - 2Nos SDB
| 40A TP MCB 10kA D curve - 2Nos SPARE | Nos | RO | RO |  |  | 0 | 0 | 0
| Supply, Installation, Testing & Commissioning of 12M modular box complete with 6/16A 2M socket & Switch, RJ45 CAT6 UTP data socket 2 No, RJ11 telephone socket with shutter, USB & C type charger (1500mA, 1M Type-C), and pre-terminated HDMI socket, | Nos | 4 | 4 | 11859 | 1319 | 47436 | 5276 | 52712
| SITC for Mobile charging port Type USB and C for meeting room | Nos | 22 | 22 | 1135 | 230 | 24970 | 5060 | 30030
|  |  |  | 0 | 0 | 0 | 0 | 0 | 0
0
| TOTAL - ELECTRICAL LT WORKS | [5 empty] | 4715431 | 960923 | 5676354

## LGT BOQ
PROJECT | : PAYTM BANGALORE
SUBJECT | : BILL OF QUANTITES - LIGHTING
DATE | : 30.03.2026
VERSION | : V0
Sl.No. | DESCRIPTION | REFERENCE IMAGES | UNIT | 6F | Total | RATE |  | TOTAL |  | TOTAL AMOUNT | REMARKS
[6 empty] | Supply | Installation | Supply | Installation
XIII | Supply, Installation, testing & commissioning of Light fixtures and lamps with all accessories, fixing on the wall / ceiling/false ceiling/open ceiling with wooden blocks, screws ,hardware's ,suspension chain hooks/ wires with anchor fasteners as required as per the site conditions (including the earthing of fixture)
Light fixtures complete with accessories like control gear, low loss (<5W ) HF Electronic ballast ,HF Electronic analogue driver, HF dimmable dali driver, HPF condensor (PF shall be >0.85 lag. ) , energy efficient high lumen output LED/fluorescent tubes / CFL lamps etc.,
Note : The make & the catalogue no. mentioned here is only indicative & any of the make mentioned in recommended list of makes is preferred.
The rate shall include for fittings along with transformers where required, diffuser, drivers, power factor improvement capacitors, wires, downrods etc., complete with all accessories to complete the installation as required.
The Electronic analogue driver & dimmable dali driver shall be with THD between 6-8 %.
Glare free symmetrical distribution
IP 20
Light Distribution: Direct symmetrical.
CRI(Ra) >= 80
surge protection: 2.5kV.
Electrical protection: Class II
Uniformity factor 0.8
LED colour to be 6500k or as per Architect/client approval.
LED working life 50,000 burning hours.
Glare factor < 19
LPD < .6Watt/sqft.
Driver power factor >= 0.88
Driver of the luminaire shall have THD<10% and PF>0.9.
120 Lumens / Watts
Spacing between connectors (terminal box) & Light fixture should be adequate enough so that connector (terminal block) should not touch light fixture. Outer body of the light fixture RAL colour as per the architect approval. The quoted rate shall include any modification in colour as per the architect Choice. All light fixture should be as per look & feel presentation
Note : Cost shall Include all necessary supports required for Functional as well as Decorative light fixtures
A | OFFICE AREA LIGHTS
13.1 | Supply, Installation, testing & commisioning of Pendant Luminaire VIRAJ 70 with LED (Light Emitting Diode ) system power 30W / Meter , Should be,Luminous Flux of luminaire is ,6500k , Neutral White ,CRI >80, 230V, Direct Emission, Profile in Anodised Aluminium with Natural , Black , Champagne Light , Champagne Dark and Brown Anodising , Pre-wired batten made of Anodised Aluminium , Snap-Fit System , Screw less End-caps, Halogen free internal wiring , PMMA Diamond Prism Diffuser for Homogenous Light distribution.length - 1200mm (L ) x 80mm (H)x 60mm (W) |  | Mtrs | 55 | 55 |  | 316 | 0 | 17380 | 17380
[5 empty] | 0 |  | 0 | 0 | 0 | 0
13.2 | Supply, Installation, testing & commisioning of Pendant Luminaire VIRAJ 70 with LED (Light Emitting Diode ) system power 30W / Meter , Should be,Luminous Flux of luminaire is 6500k , Neutral White ,CRI >80, 230V, Direct Emission, Profile in Anodised Aluminium with Natural , Black , Champagne Light , Champagne Dark and Brown Anodising , Pre-wired batten made of Anodised Aluminium , Snap-Fit System , Screw less End-caps, Halogen free internal wiring , PMMA Diamond Prism Diffuser for Homogenous Light distribution.length - 1200mm (L ) x 80mm (H)x 60mm (W)(DALI DIMMABLE DRIVER) |  | Mtrs | 45 | 45 |  | 316 | 0 | 14220 | 14220
0
13.3 | Supply, Installation, testing & commisioning of Pendant Luminaire VIRAJ 70 with LED (Light Emitting Diode ) system power 30W / Meter , Should be,Luminous Flux of luminaire is ,6500k , Neutral White ,CRI >80, 230V, Direct Emission, Profile in Anodised Aluminium with Natural , Black , Champagne Light , Champagne Dark and Brown Anodising , Pre-wired batten made of Anodised Aluminium , Snap-Fit System , Screw less End-caps, Halogen free internal wiring , PMMA Diamond Prism Diffuser for Homogenous Light distribution.length - 1500mm (L ) x 80mm (H)x 60mm (W) |  | Mtrs | 16 | 16 |  | 316 | 0 | 5056 | 5056
[5 empty] | 0 |  | 0 | 0 | 0 | 0
13.4 | Supply of Recessed linear Luminaire with LED (Light Emitting Diode ) system power 26W / Meter ,230V, Direct Emission, Profile in Anodized Aluminum with Natural , Black , Champagne Light , Champagne Dark and Brown Anodizing , Pre-wired batten made of Anodized Aluminum , Snap-Fit System , Screw less End-caps, Halogen free internal wiring , PMMA Diamond Prism Diffuser for Homogenous Light distribution. |  | Mtrs | 0 | 0 |  | 0 | 0 | 0 | 0
[5 empty] | 0 |  | 0 | 0 | 0 | 0
13.5 | Supply of Recessed linear Luminaire with LED (Light Emitting Diode ) system power 20 W / Meter , (with Dali dimmable driver) 230V, Direct Emission, Profile in Anodized Aluminum with Natural , Black , Champagne Light , Champagne Dark and Brown Anodizing , Pre-wired batten made of Anodized Aluminum , Snap-Fit System , Screw less End-caps, Halogen free internal wiring , PMMA Diamond Prism Diffuser for Homogenous Light distribution. |  | Mtrs | 45 | 45 |  | 271 | 0 | 12195 | 12195
[5 empty] | 0 |  | 0 | 0 | 0 | 0
13.6 | Supply, Installation, testing & commissioning of Recessed ceiling luminaire GENISO LED for LED(Light Emitting Diode ) 30W 230V, direct light emission, Sheet metal housing, powder coated white, opal diffuser in synthetic material, fixation with of support, halogen-free internal wiring, HF electronic control gear Protection class I, IP40 L = 595 mm B = 595 mm , H=60mm |  | Nos | 6 | 6 |  | 226 | 0 | 1356 | 1356
[5 empty] | 0 |  | 0 | 0 | 0 | 0
13.7 | Supply, Installation, testing & commissioning of Recessed ceiling luminaire GENISO LED for LED(Light Emitting Diode ) 30W (with Dali dimmable driver) 230V, direct light emission, Sheet metal housing, powder coated white, opal diffuser in synthetic material, fixation with of support, halogen-free internal wiring, HF electronic control gear Protection class I, IP40 L = 595 mm B = 595 mm , H=60mm |  | Nos | 34 | 34 |  | 226 | 0 | 7684 | 7684
[5 empty] | 0 |  | 0 | 0 | 0 | 0
13.8 | Supply, Installation, testing & commissioning of Recessed ceiling luminaire GENISO LED for LED(Light Emitting Diode ) 30W. 230V, direct light emission, Sheet metal housing, powder coated white, opal diffuser in synthetic material, fixation with of support, halogen-free internal wiring, HF electronic control gear Protection class I, IP65 L = 595 mm B = 595 mm , H=60mm (For kitchen area) |  | Nos |  | 0 |  | 0 | 0 | 0 | 0
[5 empty] | 0 |  | 0 | 0 | 0 | 0
13.9 | 4ft Linear LED Batten with a nominal system lumen output of 2000 lumens and a minimum system efficacy of 105 lm/W. System wattage should not exceed 19W. The luminaire housing should be made of CRCA with a PC glossy diffuser. |  | Nos | 12 | 12 |  | 136 | 0 | 1632 | 1632
[5 empty] | 0 |  | 0 | 0 | 0 | 0
14 | Supply, Installation, testing & commissioning of Recessed light with LED (Light Emitting Diode) System Power -12W with 6 inch diameter |  | Nos | 109 | 109 |  | 226 | 0 | 24634 | 24634
[5 empty] | 0 |  | 0 | 0 | 0 | 0
13.2 | Supply, Installation, testing & commissioning of Recessed light with LED (Light Emitting Diode) System Power -12W (with Dali dimmable driver) with 6 inch diameter |  | Nos | 40 | 40 |  | 226 | 0 | 9040 | 9040
[5 empty] | 0 |  | 0 | 0 | 0 | 0
13.21 | Supply, Installation, testing & commissioning of Recessed light with LED (Light Emitting Diode) System Power -12W with 6 inch diameter |  | Nos |  | 0 |  | 0 | 0 | 0 | 0
[5 empty] | 0 |  | 0 | 0 | 0 | 0
13.21 | Supply, installation, testing & commisioning of MACTY ROUND pendant with LED (Light Emitting Diode) COB, 230V, System power-15W, Luminous Flux of Luminnaire-1168.5lm, direct light emission, housing in Aluminium Die casting white, electronic control gear, On/OffProtection class I, IP20 MACTY ROUND , Dia.=150mm, H=300mm |  | Nos | 55 | 55 |  | 271 | 0 | 14905 | 14905
[5 empty] | 0 |  | 0 | 0 | 0 | 0
13.22 | Supply, installation, testing & commisioning of MACTY ROUND pendant with LED (Light Emitting Diode) COB, 230V, System power-15W, (with dali dimmable drivers) Luminous Flux of Luminnaire-1168.5lm, direct light emission, housing in Aluminium Die casting white, electronic control gear, On/OffProtection class I, IP20 MACTY ROUND , Dia.=150mm, H=300mm |  | Nos | 35 | 35 |  | 271 | 0 | 9485 | 9485
[5 empty] | 0 |  | 0 | 0 | 0 | 0
PART B | DECORATIVE LIGHTS |  |  |  | 0 |  | 0 | 0 | 0 | 0
[5 empty] | 0 |  | 0 | 0 | 0 | 0
13.23 | Supply, Installation, testing & commissioning of LED strip(Light Emitting Diode ) system power 5.5W per mtr ,3000/4000k , Warm White ,CRI >70, 230V, Direct Emission Halogen free internal wiring |  | Mtrs | 50 | 50 |  | 46 | 0 | 2300 | 2300
[5 empty] | 0 |  | 0 | 0 | 0 | 0
13.24 | SITC of decorative lights 20W as per design approval |  | Nos | 1 | 1 |  | 271 | 0 | 271 | 271 | Reception
[5 empty] | 0 |  | 0 | 0 | 0 | 0
13.25 | SITC of decorative lights 20W as per Image |  | Nos | 11 | 11 |  | 271 | 0 | 2981 | 2981
13.5 | SITC of decorative lights 20W as per design approval |  | Nos | 10 | 10 |  | 271 | 0 | 2710 | 2710
| TOTAL - LIGHTS | [6 empty] | 0 | 125849 | 125849

## HVAC BOQ
PROJECT | PAYTM
SUBJECT | HVAC BOQ
VERSION | V0
Sl.No. | DESCRIPTION | UNIT | QNT | RATE |  | AMOUNT |  | Total
|  |  |  | Supply | Installation | Supply | Installation
Note :Prices quoted in this tender shall be inclusive of cost of materials, labours, supervision, Supply ,installation, testing and commissioning, materials erection, tools, plant appliances, scaffolding, sleeves, cutting, patching, painting, storage of material, service connections, transport to site,
PART -A | AIR DISTRIBUTION WORKS
1 | GI FACTORY FABRICATED SUPPLY AIR PLENUMS
| SITC of 50 mm thk double skin panel factory fabricated plenum as per shop drawing. Plenum shall be made of outer skin 20 G powder coated G.I sheet and inner skin shall be of with 22 G plain GSS with aluminium extrusions. Density of puf panel shall be 48 kg / cub mt. with 40mm thick puf insulation ,Plenum shall suitable size to handle the required cfm not exceeding 750 fpm velocity. The price quoted shall include MS supporting arrangement for suspending the plenum from the ceiling slab ,Canvas connection to be part of scope for AHU connection ,Access doors shall be not less than 60 cm x 60 cm in size.Appropriate cutout to be made to connecte the branch ducts with dampers as per approved drawing | Sqmt | 25 | 3300 | 350 | 82500 | 8750 | 91250
|  |  | 0 |  |  | 0 | 0 | 0
2 | SITC of duct silencers / Sound attenuators in supply and return air path in AHU rooms as per the approved drawings. |  | 0 |  |  | 0 | 0 | 0
| Sound attenuator qty shall be on surface area basis. |  | 0 |  |  | 0 | 0 | 0
| COMPUTER SELECTION SHOULD BE ATTACHED |  | 0 |  |  | 0 | 0 | 0
| Sound Attenuators made dissipative type to be provided on the supply & Return air duct entering the AHU Room. |  | 0 |  |  | 0 | 0 | 0
| Sound Attenuators shall consist of outer casing, sound absorbing material and internal baffles, splitters and supports ,The sound attenuators shall be suitable for minimum 18dB reduction at 250Hz octave band. |  | 0 |  |  | 0 | 0 | 0
| Casing shall be of galvanized steel of not less than 20G in thickness. Casings shall be tested to 150mmwg and shall show no leakage or distortion in this condition. |  | 0 |  |  | 0 | 0 | 0
| Sound absorbing material shall be high density Fiber glass held in place with at least 5% compression to prevent voids due to settling. Absorption material density shall be minimum 48 kg/cum. Fiberglass faced with minimum 24 g perforated galvanized sheet metal of minimum 40% open area. |  | 0 |  |  | 0 | 0 | 0
| Supply, Installation & commissioning | Sqm | 15 | 3450 | 2350 | 51750 | 35250 | 87000
|  |  | 0 |  |  | 0 | 0 | 0
3 | SITC of Motorised Fire dampers -Multi blade motorised 16G GI TDF flanges type Fire Dampers with necessary accessories for supply air ducts along with motorized actuator including fire damper control panel for supply air ducts . The fire rating of the damper shall be of 90min and shall be with 600 mm sleeves suitable for the wall mounting, CBRI approved.Fire Damper shall be complete with 240/24 transformer, damper on/off indicating lamps and distribution Price shall be inclusive of copper power cabling ,control wiring,actuator with control panel, sensor and inter-locking / wiring / connection for tripping of AHU fan motor , FA intergation. | Sqm | 6 | 10800 | 2200 | 64800 | 13200 | 78000
| Actuators with Control Panel for above fire dampers- actuotors should have potential free contact to know the status of the actuator Fast acting actuators Should be of High Torque Type ( 20 sec closure max, 75sec opening max ) Spring return type : 10NM (up to 0.6sqm);16NM (up to 1.6 sqm);20NM (up to 3.2sqm) | No's | 12 | 13500 | 1250 | 162000 | 15000 | 177000
|  |  | 0 |  |  | 0 | 0 | 0
4 | Fire dampers -Fusible link & confirm to UL listed. |  | 0 |  |  | 0 | 0 | 0
| Supply, Installation, Testing & Commissioning of Fusible link type fire damper. Should be UL (555) listed & CBRI approved. With one or 2 side flanges as per the site condition. Fire rating should be 90min as per the UL 555. Blades shall be held in position through fusible link of temp. of 74 deg. c. Gauge of blades & frame should be 16 G. Should supply with GI made Transition piece(22Gauge) & Back draft(Gravity) damper. | Sqm | 1 | 7841 | 1623 | 7841 | 1623 | 9464
|  |  | 0 |  |  | 0 | 0 | 0
|  |  | 0 |  |  | 0 | 0 | 0
5 | AIR DISTRIBUTION SYSTEM: |  | 0 |  |  | 0 | 0 | 0
| RECTANGULAR DUCT -FACTORY FABRICATED DUCTING - TDF /TDC FLANGES |  | 0 |  |  | 0 | 0 | 0
| Supply, Installation Testing & Commissioning of factory fabricated GSS Ducting with TDF /TDC flange with GI bolt & nuts (the cleat into the flange Used for C and G together with Bolt) and necessary supporting arrangement using GI full threaded rods and slotted rail. |  |  |  |  | 0 | 0 | 0
| Ducting shall be designed for 500pa pressure, Galvanized steel sheet shall be of Class VIII – 120 gm /sqm zinc coating IS-277.All ducts above 1000 mm shall have Stiffener rod made of GI 1.6mm thick . |  |  |  |  | 0 | 0 | 0
| Spacing between duct supports should not exceed 2m i.e GI rods with GI "C" channels. In case of duct sizes above 1800mm, MS angles duly painted with black enamel paint should be used along with neoprene pad in between the duct & MS angle. All duct support to be provided with check nuts (lock nuts). |  |  |  |  | 0 | 0 | 0
| All duct construction and installation shall be as per SMACNA standards |  |  |  |  | 0 | 0 | 0
| The scope shall include duct supports (including MS angle/channel arrangements for vibration-free installation), scaffolding charges, cleat joints, elbows, bends, shoe pieces, vanes, stripper rods, gaskets, bolts & nuts, end caps, Y-branches, cut ducts, droppers, offsets, mouth pieces, duct covers for transportation/installation/storage, and a 450x450 vertical trap door with handle in main ducts for servicing and cleaning |  | 0 |  |  | 0 | 0 | 0
| Pressure Testing of Ducts - Pressure testing of sheet metal ducts with necessary components like semi-rigid flexible ducts, fans and the measuring kit. Pressure testing shall be carried out for complete air distribution system excluding flexible ducts, diffuser box, diffusers and grilles. Pressure testing shall be carried out prior to thermal insulation and light test as per SMACNA standards and approval shall be obtained from PMC and consultants. , |  | 0 |  |  | 0 | 0 | 0
| Air Balancing of Air Distribution System - Third party Air balancing should be done for two times - Pre occupancy & Post occupancy along with client/PMC & Facility teams. Duct pressure testing should be with Duct leak testing machine and Air-balancing should be with Digital Hood method. All necessary tools(digital hood) should be consider in costing. Air Balancing of each individual supply air outlet to within +10% or -5% of the design air quantity and tabulating the same in a form of report and also the final air balancing figures to be indicated against each measured outlets in the as built drawings. Balancing also includes balancing of return air, supply air and outdoor fresh air quantity. Air flow hoods to be used for measuring the air flow across the Grill/diffusers. |  | 0 |  |  | 0 | 0 | 0
| Testing shall be coordinated through licensed Test and Balance supplier with the Commissioning Agent , All the duct work and equipment to be labelled with the direction of flow ,Duct system will be capable of air balancing at each floor and sub main by means of a manual damper, Adequate test ports to be provided for testing and commissioning ,Materials of construction welded galvanized steel . Note :- All the ducts laying in open ceiling has to be painted as per architect colour recomendation /specification. Painting to be considered as one coat primer and two coats of paints (Spray paint/ roller finishing). Paint cost should be part of the duct cost itself |  |  |  |  | 0 | 0 | 0
| 0.50 mm (26 WG) | Sqmt | RO |  |  | 0 | 0 | 0
| 0.63 mm (24 WG) | Sqmt | 170 | 840 | 217 | 142800 | 36890 | 179690
| 0.80 mm (22 WG) | Sqmt | 100 | 940 | 217 | 94000 | 21700 | 115700
| 1.00 mm (20 WG) | Sqmt | 150 | 1000 | 217 | 150000 | 32550 | 182550
| 1.25 mm (18 WG) | Sqmt | RO |  |  | 0 | 0 | 0
|  |  | 0 |  |  | 0 | 0 | 0
6 | Elliptical ducts |  | 0 |  |  | 0 | 0 | 0
| ELLIPTICAL /OVAL DUCT -FACTORY FABRICATED DUCTING - TDF /TDC FLANGES WITH INTERNAL INSULATION |  |  |  |  | 0 | 0 | 0
| Supply, installation, testing & Commissioning of Factory fabricated oval GSS ducting with Hitech Supports and with with TDF /TDC flange with GI bolt & nuts ( the cleat into the flange Used for C and G together with Bolt).Necessary bends should be made as per the drawing, All ducts should be supported with wire rope supports and shall be hang through the cleats or wire rope threaded studs can be screwed into the anchor fasteners. |  |  |  |  | 0 | 0 | 0
| Ducting shall be designed for 500pa pressure, Galvanized steel sheet shall be of Class VIII – 120 gm /sqm zinc coating IS-277.All ducts above 1000 mm shall have Stiffener rod made of GI 1.6mm thick ,Ducting to brought at site in box form. |  |  |  |  | 0 | 0 | 0
| Spacing between duct supports should not exceed 2m i.e Wire Rope Hanger support . In case of Wire Rope Hanger support for duct sizes above 1800mm, MS angles duly painted with black enamel paint should be used along with neoprene pad in between the duct & MS angle. All duct support to be provided with check nuts (lock nuts). |  |  |  |  | 0 | 0 | 0
| All duct construction and installation shall be as per SMACNA standards |  |  |  |  | 0 | 0 | 0
| The scope shall include Wire rope supports ,Ring clamp ,universal clamps,studs, screws , anchor fasteners , scaffolding charges, cleat joints, elbows, bends, shoe pieces, vanes, stripper rods, gaskets, bolts & nuts, end caps, Y-branches, cut ducts, droppers, offsets, mouth pieces, duct covers for transportation/installation/storage, and a 450x450 vertical trap door with handle in main ducts for servicing and cleaning |  |  |  |  | 0 | 0 | 0
| Ducts to be provided with internal thermal insulation with 13mm thick closed cell elastromeric nitrile rubber insulation manafactured as per ASTM E 84 test with density between 40-60 kg / m³ , Material shall be FM GLOBAL approved, food grade material with antimicrobial properties, Class 'O'. Insulation material should meet NFPA 90A ,Insulation sheets should have factory applied self-adhesive backing for faster installation and better quality. The adhesive used in self-adhesive backing should be Fire Retardant, LEED compliant and zero VOC. open cell 15mm thick Elastromeric nitrile rubber insulation manafactured as per ASTM E 84 test with density140- 180 kg / m³, Material shall be FM rated ,First 5 Meters from outlet of AC unit to be considered with acoustic insulation |  |  |  |  | 0 | 0 | 0
| Pressure Testing of Ducts - Pressure testing of sheet metal ducts with necessary components like semi-rigid flexible ducts, fans and the measuring kit. Pressure testing shall be carried out for complete air distribution system excluding flexible ducts, diffuser box, diffusers and grilles. Pressure testing shall be carried out prior to thermal insulation and light test as per SMACNA standards and approval shall be obtained from PMC and consultants. |  | 0 |  |  | 0 | 0 | 0
| Air Balancing of Air Distribution System - Third party Air balancing should be done for two times - Pre occupancy & Post occupancy along with client/PMC & Facility teams. Duct pressure testing should be with Duct leak testing machine and Air-balancing should be with Digital Hood method. All necessary tools(digital hood) should be consider in costing. Air Balancing of each individual supply air outlet to within +10% or -5% of the design air quantity and tabulating the same in a form of report and also the final air balancing figures to be indicated against each measured outlets in the as built drawings. Balancing also includes balancing of return air, supply air and outdoor fresh air quantity. Air flow hoods to be used for measuring the air flow across the Grill/diffusers. |  | 0 |  |  | 0 | 0 | 0
| Testing shall be coordinated through licensed Test and Balance supplier with the Commissioning Agent , All the duct work and equipment to be labelled with the direction of flow ,Duct system will be capable of air balancing at each floor and sub main by means of a manual damper, Adequate test ports to be provided for testing and commissioning ,Materials of construction welded galvanized steel .Air flow testing should be done with Hoods , Note : All supply ducts laying in open area has to be internally insulated & all ducts will be painted as per architect colour specification.Painting to be considered as one coat primer and two coats of paints (Spray paint/ roller finishing). Internal insulation labour charge & Painting cost should be part of the duct costing itself. |  | 0 |  |  | 0 | 0 | 0
| 0.50 mm (26 WG) | Sqmt | 200 | 1140 | 217 | 228000 | 43400 | 271400
| 0.63 mm (24 WG) | Sqmt | 130 | 1290 | 217 | 167700 | 28210 | 195910
| 0.80 mm (22 WG) | Sqmt | 100 | 1390 | 217 | 139000 | 21700 | 160700
| 1.00 mm (20 WG) | Sqmt | RO |  |  | 0 | 0 | 0
6.1 | Flatoval duct volume control damper -Supply, installation and testing of GSS construction of opposed blade volume control dampers with in elliptical /spiral ducts to be provided with suitable links, levers and quadrants for manual control of volume of air flow. Note: Elliptical VCD gague should be one gauge higher than duct. | Sqmt | 4 | 9017 | 1623 | 36068 | 6492 | 42560
[6 empty] | 0 | 0 | 0
6.2 | Rectangular duct volume control damper -Supply, installation and testing of GSS construction of opposed blade volume control dampers with in elliptical /spiral ducts to be provided with suitable links, levers and quadrants for manual control of volume of air flow. Note: Elliptical VCD gague should be one gauge higher than duct. | Sqmt | 3 | 7075 | 1623 | 21225 | 4869 | 26094
|  |  | 0 |  |  | 0 | 0 | 0
6.3 | Round duct, It should be of 24G ,Note -Duct Dropper of length 100/ 150mm for round diffuser connection to be include |  | 0 |  |  | 0 | 0 | 0
| 150 mm dia | Rmt | RO |  |  | 0 | 0 | 0
| 200 mm dia | Rmt | RO |  |  | 0 | 0 | 0
| 250 mm dia | Rmt | RO |  |  | 0 | 0 | 0
| 350 mm dia | Rmt | RO |  |  | 0 | 0 | 0
| 400 mm dia | Rmt | RO |  |  | 0 | 0 | 0
| Round VCD -frame shall be made of 20G and blades shall be made of 20G | Sqm | RO |  |  | 0 | 0 | 0
[6 empty] | 0 | 0 | 0
6.4 | SITC of powder coated Extruded Aluminium round supply diffusers with collar dampers in accordance with the approved shop drawings and specifications. |  | 0 |  |  | 0 | 0 | 0
| 150 mm dia | No | RO |  |  | 0 | 0 | 0
| 200 mm dia | No | RO |  |  | 0 | 0 | 0
| 250 mm dia | No | RO |  |  | 0 | 0 | 0
| 350 mm dia | No | RO |  |  | 0 | 0 | 0
|  |  | 0 |  |  | 0 | 0 | 0
7 | VOLUME CONTROL DAMPERS AND COLLAR DAMPERS |  | 0 |  |  | 0 | 0 | 0
| SITC of VCD -thickness of 18 gauge, utilizes aluminium aerofoil blades, incorporates a gear type VCD rated for 120 GSM, and is constructed with a 1.55 mm thick galvanized steel frame and blades. | Sqmt | 5 | 7075 | 1623 | 35375 | 8115 | 43490
|  |  | 0 |  |  | 0 | 0 | 0
8 | SITC of MVCD -constructed with an 18-gauge GSS frame and 20-gauge blades. It is equipped with TDF flanges on both sides and features an actuator . The actuator operates on 24 V AC or 230 V AC, is a non-spring return ON/OFF type, and has a torque rating of 5/10 /20 NM as per OEM recomendation sized appropriately for the VCD dimensions. | Sqm | 1 | 9147 | 1623 | 9147 | 1623 | 10770
| Actuators with control panel ,6 A 3-Pin Socket with plug mounted on PVC Box which has to be fixed to near the Damper for Actuator termination. Socket should be of modular type,3 runs of 2.5 sq.mm HFLS Cu Wire in 19 mm dia GI Conduit for VFD panel to damper of 20m ,4 way TPN MCB DB with 40 A 4 pole RCCB as incomer and 4 nos 10 A SP MCBs as outgoings in sheet enclosure for Motorised Volume control Dampers to be part of | Nos | 1 | 8625 | 1353 | 8625 | 1353 | 9978
|  |  | 0 |  |  | 0 | 0 | 0
9 | Supply, installation and adjusting of GSS made fresh motorized volume contol damper with actuators . opposed blades , frame shall be made of 18G and blades shall be made of 20G with prefilters for the louvers in all AHU room | Sqm | RO |  |  | 0 | 0 | 0
[6 empty] | 0 | 0 | 0
10 | SITC of Collar Dampers made of Al. extrusions with black powder coating for Grilles / Diffusers -Collar Dampers or neck damper of opposed blade type made out of Aluminium alloy extrusion with anodised matt black finish (AL.blade thickness 1.0mm, Border thickness-1.3 MM) | Sqm | RO |  |  | 0 | 0 | 0
|  |  | 0 |  |  | 0 | 0 | 0
11 | SITC of Backdraft dampers -frame shall be made of 18G and blades shall be made of 20G. Gasket shall be provided on the bottom of the blades edges to avoid noise while on operation | Sqmt | 1 | 6209 | 1353 | 6209 | 1353 | 7562
|  |  | 0 |  |  | 0 | 0 | 0
12 | SITC of powder coated Extruded Aluminium 4-way diffusers Supply in accordance with the approved shop drawings and specifications. The diffuser Neck size shall be as given below. Outer size shall be as per the F/c grid, Diffuser shall be removable core type, shall have concealed fixing screw. Color code shall be as per architect approval. Supply diffuser with colar damper of opposed blade type made out of Aluminium alloy extrusion with anodised matt black finish (AL.blade thickness 1.0mm, Border thickness-1.3 MM) to be include. |  | 0 |  |  | 0 | 0 | 0
12.1 | 600 x 600 Outer Size (525x 525 Neck size in mm) | Nos | RO |  |  | 0 | 0 | 0
12.2 | 600 x 600 Outer Size (450 x 450 Neck size in mm) | Nos | RO |  |  | 0 | 0 | 0
12.3 | 600 x 600 Outer Size (375 x 375 Neck size in mm) | Nos | 16 | 2000 | 450 | 32000 | 7200 | 39200
12.4 | 600 x 600 Outer Size (300x 300 Neck size in mm) | Nos | RO |  |  | 0 | 0 | 0
12.5 | 600 x 600 Outer Size (225 x 225 Neck size in mm) | Nos | RO |  |  | 0 | 0 | 0
12.6 | 600 x 600 Outer Size (150 x 150 Neck size in mm) | Nos | RO |  |  | 0 | 0 | 0
|  |  | 0 |  |  | 0 | 0 | 0
13 | SITC of powder coated Extruded Aluminium 4-way diffusers Return in accordance with the approved shop drawings and specifications. The diffuser Neck size shall be as given below. Outer size shall be as per the F/c grid, Diffuser shall be removable core type, shall have concealed fixing screw,. Color code shall be as per architect approval. |  | 0 |  |  | 0 | 0 | 0
13.1 | 600 x 600 Outer Size (525x 525 Neck size in mm) | Nos | RO |  |  | 0 | 0 | 0
13.2 | 600 x 600 Outer Size (450 x 450 Neck size in mm) | Nos | RO |  |  | 0 | 0 | 0
13.3 | 600 x 600 Outer Size (375 x 375 Neck size in mm) | Nos | 16 | 1400 | 300 | 22400 | 4800 | 27200
13.4 | 600 x 600 Outer Size (300x 300 Neck size in mm) | Nos | RO |  |  | 0 | 0 | 0
13.5 | 600 x 600 Outer Size (225 x 225 Neck size in mm) | Nos | RO |  |  | 0 | 0 | 0
13.6 | 600 x 600 Outer Size (150 x 150 Neck size in mm) | Nos | RO |  |  | 0 | 0 | 0
|  |  | 0 |  |  | 0 | 0 | 0
15 | SITC of Grills -Extruded Al. powder coated Grills for all supply & return air distribution of 100 to 600 mm wide x height and Continous grill with 0 / 15 / 30 / 45 deg (AL.frame thickness 1.2MM, Louver thickness-3 MM). Deflection and final sizes as per approved shop drawings. Grilles complete with integral flanges on both sides & ends as required complete with corner pieces .Supply grill with collarr damper to be consider , Color shade shall be approved by architect. Supply grill with Collar Dampers of opposed blade type made out of Aluminium alloy extrusion with anodised matt black finish (AL.blade thickness 1.0mm, Border thickness-1.3 MM)to be consider , Color shade shall be approved by architect. | Sqmt | 8 | 8678 | 1760 | 69424 | 14080 | 83504
|  |  | 0 |  |  | 0 | 0 | 0
16 | SITC of powder coated Extruded Aluminium Slot diffusers with hit & miss dampers at supply collar ,end flanges and necessary accessories in accordance with the approved shop drawings and specifications. Color code shall be as per architect approval. |  | 0 |  |  | 0 | 0 | 0
16.1 | 1 Slot Diffuser (with 25mm slot openning) | Rmt | RO |  |  | 0 | 0 | 0
16.2 | 2 Slot Diffuser (with 25mm slot openning) | Rmt | 12 | 1280 | 240 | 15360 | 2880 | 18240
16.3 | 3 Slot Diffuser (with 25mm slot openning) | Rmt | RO |  |  | 0 | 0 | 0
|  |  | 0 |  |  | 0 | 0 | 0
17 | SITC of spigot & Butterfly Dampers - manually operated damper with a handle, constructed from GSS (Galvanized Steel Sheet). The casing and blades has a thickness of 20 gauge, round flange , rubber lining and necessary accessories to be provided . |  | 0 |  |  | 0 | 0 | 0
17.1 | 300 mm dia | Nos | RO |  |  | 0 | 0 | 0
17.2 | 250 mm dia | Nos | RO |  |  | 0 | 0 | 0
17.3 | 200 mm dia | Nos | 28 | 1100 | 860 | 30800 | 24080 | 54880
17.4 | 150 mm dia | Nos | RO |  |  | 0 | 0 | 0
|  |  | 0 |  |  | 0 | 0 | 0
18 | SITC insulated Aluminium foil flexible ducts - insulation is made from fibreglass, and its construction consists of fibreglass with an aluminium foil facing. It has a density of 16 kg/m³ and a thickness of 25 mm. Universal clamp , tape ,Circular clip with chain/GI threaded rod and necessary accessories to be provided ,Duct should confirm to fire rating standards BS-476 part 5, 6 & 7 |  | 0 |  |  | 0 | 0 | 0
18.1 | 300 mm dia - Insulated | Rmt | RO |  |  | 0 | 0 | 0
18.2 | 250 mm dia - Insulated | Rmt | RO |  |  | 0 | 0 | 0
18.3 | 200 mm dia - Insulated | Rmt | 45 | 550 | 120 | 24750 | 5400 | 30150
18.4 | 150 mm dia - Insulated | Rmt | RO |  |  | 0 | 0 | 0
|  |  | 0 |  |  | 0 | 0 | 0
19 | SITC of factory fabricated "L" / "Z" shaped cross talk attenuators for full height cabins & rooms with 26 G GSS, CTA with grill shall be acoustically insulated with 15 mm thick of open cell nitrile rubber Class "1" grade of 140-160Kg/Cum density as per the specifications. Material thermal conductivity should be 0.047 W/mK @ 20 deg C & fire performance in accordance with BS476 Part 7 1997 & UL94 1996. manufacturer recommended Adhesive should be used to fix the Acoustic lining in the ducts. The area of the CTA area shall be calculated as like ducitng. Fabrication of CTA shall be as per the approved shop drawing Material shall be FM rated.Quoted price shall be inclusive of GSS channel, metal screws, washers ,26G AL perforated sheet etc | Sqmt | RO |  |  | 0 | 0 | 0
19A | SITC of factory fabricated "L" / "Z" shaped cross talk attenuators for full height cabins & rooms with 26 G GSS, CTA with grill shall be acoustically insulated with 15 mm thick of open cell nitrile rubber Class "1" grade of 140-160Kg/Cum density as per the specifications. Material thermal conductivity should be 0.047 W/mK @ 20 deg C & fire performance in accordance with BS476 Part 7 1997 & UL94 1996. manufacturer recommended Adhesive should be used to fix the Acoustic lining in the ducts. The area of the CTA area shall be calculated as like ducitng. Fabrication of CTA shall be as per the approved shop drawing Material shall be FM rated.Quoted price shall be inclusive of GSS channel, metal screws, washers ,24G AL perforated sheet etc | Sqmt | 15 | 2028 | 276 | 30420 | 4140 | 34560
20 | SITC of Plenum boxes (Mixing champers) made of 24 G G.I , 120 gsm , with necessary adjustable chains for supporting & anchor fasteners, diffuser plenum shall be having spigot, & openning at bottom in accordance with diffuser neck sizes. and the sizes given below,Sizes should be taken based on shop drawing approval ,Supporting chains of Spill air boxes should be quantified. elastomeric nitrile insulation 15 mm open cell insulation as per OEM recommendation to be consider |  | 0 |  |  | 0 | 0 | 0
| 375 x 375 x 300 mm Ht | Nos | RO |  |  | 0 | 0 | 0
| 550 x 550 x 400 mm Ht | Nos | RO |  |  | 0 | 0 | 0
| 600 X 600 X 400 mm Ht | Nos | 12 | 1893 | 362 | 22716 | 4344 | 27060
| 900 x 150 x 400 mm Ht | Nos | RO |  |  | 0 | 0 | 0
[6 empty] | 0 | 0 | 0
21 | Curved grill aesthetically with collar damper -Aluminium extruded Powder Coated Grille 15 deg deflection with the Size of 4"/6"/ 8" with end flanges | Sqm | 9 | 9670 | 3155 | 87030 | 28395 | 115425
|  |  | 0 |  |  | 0 | 0 | 0
22 | Fixed linear bar grill with Zero deflection type of Powder coated extruded aluminum construction. with collar damper -(grilles of 100, 150, 200 mm wide with 0 / 15 / 30 / 45 deg. Deflection as specified In the approved shop drawings)Aluminium extruded Powder Coated Grille | Sqm | RO |  |  | 0 | 0 | 0
|  |  | 0 |  |  | 0 | 0 | 0
23 | Kitchen ducting 16 G thick mild steel with welded construction and with all accessories as per specifications. (with clean outs as per NFPA , maximum at every 6.1 M ), Fire rated duct Painting should be considered -Minimum 2 hours fire rating. |  | 0 |  |  | 0 | 0 | 0
| The Duct shall be supported with Hi-tech Supports at regular intervals to be consider . |  | 0 |  |  | 0 | 0 | 0
| 16 G Mild Stell VCD | Sqm | RO |  |  | 0 | 0 | 0
| 16 G Mild Stell Duct | Sqm | RO |  |  | 0 | 0 | 0
[6 empty] | 0 | 0 | 0
25 | Supply air of Extruded. Aluminium Square / rectangular grill with Collar Damper. Outer 600 x 600 mm 18G AL and type of painting/ powder coating as per the colour approved by Architect /Client /Consultant . |  | 0 |  |  | 0 | 0 | 0
| (All are of 600 x 600 MM Outer to Outer Size) |  | 0 |  |  | 0 | 0 | 0
25.1 | 600x 600 MM (Neck Size) | No | RO |  |  | 0 | 0 | 0
25.2 | 450 x 450 MM (Neck Size) | No | RO |  |  | 0 | 0 | 0
25.3 | 375 x 375 MM (Neck Size) | No | RO |  |  | 0 | 0 | 0
25.4 | 150 x 150 MM (Outer Size) | No | RO |  |  | 0 | 0 | 0
25.5 | 200 x 200 MM (Outer Size) | No | RO |  |  | 0 | 0 | 0
|  |  | 0 |  |  | 0 | 0 | 0
26 | Return air of Extruded. Aluminium Square / rectangular grill without Collar Damper. Outer 600 x 600 mm 18G AL and type of painting/ powder coating as per the colour approved by Architect /Client /Consultant . |  | 0 |  |  | 0 | 0 | 0
| (All are of 600 x 600 MM Outer to Outer Size) |  | 0 |  |  | 0 | 0 | 0
26.1 | 600x 600 MM (Neck Size) | No | RO |  |  | 0 | 0 | 0
26.2 | 450 x 450 MM (Neck Size) | No | RO |  |  | 0 | 0 | 0
26.3 | 375 x 375 MM (Neck Size) | No | RO |  |  | 0 | 0 | 0
26.4 | 150 x 150 MM (Outer Size) | No | RO |  |  | 0 | 0 | 0
26.5 | 200 x 200 MM (Outer Size) | No | RO |  |  | 0 | 0 | 0
|  |  | 0 |  |  | 0 | 0 | 0
27 | THERMODIFFUSER -Thermafusers Supply, Installation, testing and commissioning and balancing of thermally powered STANDALONE TYPE Square VAV diffusers (Thermal - VAV diffuser) suitable for COOLING only. Each diffuser shall be a complete VAV terminal and thermostat self contained in a nominal 600mm x 600mm diffuser. The diffusers shall vary the supply air volume to provide VAV cooling. The diffuser shall be suitable for manual type set point adjustment of temperature for a range from 21°C to 26°C. Each diffuser shall have perimeter blade dampers and powder coated appearance hinged panel that can be unlatched and folded down to hang allowing hands to be free for adjusting temperature set points. Instructions for the module shall be on the inside of the appearance panel. Pressure ranges for the unit shall be from 12 Pa to 62 Pa and noise levels from 15 to 30NC. Product shall be warranted for minimum of 10 yrs. Neck size = 150mm/200mm/250mm/300mm dia. There will be no external power required to operate the perimeter dampers, Shade must be as per the approval from the Architect/Client /Consultant . |  | 0 |  |  | 0 | 0 | 0
27.1 | AIR FLOW = 150 CFM TO 500 CFM | No | RO |  |  | 0 | 0 | 0
|  |  | 0 |  |  | 0 | 0 | 0
28 | SITC of louvers and bird wire mesh -Aluminium Profile 1.2mm thickness powder coated louver with dampers & bird Mesh for avoiding insect ingress for with min. 60 % free area, as per specification with angle frame work & fixing accessories, to be fixed on external wall to ambient .Louvers need to be suitable in order avoid rain water entry in to floor @ 15 degree deflection | Sqm | RO |  |  | 0 | 0 | 0
|  |  | 0 |  |  | 0 | 0 | 0
28.1 | Supply, installation, testing and commissioning Powder Coated Extruded Aluminium Air transfer door grilles with rear side frame as per approved shop drawings. | Sqm | RO |  |  | 0 | 0 | 0
|  |  | 0 |  |  | 0 | 0 | 0
29 | JET Diffusers - Material -18G Al powder coated for supply air distribution - ,diffuser can adjustable 30 deg upwards /downwards .High air handling capacity with low noise level ,fixing by means of metal screws on flanges in sidethrow or fixed directly with plenum boxes |  | 0 |  |  | 0 | 0 | 0
29.1 | 350 mm dia | No's | RO |  |  | 0 | 0 | 0
29.2 | 300 mm dia | No's | RO |  |  | 0 | 0 | 0
29.3 | 250 mm dia | No's | RO |  |  | 0 | 0 | 0
|  |  | 0 |  |  | 0 | 0 | 0
30 | Swirl diffuser -18G powered coated extruded aluminum construction. Material with corrosion resistance with fixed vanes ,slotted rotary face design |  | 0 |  |  | 0 | 0 | 0
30.1 | 600 mm dia | No's | RO |  |  | 0 | 0 | 0
30.2 | 400 mm dia | No's | RO |  |  | 0 | 0 | 0
30.3 | 300 mm dia | No's | RO |  |  | 0 | 0 | 0
30.4 | 250 mm dia | No's | RO |  |  | 0 | 0 | 0
|  |  | 0 |  |  | 0 | 0 | 0
31 | Plaque diffuser -18G powered coated extruded aluminium diffuser |  | 0 |  |  | 0 | 0 | 0
31.1 | 450 x 450 MM (Neck Size) | No's | RO |  |  | 0 | 0 | 0
31.2 | 375 x 375 MM (Neck Size) | No's | RO |  |  | 0 | 0 | 0
31.3 | 300 x 300 MM (Neck Size) | No's | RO |  |  | 0 | 0 | 0
| Note - Diffuser Colour should be as per the client / architect confirmation |  | 0 |  |  | 0 | 0 | 0
|  |  | 0 |  |  | 0 | 0 | 0
32 | SITC of duct mounted static pressure sensor with display and connecting to VFD (being provided by base builder) to vary the speed of the AHU depends on the static pressure in the ducting. The necessary control cabling in the AHU room from static pressure sensor to VFD shall be in the scope. Static pressure sensor shall be connected to VFD directly and shall be compatable to VFD being provided by base builder. Ductstatic pressure sensor shall be installed in the supply duct at 2/3 distance from AHU. | Nos. | 1 | 9652 | 857 | 9652 | 857 | 10509
[6 empty] | 0 | 0 | 0
33 | Insulation |  | 0 |  |  | 0 | 0 | 0
33.1 | SITC of Thermal Insulation of ducts .- The material is closed cell Class 'O' elastomeric nitrile rubber insulation. fire performance rating of Class 'O' as per BS 476 Parts 6 & 7. The insulation thickness is 13 mm , operational temperature rating ranges from -40°C to +105°C. The material has a thermal conductivity of ≤ 0.036 W/mK at 20°C, a density between 40 to 60 kg/m³, and a water vapour diffusion resistance factor (µ) of ≥ 7000. All joints supports ,strips ,screws ,Insulation material shall be bonded with the ducts using metal screw and washers shall be included Material shall be FM GLOBAL approved, food grade material with antimicrobial properties, aluminium foil which to be laid over the thermal insulation,The adhesive used in self-adhesive backing should be Fire Retardant, LEED compliant and zero VOC. | Sqmt | 380 | 280 | 110 | 106400 | 41800 | 148200
|  |  | 0 |  |  | 0 | 0 | 0
33.2 | SITC of Duct Acoustic Insulation - The material is open cell nitrile rubber insulation, which operates within a temperature range of -40°C to +105°C and has a thermal conductivity of 0.047 W/mK at 20°C. It is supplied in a 15 mm thickness for duct applications, has a density between 150 and 200 kg/m³, and achieves a fire safety rating of Class 1 as per BS476 Part 7 .Inside main air ducts for 1st 6m shall be Acoustic insulation . All joints supports ,strips ,screws ,Insulation material shall be bonded with the ducts using metal screw and washers shall be included Material shall be FM GLOBAL approved, food grade material with antimicrobial properties, aluminium foil which to be laid over the thermal insulation,The adhesive used in self-adhesive backing should be Fire Retardant, LEED compliant and zero VOC. | Sqmt | 40 | 1000 | 140 | 40000 | 5600 | 45600
|  |  | 0 |  |  | 0 | 0 | 0
34 | Supply, Installation, Testing & Commissioning of Disc Valve with damper |  | 0 |  |  | 0 | 0 | 0
| 150mm dia | Nos | 0 |  |  | 0 | 0 | 0
| 200mm dia | Nos | 14 | 632 | 150 | 8848 | 2100 | 10948
| Uninsulated AL flexible duct 150mm /200 mm dia as per Shop drawing approval ,Universal clamp , tape ,Circular clip with chain/GI threaded rod and necessary accessories to be provided | Rmt | 28 | 217 | 88 | 6076 | 2464 | 8540
|  |  | 0 |  |  | 0 | 0 | 0
35 | Floor Flushout : As per LEED requirement each Floor Flushing to be done with temporary exhaust fan ,After construction ends on site, prior to occupancy and with all interior finishes installed, a building flush out should be performed taking air at ambient temp as per the LEED requirement. The purpose of this flushing out is to get rid of particulate matter and VOCs produced by particle-emitting construction materials, furnishings, interior finishes and cleaning agents,Cost of arranging Temporary exhaust fan & related electrical cable requirement is part of the cost. | Lot | 1 | 0 | 70000 | 0 | 70000 | 70000
36 | Associated Civil Works -Chipping, chassing & Plastering the wall openings in cement mortor 1:6 of 15 mm thick finishing to line and level with sand faced finshing at all levels, including all leads & lifts, scaffolding, curing etc complete work will included from AHU to Grill all HVAC work (for Supply & Return air duct openings in ahu rooms ,chequered plate of 8mm thick ness for shaft closure with all necessary supports etc) | Sqm | 4 | 1623 | 722 | 6492 | 2888 | 9380
|  |  | 0 |  |  | 0 | 0 | 0
| VENTIALTION UNITS |  | 0 |  |  | 0 | 0 | 0
37 | SITC Cabinet Exhasut fan - The unit is a double-skin construction, ceiling-mounted type, featuring an EC fan with a direct drive arrangement. The panel has a thickness of 25 mm (+/- 2 mm) with PUF insulation with density 38kg/cum / 32 mm Nitrile rubber of density140- 180 kg / m³, The outer skin is made of 0.8 mm thick Pre-Coated GI, and the inner skin is made of 0.6 mm thick Plain GI. The noise level at a one-meter distance is less than 75 dB(A). Overall dimensions for a unit up to 6000 CFM should be less than 700 mm (Length), 700 mm (Width), and 700 mm (Height). A static pressure of 30 mm Wg is to be considered as a baseline; however, the vendor must calculate the required static pressure based on the shop drawing location before ordering the unit, and the calculation shall be submitted for approval. An electrical panel will be provided, including an MCB, an auto/manual dongle switch, a potentiometer, and internal wiring. A control panel suitable for the EC fan will also be provided, capable of controlling AC and DC power,Limit switch wiring ,lighting & motor interlock to be provided with 3 core 2.5sqmm cable in 19mm dia GI conduit /OEM recommendation The unit shall have an IP54 rating. It shall be supplied complete with necessary spring vibration isolators, limit switches, an inspection door, a fire-retardant canvas-type flexible connection, a duct cowl piece, supports, and all other necessary accessories,control system must be capable of integration with a BMS (Building Management System) via Bacnet or Modbus communication protocols. |  | 0 |  |  | 0 | 0 | 0
[6 empty] | 0 | 0 | 0
37.1 | 200 Cfm | Nos | RO |  |  | 0 | 0 | 0
37.2 | 500 Cfm | Nos | RO |  |  | 0 | 0 | 0
37.4 | 300 Cfm | Nos | RO |  |  | 0 | 0 | 0
37.8 | 500 Cfm ith hydrogen sensor for battery room Note: Inlinefan with H2 sensor , timer & hooter with 40 mm static pressure, requried panel & electrical works to be included in the same line item. Should generate an alarm if the H2 LEVEL in the room temperature goes beyond the set point .H2 Sensor panel should be provided with BMS compatibility. | Nos | 1 | 95181 | 4506 | 95181 | 4506 | 99687
37.9 | 1500 Cfm with hydrogen sensor for battery room Note: Inlinefan with H2 sensor , timer & hooter with 40 mm static pressure, requried panel & electrical works to be included in the same line item. Should generate an alarm if the H2 LEVEL in the room temperature goes beyond the set point .H2 Sensor panel should be provided with BMS compatibility. | Nos | RO |  |  | 0 | 0 | 0
37.1 | 5000 Cfm with hydrogen sensor for battery room Note: Inlinefan with H2 sensor , timer & hooter with 40 mm static pressure, requried panel & electrical works to be included in the same line item. Should generate an alarm if the H2 LEVEL in the room temperature goes beyond the set point .H2 Sensor panel should be provided with BMS compatibility. | Nos | RO |  |  | 0 | 0 | 0
VENTILATION FANS
37.11 | 600 Cfm | Nos | 1 | 9462 | 1353 | 9462 | 1353 | 10815
37.12 | 800 Cfm | Nos | RO |  |  | 0 | 0 | 0
37.13 | 1000 Cfm | Nos | 1 | 14644 | 1353 | 14644 | 1353 | 15997
37.13 | 1250 Cfm | Nos | RO |  |  | 0 | 0 | 0
37.14 | 1500 Cfm | Nos | RO |  |  | 0 | 0 | 0
37.15 | 1800 Cfm | Nos | RO |  |  | 0 | 0 | 0
37.15 | 2000 Cfm | Nos | RO |  |  | 0 | 0 | 0
37.16 | 3000 Cfm | Nos | RO |  |  | 0 | 0 | 0
37.17 | 5000 Cfm | Nos | RO |  |  | 0 | 0 | 0
37.18 | 2000 cfm SISW kItchen Exhaust fan 80mm ESP | Nos | RO |  |  | 0 | 0 | 0
| Supply, installation, testing and commissioning of (SISW) Double Skin units, complete with double skin (45±2 mm) insulated Rockwool insulation material of density 60 kg/cum. The sheet thickness shall be minimum 0.8 mm for the outer skin and 0.8 mm thickness for the inner skin of GI . Single inlet single width backward fan fireproof fans with VFD . Each fan shall be complete with totally enclosed fan cooled IE5 motor , direct drive, motor shall be placed outside from the airflow path ,pulley mounted on motor & fan shaft ,Unit should include vibration isolator. The motor shall be suitable for 415 V + 10% volts 3 phase 50 cycles, AC supply & suitable for operating through VFD. The motor selected shall be energy efficient having efficiency at full load ranging between 82.5% to 92% in accordance with motor rating as per specification ,Kitchen exhaust Connectors ,fan and Junction boxes must be fireproof |  |  |  |  | 0 | 0 | 0
37.14 | 2000 cfm Dry Scrubber for kitchen exhaust fan | Nos | RO |  |  | 0 | 0 | 0
| Dry Scrubber - Supply, Installation, Testing and Commissioning of Scrubber each comprising of extract air intake section, electrostatic precipitation technology, dry type air cleaner to remove oil, smoke and fumes from exhaust air ,Electrostatic section shall be made of 16 gauge galvanized sheet, high bake epoxy powder coated, washable type aluminium mesh filters, stainless steel spiked ionizers to create high voltage DC field, aluminium collector plates which should be alternatively charged positive and negative with large collecting area with 14" deep cell, to work as magnet for charged smoke and oil particles. Average efficiency of 90-95% in single pass as per ASHRAE test method. |  |  |  |  | 0 | 0 | 0
[6 empty] | 0 | 0 | 0
38 | SITC Cabinet Fresh air fan - The unit is a double-skin construction, ceiling-mounted type, featuring an EC fan with a direct drive arrangement. The panel has a thickness of 25 mm (+/- 2 mm) with PUF insulation with density 38kg/cum / 32 mm Nitrile rubber of density140- 180 kg / m³, The outer skin is made of 0.8 mm thick Pre-Coated GI, and the inner skin is made of 0.6 mm thick Plain GI. The noise level at a one-meter distance is less than 75 dB(A). Overall dimensions for a unit up to 6000 CFM should be less than 1500 mm (Length), 1500 mm (Width), and 700 mm (Height). A static pressure of 30 mm Wg is to be considered as a baseline; however, the vendor must calculate the required static pressure based on the shop drawing location before ordering the unit, and the calculation shall be submitted for approval. An electrical panel will be provided, including an MCB, an auto/manual dongle switch, a potentiometer, and internal wiring. A control panel suitable for the EC fan will also be provided, capable of controlling AC and DC power,Limit switch wiring ,lighting & motor interlock to be provided with 3 core 2.5sqmm cable in 19mm dia GI conduit /OEM recommendation The unit shall have an IP54 rating. It shall be supplied complete with necessary spring vibration isolators, limit switches, an inspection door, a fire-retardant canvas-type flexible connection, a duct cowl piece, supports, and all other necessary accessories,control system must be capable of integration with a BMS (Building Management System) via Bacnet or Modbus communication protocols. The pre-filter material to be Synthetic Non-Woven, rated EU-4 (MERV 8 ) with 90% efficiency down to 10 microns to be considered for all fresh air fans |  | 0 |  |  | 0 | 0 | 0
38.1 | 300 Cfm | Nos | RO |  |  | 0 | 0 | 0
38.2 | 400 Cfm | Nos | RO |  |  | 0 | 0 | 0
38.3 | 600 Cfm | Nos | RO |  |  | 0 | 0 | 0
38.4 | 700 Cfm | Nos | RO |  |  | 0 | 0 | 0
38.5 | 800 Cfm | Nos | RO |  |  | 0 | 0 | 0
38.6 | 1000 Cfm | Nos | RO |  |  | 0 | 0 | 0
38.7 | 1500 Cfm | Nos | RO |  |  | 0 | 0 | 0
38.8 | 2000 Cfm | Nos | RO |  |  | 0 | 0 | 0
38.9 | 3000 Cfm | Nos | RO |  |  | 0 | 0 | 0
38.1 | 4000 Cfm | Nos | RO |  |  | 0 | 0 | 0
|  |  | 0 |  |  | 0 | 0 | 0
| TOTAL - VENTIALTION UNITS |  | 0 |  |  | 0 | 0 | 0
[6 empty] | 0 | 0 | 0
39 | Electronic air cleaners(EAC) for existing and new AHU’s (Per floor 2 no's) | Lot | RO |  |  | 0 | 0 | 0
[6 empty] | 0 | 0 | 0
40 | UNDERDECK INSULATION |  | 0 |  |  | 0 | 0 | 0
| .Under deck insulation 32mm thick Nitrile rubber insulation with density not less than 40 to 60 kg / m3 suitably factory laminated with AL Foil /GC cloth ( (Client approval should be obtained ) & necessary accessories /supports to be include . | Sqm | RO |  |  | 0 | 0 | 0
[6 empty] | 0 | 0 | 0
41 | UV lamp in AHU plenum (10000 cfm to 25000 cfm) | Lot | RO |  |  | 0 | 0 | 0
| Supply of Advanced Oxidation PentagonPlasma (AOP) cells comprising of UVC lamp 254 NM on NANO metallic compound target Alumninum matrix cell duly enclosed by a poly casing tube, with the capability to produce plasma Hydroxyl oxidizers. The unit shall have inbuilt multipin Bi polar ion generator pins along with ultrasonic radio frequency waves for pest repellancy. The UV-C lamp will be a low-pressure mercury type and of such intensity as to provide minimum performance as listed below. The UV-C lamp will produce only Germicidal UV (by definition this means 99.99% UV-C energy). The life of the lamp shall be atleast 18000 hours. The cell will have built in LED indication system stating the operation of the 3 technologies the UV lamp, ionizer and pest repellant.The wattage of the lamp shall not be less than 21 watts upto 6500 CFM ,36 watts upto 20000 CFM and a minimum of 48 watts upto 28000 CFM or combination based on the application area. The system shall be capable of reducing microbial bacteria, virus and spores , VoC’, odors and particulates matter. The equipment shall have to GREENPRO,TUV,CE, ISO 13485, ROHS with 2014/35/EU Low Voltage Directive along with FDA compliance certifications. The AOP cell shall a microbiological testing report against Bacteriophage (MS-2 FDA) surrogate SARS Cov-2 with a minimum efficiency of 99 percent along with a Virology report from CCMB lab with an minimum efficiency of 99 percent against SARS COV2 within 45 minutes. The power / control cabling between the AOP cell and the power source / controls shall be included in the cost .The system shall be capable of reducing microbial bacteria, virus and spores, VoC’s, odors and particulate matter. The Pentagon cells should be selected by considering a load factor calculation for each specific area where the equipment is to be installed..The AOP cell should be mounted within the AHU or at supply air duct/plenum. |  | 0 |  |  | 0 | 0 | 0
[6 empty] | 0 | 0 | 0
42 | Firesealent for passive fire protection material on walls /duct gaps ( supply / return air ducts/Exhaust ) Fire Barrier Sealant shall be a one component, ready-to-use, gun-grade, latex-based, intumescent firestop sealant. tensile strength 85psi,The material shall be thixotropic and shall be applicable to firestops | Sqm | RO |  |  | 0 | 0 | 0
[6 empty] | 0 | 0 | 0
43 | BTU meters -Ultrasonic type and including necessary accessories/connection |  |  |  |  | 0 | 0 | 0
| 150mm | Nos. | RO |  |  | 0 | 0 | 0
| 125mm | Nos. | RO |  |  | 0 | 0 | 0
| 100mm | Nos. | RO |  |  | 0 | 0 | 0
| 80mm | Nos. | RO |  |  | 0 | 0 | 0
| 65mm | Nos. | RO |  |  | 0 | 0 | 0
| 50mm |  |  |  |  | 0 | 0 | 0
[6 empty] | 0 | 0 | 0
44 | MERV 8 Filters for AHU's with frame and necessary supports,Efficiency grade 90% down to 10 microns Preferably Box type design . All Filters shall be covered with polyethylene cover and packed in good quality cartons box for safe handling and storage.The cost shall include the cost of removal of existing MERV Filters and replacement with new MERV Filters . Contractor to check the space avaialble in existing AHU and select the Filter depths accordingly | Sets | RO |  |  | 0 | 0 | 0
[6 empty] | 0 | 0 | 0
45 | MERV 13 Filters for AHU's with frame and necessary supports,Efficiency grade 95% down to 5 microns Preferably Box type design . All Filters shall be covered with polyethylene cover and packed in good quality cartons box for safe handling and storage.The cost shall include the cost of removal of existing MERV Filters and replacement with new MERV Filters . Contractor to check the space avaialble in existing AHU and select the Filter depths accordingly | Sets | RO |  |  | 0 | 0 | 0
[6 empty] | 0 | 0 | 0
46 | FIRE RATED COATING COMPUND FOR DUCT |  |  |  |  | 0 | 0 | 0
| Supply, fabrication, Installation and testing of Fire rated coating compound STARCOAT CRC /Foster/3M to be provided over duct. Fire rated coating compound used for construction of fire rated ductwork shall be protected with minimum 0.7mm to 1mm nominal thickness tested to properties as per the requirements of BS 476: 6 & 7, including non-combustibility Class O and fire propagation - Class 1 surface spread of flame & materials in accordance with building regulations for the determination of BS 476 Part 24 (Test Certificate required from CBRI or BS Certified Lab).Insulation shall be applied after this coating as per specifications. | sqm | RO |  |  | 0 | 0 | 0
|  |  | 0 |  |  | 0 | 0 | 0
| TOTAL - Air distribution |  |  |  |  | 0 | 0 | 0
[6 empty] | 0 | 0 | 0
PART -B | VAV WORKS |  |  |  |  | 0 | 0 | 0
|  |  | 0 |  |  | 0 | 0 | 0
1 | Variable Air Volume (VAV) Units -( Reactangular Type ) |  | 0 |  |  | 0 | 0 | 0
| Supply, Assembly, Installation, Testing, Balancing & Commissioning of VAV boxes in supply air duct, VAV shall be fabricated out of 22 G GI sheet and shall be insulated with 10 mm thk open cell nitrile rubber,The VAV unit shall be pressure independent, complete ,controller for receiving Temp. & DP Signal, actuator, associated acessories etc. |  | 0 |  |  | 0 | 0 | 0
1.1 | Up to 650 CFM | Nos. | 8 | 20276 | 2253 | 162208 | 18024 | 180232
1.2 | From 651 to 1350 CFM | Nos. | 2 | 20726 | 2253 | 41452 | 4506 | 45958
1.3 | From 1351 to 2100 CFM | Nos. | 1 | 21176 | 2253 | 21176 | 2253 | 23429
1.4 | From 2101 to 3200 CFM | Nos. | RO |  |  | 0 | 0 | 0
1.5 | Above 3200 CFM | Nos. | RO |  |  | 0 | 0 | 0
|  |  | 0 |  |  | 0 | 0 | 0
2 | Variable Air Volume (VAV) Units -( Oval Duct ) |  | 0 |  |  | 0 | 0 | 0
| Supply, Assembly, Installation, Testing, Balancing & Commissioning of VAV boxes in supply air duct, VAV shall be fabricated out of 22 G GI sheet and shall be insulated with 10 mm thk open cell nitrile rubber, Eliptical duct -VAV to be inside the duct with controllers , VAV to duct connection , Conical pieces, tapper piecs part of scope ,The VAV unit shall be pressure independent, complete ,controller for receiving Temp. & DP Signal, actuator, associated acessories etc. |  | 0 |  |  | 0 | 0 | 0
2.1 | Up to 650 CFM | Nos. | 2 | 20558 | 2253 | 41116 | 4506 | 45622
2.2 | From 651 to 1350 CFM | Nos. | 2 | 21797 | 2253 | 43594 | 4506 | 48100
2.3 | From 1351 to 2100 CFM | Nos. | 1 | 23542 | 2253 | 23542 | 2253 | 25795
2.4 | From 2101 to 3200 CFM | Nos. | 2 | 25289 | 2253 | 50578 | 4506 | 55084
2.5 | Above 3200 CFM | Nos. |  |  |  | 0 | 0 | 0
|  |  | 0 |  |  | 0 | 0 | 0
3 | Thermostats |  | 0 |  |  | 0 | 0 | 0
3.1 | Analogue thermostat | Nos. | 8 | 1142 | 451 | 9136 | 3608 | 12744
3.2 | Digital thermostat | Nos. | 10 | 1142 | 451 | 11420 | 4510 | 15930
|  |  | 0 |  |  | 0 | 0 | 0
4 | Supply, Installation, Testing and Commissioning of VAV integrators for integrating the VAVs with third party BMS. Integrators shall be located in the AHU Rooms. Each integrator shall be capable of integrating minimum 50 no. VAVs. Integrators shall be placed in the AHU room. | Nos | 1 | 36044 | 1353 | 36044 | 1353 | 37397
| Note :- VAV sizing & qty - VAV size shall vary with respect to final approved scheme. Contractor to order VAVs based on approved drawing. |  | 0 |  |  | 0 | 0 | 0
|  |  | 0 |  |  | 0 | 0 | 0
5 | Cables & Conduits |  | 0 |  |  | 0 | 0 | 0
5.1 | 2core, 1.5 Sqmm, screened ATC/shielded twisted pair cable for communication looping between VAV’s (VAV to VAV) & BMS. | Rmt | 270 | 103 | 24 | 27810 | 6480 | 34290
5.2 | 4core, 1.5 Sqmm, screened ATC/shielded /Flexible twisted pair cable for communication looping between VAV’s (VAV to Thermostats) & BMS. | Rmt | 150 | 135 | 32 | 20250 | 4800 | 25050
5.3 | 3core, 1 Sqmm, screened ATC/shielded twisted pair cable for communication looping between VAV’s & BMS. (for analogue thermostats) | Rmt | 80 | 105 | 24 | 8400 | 1920 | 10320
5.4 | 6core, 1 Sqmm, screened ATC/shielded twisted pair cable for communication looping between VAV’s & BMS. (fro digitial thermostats) | Rmt | 100 | 150 | 38 | 15000 | 3800 | 18800
5.5 | GI - FRLS Conduit of 19 mm dia | Rmt | 450 | 89 | 20 | 40050 | 9000 | 49050
5.6 | Supply, Installation of Power Cable -3Core * 1.5Sqmm (VAV) | Rmt | 100 | 118 | 20 | 11800 | 2000 | 13800
7 | Cable tray :Supply and Erection of preforated Heavy duty GI perforrated 2mm thick hot dipped galvanized by 610gms/sqm (87 microns) in line with IS: 4759. The tray and accessories includes cleat angle, rungs, side runner, coupler plate, Elbows, Bends, Tees and Reducers and Hardware .The fixing of cable trays include necessary ceiling suspended / wall mounted supports fixed in ceiling with Fabricated Ms Angle supports,Ms C channel,Base plate etc, The rate shall include bends, angles, Ts, HITECH ROD and all accessories complete Supports Shall be provided at every 1200mm. The cost of supports to be included. Supports must be welded to a square true ceiling base plate with arc welding, the base plate must be fixed to the true ceiling with 04 nos. of HILTI anchor fasteners. The cost of 2runs of 25x3mm GI Strip to be included in the cost of the cable tray. Supports must be made out of MS L angle type for cable tray width of 450mm and above. For Less than 450mm width tray support with hi-tech threaded rods & anchor fasteners. |  |  |  |  | 0 | 0 | 0
| 100 mm X 50 mm | Rmt | 50 | 659 | 96 | 32950 | 4800 | 37750
| 200 mm X 75 mm | Rmt | 35 | 767 | 110 | 26845 | 3850 | 30695
| 400 mm X 100 mm | Rmt | RO |  |  | 0 | 0 | 0
| 600 mm X 100 mm | Rmt | RO |  |  | 0 | 0 | 0
[6 empty] | 0 | 0 | 0
| TOTAL - VAV |  | 0 |  |  | 0 | 0 | 0
|  |  | 0 |  |  | 0 | 0 | 0
PART -C | DX SYSTEM WORKS |  | 0 |  |  | 0 | 0 | 0
|  |  | 0 |  |  | 0 | 0 | 0
1 | DX HI WALL SPLIT UNITS |  | 0 |  |  | 0 | 0 | 0
| Hi wall DX split air conditioners (Includes indoor & outdoor unit ) with Inverter rotory compressors consisting of compressors motor units, copper condenser ,evaporator fan and ect , necessary stand for mounting bracket ODU and IDU along with remote with Display, .Star rating -BEE tabel 2.6 Condensate drain pump to be consider along with unit (Max. flow 12L/h)230V/50Hz/Single Phase,Ambient Temp Cooling 50 degree C ,R32/R410a,NB 40 Noise level in indoor,Including refrigerant charge .PVC insulated armoured copper cable between indoor unit and outdoor unit with supports, clamping, end terminations, Control copper wiring ODU to IDU 4C x 1.0 /Manufacture recommend,Power cable copper to ODU 3C x 1.0 ,ODU Breaker Amps 16 . |  | 0 |  |  | 0 | 0 | 0
| Soft drawn Copper piping ( Suction gas line & liquid line ) 15 m supplied along with unit , shall be insulated with 13 mm thick Sleeveless nitrile rubber insulation. Both the pipelines shall be insulated with nitrile tubular insulation of Class "O". Insulation. Exposed piping insulation shall be painted with two coats of UV resistance paint.Necessary electrical/control cable between indoor and outdoor unit shall be included in the scope. (if lenght is increased as per OEM recommended , unit need to size higher capacity & need to deliver as specificed TR in Boq) |  | 0 |  |  | 0 | 0 | 0
1.1 | 1.5 TR -Hi Wall | Nos | RO |  |  | 0 | 0 | 0
1.2 | 2.0 TR -Hi Wall | Nos | RO |  |  | 0 | 0 | 0
1.3 | 2.8 TR -Hi Wall | Nos | RO |  |  | 0 | 0 | 0
|  |  | 0 |  |  | 0 | 0 | 0
2 | SITC of Auto Sequential control panel for automatic change over between working unit and stand by unit in case of failure running unit based on the temperature, in Critical/Boardrooms/Server room units. Air conditioning units shall be able to restart automatically after power failure/interruption. Scheduling shall be possible between working AHU and stand by DX/VRF Hiwall split units. The panel shall be provided with potential free contact for fire protection. | Nos | 3 | 20276 | 2253 | 60828 | 6759 | 67587
|  |  | 0 |  |  | 0 | 0 | 0
| TOTAL - DX System |  | 0 |  |  | 0 | 0 | 0
|  |  | 0 |  |  | 0 | 0 | 0
PART -D | VRF SYSTEM WORKS - Equipment with 3 years Warranty and one years AMC |  | 0 |  |  | 0 | 0 | 0
|  |  | 0 |  |  | 0 | 0 | 0
1 | VRF /VRV OUTDOOR UNIT (Variable Refrigerant Flow System ) for Command Centre UPS Room and Hub Room |  | 0 |  |  | 0 | 0 | 0
| Supply,installation,testing and commissioning of inverter based variable refrigerant flow (VRF /VRV) air conditioning system suitable for cooling with highly efficient hermetically sealed scroll inverter type compressor in each module of outdoor unit which runs at various compressor speeds to regulate capacities to suit actual load requirements and with high efficiency heat transfer cooling coil suitable for eco friendly R410A refrigerant.The VRF is specially designed to deliver 100% capacity at a higher ambient temperature of 43 deg C,Non-stop cooling even at 50 deg C and is designed to operate efficiently even with very long piping lengths of upto 1 km.The unique design of inverter compressor ensures that the refrigerants injects directly into the compressor chamber.Since the suction gas enters directly into the scroll,there is no superheat gain due to the compressor motor assembly.VRF units are fitted with 100% inverter compressors.,Air cooled propeller type condenser fan with DC motor drive,interconnecting piping, suction line insulation etc., Micro-processor control panel suitable for automatic operation,High speed calculation inverter control, active oil control mechanism incorporating all safety functions as per equipment specifications & other points as listed below ,Unit shall have a multiple compressors. And each compressor shall run independently even though there is a failure in the other compressor. Costing shall include air balancing , commisisioning & handing over as per project inchagre requirement.VRV system to be BMS compatible it should give Modbus/ Bacnet over LON works |  | 0 |  |  | 0 | 0 | 0
| Outdoor unit shall be designed to work on variable refrigerant circulation depending on the actual load sensing. The unit shall have atleast one compressor whose capacity is variable in each outdoor module, in multi modular combination, together with additional constant capacity compressors to deliver rated capacity. The variable capacity compressor shall be of digital/ inverter control as per manufacturer's design. The condenser fins shall be coated with anti corrosive material for longer life. The unit shall have oil arrestor to prevent oil migration. Suction accumulator and liquid receiver shall be provided to balance variable refrigerant circulation. The system shall operate with only two pipes i.e., suction and liquid line that can be connected to multiple indoor units.Refigerant should be R410-a , ODU should function in case of any single IDU failure in the circuit . |  | 0 |  |  | 0 | 0 | 0
| The unit mouted starter panel shall be complete with IP-55 protection consisting of power disconnecting switches with fuses, soft starters, for compressor motors, under/over voltage trip, single phase preventers, communication card which can accept 4-20 mA or 2-10 Vdc analog signal. MS Channel frame for outdoor units complete with epoxy black painted,vibration isolation pads,cowl piece and necessary MS supports to be included in the costing. Scope also included preesure testing with nitrogen gas & Vaccumising including all consumables. Scope includes pressure testing and Refrigerant gas charging |  | 0 |  |  | 0 | 0 | 0
| 6HP VRF / VRV ODU | Nos | RO |  |  | 0 | 0 | 0
| 8HP VRF / VRV ODU | Nos | RO |  |  | 0 | 0 | 0
| 10 HP VRF / VRV ODU | Nos | 2 | 196857 | 9012 | 393714 | 18024 | 411738
| 12 HP VRF / VRV ODU | Nos | RO |  |  | 0 | 0 | 0
| 14HP VRF / VRV ODU | Nos | RO |  |  | 0 | 0 | 0
| 16HP VRF / VRV ODU | Nos | RO |  |  | 0 | 0 | 0
| 18 HP VRF / VRV ODU | Nos | RO |  |  | 0 | 0 | 0
| 20 HP VRF / VRV ODU | Nos | RO |  |  | 0 | 0 | 0
| 22 HP VRF / VRV ODU | Nos | RO |  |  | 0 | 0 | 0
| 24 HP VRF / VRV ODU | Nos | RO |  |  | 0 | 0 | 0
| 26 HP VRF / VRV ODU | Nos | RO |  |  | 0 | 0 | 0
| 28HP VRF / VRV ODU | Nos | RO |  |  | 0 | 0 | 0
| 30 HP VRF / VRV ODU | Nos | RO |  |  | 0 | 0 | 0
| 32 HP VRF / VRV ODU | Nos | RO |  |  | 0 | 0 | 0
| 38 HP VRF / VRV ODU | Nos | RO |  |  | 0 | 0 | 0
| 42 HP VRF / VRV ODU | Nos | RO |  |  | 0 | 0 | 0
| 40 HP VRF / VRV ODU | Nos | RO |  |  | 0 | 0 | 0
| 46 HP VRF / VRV ODU | Nos | RO |  |  | 0 | 0 | 0
| 52 HP VRF / VRV ODU | Nos | RO |  |  | 0 | 0 | 0
| 56 HP VRF / VRV ODU | Nos | RO |  |  | 0 | 0 | 0
| 58 HP VRF / VRV ODU | Nos | RO |  |  | 0 | 0 | 0
| 62 HP VRF / VRV ODU | Nos | RO |  |  | 0 | 0 | 0
[6 empty] | 0 | 0 | 0
2 | VRF LOW SIDE WORKS -with necessary supports and fittings. |  |  |  |  | 0 | 0 | 0
| VRF INDOOR UNITS |  |  |  |  | 0 | 0 | 0
| Ductable Unit -SITC of Ceiling Suspended Ductable unit indoor unit designed with fan, low noise, electronic expansion valve,compact cooling coil, washable filter and corded remote controller, unit shall including shifting, prefilters, supports, fire retardant double canvas connection with zip and outlet damper made with GI construction, units shall be with R 410A Refrigerant. Units shall have built in drain pumps for OEM or external drain pump with two litres storage capacity shall be provided.Switches should be made of rubber and the casing should be oil resistant for durability of the unit . |  |  |  |  | 0 | 0 | 0
| Cassette Unit- SITC of 4 way Cassette Type VRV Indoor Unit with including all accessories, supports, return air grille panel, etc. IDUs shall have built in drain pump from OEM with multi speed fan, cooling coil, remote sensor , cordless remote controller |  |  |  |  | 0 | 0 | 0
| Hi wall Unit- SITC of Hi wall Type VRV Indoor Unit with multi speed fan,cooling coil, remote sensor , drain pump and cordless remote controller to be considered |  |  |  |  | 0 | 0 | 0
| Indoor units necessary supports to be included in the costing |  |  |  |  | 0 | 0 | 0
| Note : The indoor units to be compatible for BMS integration with read /write function for necessary controls through bms. |  |  |  |  | 0 | 0 | 0
2.1 | Hi wall unit type 1 -1.0TR | Nos |  |  |  | 0 | 0 | 0
2.2 | Hi wall unit type 2 -1.5TR | Nos | 2 | 18708 | 1353 | 37416 | 2706 | 40122
2.3 | Hi wall unit type 3 -2 TR | Nos | 2 | 21195 | 1353 | 42390 | 2706 | 45096
2.4 | Hi wall unit type 4 -2.5 TR | Nos | 2 | 27792 | 1353 | 55584 | 2706 | 58290
2.5 | Hi wall unit type 4 -2.8 TR | Nos | RO |  |  | 0 | 0 | 0
3.1 | Cassette Unit- type 1 -0.8TR | Nos | RO |  |  | 0 | 0 | 0
3.2 | Cassette Unit- type 2-1.0TR | Nos | RO |  |  | 0 | 0 | 0
3.3 | Cassette Unit- type 3-1.2TR | Nos | RO |  |  | 0 | 0 | 0
4.1 | Cassette Unit- type 4-1.5TR | Nos | RO |  |  | 0 | 0 | 0
4.2 | Cassette Unit- type 5-2 TR | Nos | RO |  |  | 0 | 0 | 0
4.3 | Cassette Unit- type 6-2.5 TR | Nos | RO |  |  | 0 | 0 | 0
5.1 | Cassette Unit- type 7-3TR | Nos | RO |  |  | 0 | 0 | 0
5.2 | Cassette Unit- type 8-4.0TR | Nos | RO |  |  | 0 | 0 | 0
5.3 | Ductable Unit -type 1 -1.5TR | Nos | RO |  |  | 0 | 0 | 0
6.1 | Ductable Unit -type 1 -2.0TR | Nos | RO |  |  | 0 | 0 | 0
6.2 | Ductable Unit -type 1 2.8 TR | Nos | RO |  |  | 0 | 0 | 0
6.3 | Ductable Unit -type 2 -4.0TR | Nos | RO |  |  | 0 | 0 | 0
7.1 | Ductable Unit -type 3 -6TR | Nos | RO |  |  | 0 | 0 | 0
7.2 | Ductable Unit -type 3 -8TR | Nos | RO |  |  | 0 | 0 | 0
7.3 | Ductable Unit -type 3 -11TR | Nos | RO |  |  | 0 | 0 | 0
8.1 | Ductable Unit -type 3 -18TR | Nos | RO |  |  | 0 | 0 | 0
8.2 | Ductable Unit -type 3 -20TR | Nos | RO |  |  | 0 | 0 | 0
|  |  | 0 |  |  | 0 | 0 | 0
3 | REFRIGERANT PIPE -with necessary supports and fittings. |  | 0 |  |  | 0 | 0 | 0
| Supply and Installation of Nitrogen Pressure testing of Refrigerant copper piping with necessay fittings imported fittings, Y-joints and headers etc.,interconnecting the liquid and suction lines between the VRF outdoor units and the indoor units. The piping shall be carried out of Hard drawn copper pipes (18G)& Soft drawn copper pipes (20G) including necessary elbows,collars and 18G Copper Refnut joints refnut joints as per the layout to connect branch pipes to indoors,Header pipes and to connect multiple outdoor units as a single system.Both the suction and liquid lines shall be insulated with 19mm / 13mm thick closed cell nitrile rubber insulation to be considered.The Sizes of Refrigerant pipes as per manufacture /shop drawing specifications.This includes the pressure testing and refrigerant charge (Refrigerant gas for entire VRF Systems.Refrigerant charging will be done according to Total liquid pipe length and ambient conditions.). All wall / partition crossings with proper PVC sleeve. Nitrile foam insulation finished with 7mils woven fibre glass cloth covering adhered between two coats of fungicidal protective coating |  |  |  |  | 0 | 0 | 0
| 1/4 " dia (6.5 MM ) with 13 mm insulation | Rmt | 40 | 434 | 209 | 17360 | 8360 | 25720
| 3/8 " dia (9.5 MM ) with 13 mm insulation | Rmt | 50 | 497 | 209 | 24850 | 10450 | 35300
| 1/2 " dia (12 MM ) with 13 mm insulation | Rmt | 30 | 722 | 217 | 21660 | 6510 | 28170
| 5/8 " dia (15.6 MM ) with 13 mm insulation | Rmt | 25 | 884 | 217 | 22100 | 5425 | 27525
| 3/4 " dia (19.1 MM ) with 13 mm insulation | Rmt | 20 | 999 | 235 | 19980 | 4700 | 24680
| 7/8 " dia (22.4 MM) with 19 mm insulation | Rmt | 50 | 1218 | 235 | 60900 | 11750 | 72650
| 1 " dia (25.8 MM) with 19 mm insulation | Rmt | RO |  |  | 0 | 0 | 0
| 11/8 " dia (28.6 MM) with 19 mm insulation | Rmt | RO |  |  | 0 | 0 | 0
| 13/8 " dia (34.9 MM) with 19 mm insulation | Rmt | RO |  |  | 0 | 0 | 0
| Note: Piping and cable dia as per OEM |  |  |  |  | 0 | 0 | 0
4 | Electrical Cable between MCB to ODU -Supply and Laying of 4C X 4 Sq.mm aluminium cable with with necessary supports and fiitings for looping from MCB to outdoor units. | Rmt | 50 | 115 | 28 | 5750 | 1400 | 7150
5 | Control Cable between IDU to ODU -Supply and Laying of 2C X 1 Sq.mm Shielded Communication cable with GI Conduit pipe ( Dia 25 mm ) with necessary supports and fiitings for looping all the indoor Units with outdoor units. | Rmt | 120 | 184 | 40 | 22080 | 4800 | 26880
6 | Supply, Installation of Power Cable -3Core * 1.5Sqmm -ODU to Modbus /Bacnet (BMS Connectivity) | Rmt | 70 | 118 | 20 | 8260 | 1400 | 9660
[6 empty] | 0 | 0 | 0
7 | DRAIN PIPE -with necessary supports and fittings. |  |  |  |  | 0 | 0 | 0
| Supply and Laying CPVC / UPVC drain pipe including with 9 mm thick nitrile foam insulation , supports , clamps up to 50 mm dia. including drilling, wall chipping etc , conceal the wall openning ,fittings like couplings,elbows,T-Joints,U traps to remove condensate water from indoor units to desired drain point. |  |  |  |  | 0 | 0 | 0
6.1 | 25mm dia | Rmt | 30 | 181 | 38 | 5430 | 1140 | 6570
6.2 | 32mm dia | Rmt | 15 | 217 | 46 | 3255 | 690 | 3945
6.3 | 40mm dia | Rmt | RO |  |  | 0 | 0 | 0
6.4 | 50mm dia | Rmt | RO |  |  | 0 | 0 | 0
|  |  | 0 |  |  | 0 | 0 | 0
| TOTAL - VRF System |  |  |  |  | 0 | 0 | 0
7 | Indoor air Quality test pre and post occupancy as per the LEED requirements a) PM 10 b) CARBON MONOXIDE c) PM 2.5 d) Ozone | Nos | 4 | 0 | 5706 | 0 | 22824 | 22824
8 | VRF machine one year AMC charges post the warranty | Nos | 1 | 0 | 27034 | 0 | 27034 | 27034
| TOTAL HVAC WORKS |  |  |  |  | 3463623 | 736377 | 4200000

## FIRE & SAFETY
PROJECT | PAYTM
SUBJECT | LIFE SAFETY SYSTEM BOQ SUMMARY
DATE | 2026-04-01
VERSION | V0
BILL OF QUANTITIES FOR FIRE AND LIFE SAFETY SYSTEMS
Sl.No. | DESCRIPTION | UNIT | QNT | RATE |  | AMOUNT
|  |  |  | Supply | Installation | Supply | Installation | Total
PART-A
I | Analogue Addressable FA System
1 | Supply Installation Testing and Commissioning of UL 864, 10th Edition and FM-approved 32-bit Microprocessor based Intelligent Addressable Peer-to-Peer networkable 2 Loop Fire Alarm Control Panel. The panel shall accommodate up to 2 nos. of 12V/50AH batteries in its housing and shall have a battery charging capacity of (up to) 2 nos. of 12V/100 AH housed externally, shall have an 8" Color Touch Screen Display to show 8 simultaneous events at a time and at least 10 custom-programmable soft and hard buttons for user-specific programmable functions. Each Detection Loop shall accommodate up to 250 detectors and devices in any flexible combination (suggested to have min. 200 detectors support per loop)and shall accommodate up to 3000 Addresses at 100% capacity in any combination. Scope includes the network card for panel-to-panel integration. Edwards Make Power supply should be tap from emergency UPS | Set | 1 | 238870 | 14219 | 238870 | 14219 | 253089
[6 empty] | 0 | 0 | 0
2 | Supply Installation Testing and Commissioning of Modbus / BACnet over IP protocol for integrating FA panel with necessary hardware and accessories. | Set | 1 | 148110 | 9479 | 148110 | 9479 | 157589
[6 empty] | 0 | 0 | 0
3 | Supply Installation Testing and Commissioning of Fire Graphic Software with real time fire system status and system control options. They all interface directly with the system network Gateway. System to be compatible for BMS System. | Set | 0 |  |  | 0 | 0 | 0
[6 empty] | 0 | 0 | 0
4 | Supply Installation Testing and Commissioning of PC with the following configuration. • 8 GB of RAM • SATA hard disk drive • 1TBGB Storage • I7 3GHz Processor • XGA or higher video card PCI-Express, with OpenGL (v4.0 or above) hardware acceleration support, minimum 512 MB RAM • 1280 x 1024 pixel resolution and 65K colors • 10/100/1000 Ethernet Network Interface Card • Windows 10/11 Professional Licensed OS (64-bit) • 21'' Flat Screen Monitor • USB 3.0 • Gigabit TCP/IP Port with 100/1000Mbps network card with antivirus software, MS software with a sound card, mouse, keypad, etc. | Set | RO |  |  | 0 | 0 | 0
[6 empty] | 0 | 0 | 0
5 | Supply Installation Testing and Commissioning of Intelligent Addressable Photoelectric smoke detector with a standard base and junction box. The optical sensor element shall have a sensitivity range of 0.53 to 3.94 %/ft. (1.7 to 12.35 %/m) obscuration, air velocity range from 0 to 4,000 ft./min (0 to 20 m/s), operating temperature range from -20°C to 60°C, and the operating environment from 0 to 49°C, 0 to 93% RH, Non-Condensing. |  |  |  |  | 0 | 0 | 0
a | Above Ceiling Detectors | Nos. | 62 | 3039 | 286 | 188418 | 17732 | 206150
b | Below Ceiling Detectors | Nos. | 38 | 2812 | 286 | 106856 | 10868 | 117724
6 | Supply Installation Testing and Commissioning of Intelligent Addressable Multi-Sensor (Optical Smoke + Heat) detector with a standard base and junction box. The optical sensor element shall have multiple selectable sensitivity levels from 0.2% Obs/ft to 3.7% Obs/ft. The ROR detection element shall have a selectable rate of rising setting of 8°C per minute and 11°C per minute (or close to this value not deviating more than 1°C). The fixed temp detection element shall have two selectable settings of 57°C and 68°C (or closer to this value not deviating by 1°C). Multi-sensor detectors shall have a configuration mode that gives separate alarms for smoke detection and heat detection and shall indicate the cause of the alarm (smoke or heat). Also, the multi-sensor shall have a combined configuration mode of smoke and heat detection that gives only one evaluated alarm from a multi-sensor detector in case of a fire event. The detector shall have an operating temperature range from -9°C to 50°C and a humidity tolerance range of up to 95% RH, Non-Condensing. |  |  |  |  | 0 | 0 | 0
a | Above Ceiling Detectors | Nos. | 5 | 3215 | 286 | 16075 | 1430 | 17505
b | Below Ceiling Detectors | Nos. | 5 | 2987 | 286 | 14935 | 1430 | 16365
c | False Floor Detectors | Nos. | 0 |  |  | 0 | 0 | 0
[6 empty] | 0 | 0 | 0
7 | Supply Installation Testing and Commissioning of Intelligent Addressable Rate of Rising cum Fixed Temperature Heat Detector along with base and junction box. Rate-of-Rise temperature detection element shall have two selectable settings of 8° C and 11° C (or closer to this value not deviating by 1°C) and Fixed temperature sensing shall be independent of rate-of-rise sensing and shall have two selectable settings of 57° C and 68°C (or closer to this value not deviating by 1°C). The detector shall have an operating temperature range from 0°C to 50°C and a humidity tolerance range of up to 95% RH, Non-Condensing. | Nos. | 2 | 3039 | 286 | 6078 | 572 | 6650
[6 empty] | 0 | 0 | 0
8 | Supply Installation Testing and Commissioning of Analogue Addressable Duct sensor detector with local housing and necessary hardware and accessories. | Nos. | 1 | 10219 | 286 | 10219 | 286 | 10505
[6 empty] | 0 | 0 | 0
9 | Supply Installation Testing and Commissioning of Response indicator for all detectors located above false ceiling and below false flooring. | Nos. | 55 | 106 | 96 | 5830 | 5280 | 11110
[6 empty] | 0 | 0 | 0
10 | Supply and Installation of Addressable Single action Manual call point as per OEM (Push/Breakglass/Pull Station) with necessary hardware and accessories. | Nos. | 3 | 3585 | 286 | 10755 | 858 | 11613
[6 empty] | 0 | 0 | 0
11 | Supply Installation Testing and Commissioning of addressable type Horn / Strobe rated at 82 dBA @ 3m for Audible annunciation and 75cd flashing at 1 Hz for visual indication. | Nos. | 5 | 5495 | 286 | 27475 | 1430 | 28905
[6 empty] | 0 | 0 | 0
12 | Supply Installation Testing and Commissioning of addressable fault isolator module for isolating shorted dewired and lose circuits between two successive fault isolators with automatic resetting arrangement to protect the loop from short circuits, the rate shall include GI back box and Cu gland. | Nos. | 6 | 2669 | 286 | 16014 | 1716 | 17730
[6 empty] | 0 | 0 | 0
13 | Supply Installation Testing and Commissioning of Addressable Control Relay modules for Monitoring/controlling Input or Output. |  |  |  |  | 0 | 0 | 0
| - Access control System |  |  |  |  | 0 | 0 | 0
| - Integration with Builder fire alarm system |  |  |  |  | 0 | 0 | 0
| - PA system |  |  |  |  | 0 | 0 | 0
| - Ac Tripping(AHU/DX DUCTABLE SPLIT/DX VRF/PAC) |  |  |  |  | 0 | 0 | 0
| - For Fire Curtains / Water curtain |  |  |  |  | 0 | 0 | 0
| - For Motorised Fire Dampers/Exhaust/Fresh Air fans |  |  |  |  | 0 | 0 | 0
| the rate shall include GI back box and Cu gland | Nos. | 6 | 2669 | 286 | 16014 | 1716 | 17730
[6 empty] | 0 | 0 | 0
14 | Supply Installation Testing and Commissioning of the Control Module shall be capable of providing SPDT/DPDT contact rated at 24V DC, 2A. The quoted rate shall be with the necessary back box for mounting (for the hooter/strobe). | Nos. | 5 | 2669 | 286 | 13345 | 1430 | 14775
[6 empty] | 0 | 0 | 0
15 | Supply and Installation of 24DC, 10A power supply for Hooters, the quoted rate shall be with the necessary back box for mounting. | Nos. | 2 | 2086 | 1423 | 4172 | 2846 | 7018
[6 empty] | 0 | 0 | 0
16 | Supply Installation Testing and Commissioning of Addressable Monitor Module for Sprinkler Flow Switch and WLD with all mounting accessories, complete with MS Powder coated Junction Box for mounting and on Surface, Cable lugs at Ends, cable compression glands, cable tags and Ferruling. | Nos. | 4 | 2669 | 286 | 10676 | 1144 | 11820
[6 empty] | 0 | 0 | 0
17 | Supply and Laying of 2Cx1.5 sq. mm multistrand copper, FRLS Armoured cable. RED in colour, laid on the surface with GI saddle supports and spacers every 0.3 meters. Complete with GI junction boxes, cable lugs at both ends, cable compression glands, cable tags and ferrule, etc. | Mtrs | 1946 | 101 | 35 | 196546 | 68110 | 264656
[6 empty] | 0 | 0 | 0
18 | Removing and re-locating of existing builder detectors overlapping with interior partition walls/hvac ducts/raceways with necessary required cabling, hardware and accessories. | Nos | 4 | 0 | 380 | 0 | 1520 | 1520
[6 empty] | 0 | 0 | 0
19 | Supply and Installation of GI perforated raceways in the ceiling made of 1.6mm thick sheet steel and covered with 1.2mm sheet steel with necessary hardware including supporting with threaded hi-tech rods, junctions, etc. |  |  |  |  | 0 | 0 | 0
a | 200x50mm | Mtrs | 10 | 505 | 86 | 5050 | 860 | 5910
b | 100x50mm | Mtrs | 0 |  |  | 0 | 0 | 0
c | 50x40mm | Mtrs | 0 |  |  | 0 | 0 | 0
| Sub Total for Analogue Addressable FA System |  |  |  |  | 1035438 | 142926 | 1178364
[6 empty] | 0 | 0 | 0
II | PUBLIC ADDRESS SYSTEM |  |  |  |  | 0 | 0 | 0
| NOTE - Tapping for Workstation & Passage speakers - 6W. Tapping for closed rooms / cabins speakers - 1.5W/3W. |  |  |  |  | 0 | 0 | 0
1 | Supply Installation Testing and Commissioning of 19U rack for mounting PA system hardware with rigid frame construction, Vented front glass door with a fully vented rear steel door, Top cover with gland plate and single fan cut out, powder coated with black shade with required power distribution with castor wheels for easy maintenance. | Nos | 1 | 21613 | 2703 | 21613 | 2703 | 24316
[6 empty] | 0 | 0 | 0
2 | Supply Installation Testing and Commissioning of Voice Alarm controller 6/8 Zone with inbuilt Amplifier with a provision of having a Fire Microphone inbuilt in the controller and should have a prerecorded message as 1st level Priority automatically in case of emergency or Fire, Announcing console as 2nd level and music the least (with music zone selector) Alert and Message of Fire Evacuation as per EN54 Standards. Controller to be with the USB option. | Nos | 1 | 232234 | 14219 | 232234 | 14219 | 246453
[6 empty] | 0 | 0 | 0
3 | Supply Installation Testing and Commissioning of 480 Watts Power Amplifier in a 3U high housing with 70 V / 100 V and 8-ohm outputs, Dual inputs with priority switching, 100 V input for slave operation on 100 V speaker line, Mains, battery back-up, TÜV certified according to IEC 60849 and with necessary channel/mounting support to place the amplifier in the existing rack. | Nos | 1 | 39813 | 4740 | 39813 | 4740 | 44553
[6 empty] | 0 | 0 | 0
4 | Supply Installation Testing and Commissioning of Gooseneck microphone with keypad for zone selection and necessary accessories. | Nos | 1 | 42656 | 1423 | 42656 | 1423 | 44079
[6 empty] | 0 | 0 | 0
5 | Supply Installation Testing and Commissioning of 6W Ceiling Recessed Speaker with max SPL1M/1W 96dB. Frequency response of 80Hz-20KHz with a dispersion angle of 160 deg. The speaker should have tappings at 6W/3W/1.5W. Complete with necessary mounting hardware and accessories. | Nos | 40 | 997 | 238 | 39880 | 9520 | 49400
[6 empty] | 0 | 0 | 0
6 | Supply Installation Testing and Commissioning of 6W Wall mount speaker with max SPL1M/1W 96dB. Frequency response of 160Hz-20KHz. The speaker should have tappings at 6W/3W.complete with necessary mounting hardware and accessories. | Nos | 2 | 1138 | 238 | 2276 | 476 | 2752
[6 empty] | 0 | 0 | 0
7 | Supply Installation Testing and Commissioning of 6W Ceiling surface mounted Speaker with max SPL1M/1W 96dB. Frequency response of 80Hz-20KHz with a dispersion angle of 160 deg. The speaker should have tappings at 6W/3W/1.5W, complete with necessary mounting hardware and accessories along with the back box. | Nos | 18 | 1234 | 238 | 22212 | 4284 | 26496
[6 empty] | 0 | 0 | 0
8 | Supply and Laying of 2Cx1 sq. mm multistrand copper, FRLS Armoured cable. BLACK in colour, laid on the surface with GI saddle supports and spacers every 0.3 meters. Complete with GI junction boxes, cable lugs at both ends, cable compression glands, cable tags and ferrule, etc. | Mtrs | 840 | 101 | 35 | 84840 | 29400 | 114240
[6 empty] | 0 | 0 | 0
9 | Supply and Laying of 100x100mm UPVC cable trough wire manager with cover for dressing up of cables. | Mtrs | 10 | 551 | 86 | 5510 | 860 | 6370
| Sub Total for PA System |  |  |  |  | 491034 | 67625 | 558659
[6 empty] | 0 | 0 | 0
III | Fire Extinguishers |  |  |  |  | 0 | 0 | 0
1 | Supply and Installation of 4.5kg CO2 type fire extinguisher consisting of welded M.S cylindrical body, squeeze lever discharge valve fitted with pressure indicating gauge internal discharge tube, 2mtr long high-pressure discharge hose, discharge nozzle, suspension bracket conforming to IS: 15683 finished externally with red enamel paint and fixed to the wall with brackets or Floor mounting bracket with four legs complete with internal charge and Fluorescent Sign board, etc. | Nos | 2 | 5119 | 238 | 10238 | 476 | 10714
[6 empty] | 0 | 0 | 0
2 | Supply and Installation of 6KG ABC Type Fire Extinguisher, Stored Pressure Type, Pressure Gauge, Discharge Time less than 10 Secs, Controllable discharge mechanism, Range minimum 3 Meters, applicable on Class A, B, C and electrically started Fire, Helium Leak Detection Tested, Floor mounting bracket with four legs and Fluorescent Sign board, etc. complete, ISI and EN Approved, confirming to IS: 15683. | Nos | 9 | 2371 | 238 | 21339 | 2142 | 23481
[6 empty] | 0 | 0 | 0
3 | Supply and Installation of 4 Kg Wet Chemical Stored Pressure Class “K” Kitchen Extinguishers with floor mounting bracket with four legs and Fluorescent Sign board etc. Complete, ISI and EN Approved, confirming to IS: 15683. | Nos | 1 | 2845 | 238 | 2845 | 238 | 3083
[6 empty] | 0 | 0 | 0
4 | Supply and Installation of Ceiling mounted type clean agent automatic (FE36) fire extinguishers of capacity fitted with an automatic sprinkler valve that shall be calibrated to discharge at an ambient temperature of 68°C. The extinguisher shall be manufactured strictly as per IS standards. The quoted rate shall include necessary supports suitable for ceiling mounting. (For UPS, Battery and Hub rooms) |  |  |  |  | 0 | 0 | 0
a | 5KG | Nos | 5 | 15812 | 949 | 79060 | 4745 | 83805
B | 10KG | Nos | RO |  |  | 0 | 0 | 0
[6 empty] | 0 | 0 | 0
5 | Supply, Installation, Testing and Commissioning of Panel proection system,Fire Extinguisher -MMO FIRESPOT 4 kg with Pressure Switch (FK5112) with Heat sensitive tube - 15-20 mtrs with necessary accessories like pressure gauge, Dummy End Cap, Threaded Nipple End and mounting Bracket. (Make - Minimax/ Kanex) | Set | RO |  |  | 0 | 0 | 0
[6 empty] | 0 | 0 | 0
| Supply and Installation of 2.0kg CO2 type fire extinguisher consisting of welded M.S cylindrical body, squeeze lever discharge valve fitted with pressure indicating gauge internal discharge tube, 2mtr long high-pressure discharge hose, discharge nozzle, suspension bracket conforming to IS: 15683 finished externally with red enamel paint and fixed to the wall with brackets or Floor mounting bracket with four legs complete with internal charge and Fluorescent Sign board, etc. | Nos | 2 | 3319 | 238 | 6638 | 476 | 7114
[6 empty] | 0 | 0 | 0
[6 empty] | 0 | 0 | 0
| Sub Total for Fire Extinguishers |  |  |  |  | 120120 | 8077 | 128197
[6 empty] | 0 | 0 | 0
IV | Fire Exit Signages |  |  |  |  | 0 | 0 | 0
1 | Supply, Installation & Testing of LED Based directional exit signage boards along with mounting bracket and 2 Hrs self-maintained Battery backup. | Nos | 12 | 2276 | 380 | 27312 | 4560 | 31872
a | Supply & Installation of battery-operated LED Exit signages for Emergency fire exit doors, to be fixed above the doors. | Nos | 1 | 2276 | 380 | 2276 | 380 | 2656
b | Supply & Installation of battery-operated LED Exit signages Ceiling Suspended with dual side signages. (12" x 7") | Nos | 6 | 2276 | 380 | 13656 | 2280 | 15936
[6 empty] | 0 | 0 | 0
2 | Designing, Drafting & taking necessary client architect and consultant approval with A3 size color Evacuation Plans with photoluminescent printed with Glass on SS studs. | Set | 6 | 2845 | 475 | 17070 | 2850 | 19920
3 | Supplying and installing of Fire Alarm Panel/reprater panel with symbol -size 6"x8" location | Nos | 1 | 808 | 238 | 808 | 238 | 1046
4 | Supplying and installing of " Extinguisher Signages - Autoglow, with suspension chains (Autoglo signages, size 150 x 300) - single side | Nos | 14 | 808 | 238 | 11312 | 3332 | 14644
5 | Supplying and installing of " Manual call point signages - (Aotoglow - "Opaque" PVC foam board of computerised cut, PVC non-reflective self adhesive vinyl painted foam board) with suspension chains (Autoglo signages, size 150 x 300) - single side | Nos | 3 | 808 | 238 | 2424 | 714 | 3138
| Sub Total for Fire Exit Signages |  |  |  |  | 74858 | 14354 | 89212
V | SPRINKLER SYSTEM
1 | Supply Installation Testing and Commissioning of G.I. Pipes confirming to IS 1239 Pt -I Heavy grade with painting, a suitable type of supports (for above 80 mm dia, shall be fabricated by M.S. Channel / Angle / Falts etc), anchor fasteners, bolts nuts, clamps, "U" bolts, malleable specials such as Reducers, Tees, elbows, flanges. Including cutting, Welding, fixing in/on walls, ceiling by using suitable supports etc, as per drawings. The quoted rate shall also include chasing/chipping walls, making bore holes in walls/floor, making them good with filler material, finishing in cement mortar, etc. Welded type piping work will not be accessaptable only Fittings required for complete netwrok and accessories. |  |  |  |  | 0 | 0 | 0
a | 150 NB, Heavy Class | Mtrs | 12 | 3069 | 570 | 36828 | 6840 | 43668
b | 100 NB, Heavy Class | Mtrs | 12 | 2141 | 456 | 25692 | 5472 | 31164
c | 80 NB, Heavy Class | Mtrs | 12 | 1479 | 371 | 17748 | 4452 | 22200
d | 65 NB, Heavy Class | Mtrs | 18 | 1211 | 286 | 21798 | 5148 | 26946
e | 50 NB, Heavy Class | Mtrs | 78 | 1150 | 229 | 89700 | 17862 | 107562
f | 40 NB, Heavy Class | Mtrs | 66 | 822 | 184 | 54252 | 12144 | 66396
g | 32 NB, Heavy Class | Mtrs | 72 | 718 | 172 | 51696 | 12384 | 64080
h | 25 NB, Heavy Class | Mtrs | 140 | 565 | 138 | 79100 | 19320 | 98420
[6 empty] | 0 | 0 | 0
2 | Supply Installation Testing and Commissioning of Butterfly Valve with matching flanges. |  |  |  |  | 0 | 0 | 0
a | 150 NB | Nos. | 0 |  |  | 0 | 0 | 0
b | 100 NB | Nos. | 1 | 4096 | 475 | 4096 | 475 | 4571
[6 empty] | 0 | 0 | 0
3 | Supply Installation Testing and Commissioning of UL-listed and FM-approved Flow Switch with two NO and two NC contacts with necessary nipple and other fittings. |  |  |  |  | 0 | 0 | 0
a | 150 NB | Nos. | 0 |  |  | 0 | 0 | 0
b | 100 NB | Nos. | 1 | 7254 | 1452 | 7254 | 1452 | 8706
[6 empty] | 0 | 0 | 0
4 | Supplying, installing, testing and commissioning of Sight glass unit for sprinkler drain, drain valves, ball valves, check valves, Union etc. complete.Set shall be UL Listed | Nos. | 1 | 4740 | 475 | 4740 | 475 | 5215
[6 empty] | 0 | 0 | 0
5 | Supply Installation Testing and Commissioning of 50mm Test Valve Drain Kit with sight Glass, Ball Valve, Union and Required fittings, etc. UL-Listed and FM-approved. | Nos. | 2 | 9058 | 1813 | 18116 | 3626 | 21742
[6 empty] | 0 | 0 | 0
6 | Supply Installation Testing and Commissioning of Pressure Guage 0 - 15 Kg / cm2 with the mounting arrangement and ball valve. ISI MARKED. | Nos. | 1 | 3224 | 380 | 3224 | 380 | 3604
[6 empty] | 0 | 0 | 0
7 | Supply and Installation of a quick response, std. coverage conventional sprinkler of quartzoid bulb type with 15mm screwed end connection of 68° C temperature rating, K-factor of K80 and orifice of not less than 6mm. Sprinklers shall be UL-Listed/FM-approved. |  |  |  |  | 0 | 0 | 0
a | Upright Sprinkler | Nos. | 15 | 712 | 191 | 10680 | 2865 | 13545
b | Pendent Sprinkler | Nos. | 70 | 712 | 191 | 49840 | 13370 | 63210
c | Side Wall Sprinkler | Nos. | 0 |  |  | 0 | 0 | 0
d | Royal Flush [Concealed type sprinkler bulb] | Nos. | 6 | 1660 | 191 | 9960 | 1146 | 11106
[6 empty] | 0 | 0 | 0
8 | Supply and Installation of a quick response, std. coverage conventional sprinkler of quartzoid bulb type with 15mm screwed end connection of 93° C temperature rating, K-factor of K80 & orifice of not less than 6mm. Sprinklers shall be UL-listed and FM-approved. (Pendent sprinkler at the kitchen, tuck shop). | Nos. | RO |  |  | 0 | 0 | 0
[6 empty] | 0 | 0 | 0
9 | Supply and Installation of standard two-piece flush escutcheon/rosette plates for pendent sprinklers with 15mm screwed end connection. The escutcheon plates shall be of carbon steel material with white or brass finishes as per technical specifications. | Nos. | 70 | 77 | 20 | 5390 | 1400 | 6790
[6 empty] | 0 | 0 | 0
10 | Supply and Installation of stainless steel braided flexible drop (hose) for dropping sprinklers below the false ceiling. The sprinkler drop shall be of 16 bar pressure rating and 1500 mm long along with 2 slip nuts, sprinkler reducer, lightweight ceiling bracket component, etc. as required and complete as per technical specification. Flexible drop shall be UL/FM approved. | Nos. | 76 | 1471 | 286 | 111796 | 21736 | 133532
[6 empty] | 0 | 0 | 0
11 | Hydraulic Pressure Testing of the entire floor Sprinkler Piping Network to a pressure of 12.5 Kgs/sq.cm and retaining the pressure for a minimum period of 24 Hours. | Lot | 1 | 0 | 23698 | 0 | 23698 | 23698
[6 empty] | 0 | 0 | 0
12 | Removing of existing sprinklers (provided by base builder) at the true ceiling from the existing branch lines and re-locating them to the proposed location in coordination with interior partition walls/hvac ducts/raceways as per drawings. | Job | 1 | 0 | 18958 | 0 | 18958 | 18958
|  |  | 1 | 0 | 0 | 0 | 0 | 0
13 | Supply and paint the exposed ceiling existing sprinkler pipes with one coat of zinc primer and two coats of synthetic enamel paint of approved make and colour shade. The pipe surface shall be thoroughly cleaned to remove all dirt, grease, scale etc. before applying the primer. | Lot | 1 | 37916 | 14219 | 37916 | 14219 | 52135
[6 empty] | 0 | 0 | 0
14 | Removal and modification of sprinkler pipes. Scope includes cutting of pipes, rerouting of pipes if needed, relaying of pipes to suit the interior requirements with suitable supports, joints, elbows, etc. and paint works for pipes with necessary hardware and accessories. |  |  |  |  | 0 | 0 | 0
a | 150 NB, Heavy Class | Mtrs | 0 |  |  | 0 | 0 | 0
b | 100 NB, Heavy Class | Mtrs | 0 |  |  | 0 | 0 | 0
c | 80 NB, Heavy Class | Mtrs | 6 | 0 | 556 | 0 | 3336 | 3336
d | 65 NB, Heavy Class | Mtrs | 6 | 0 | 429 | 0 | 2574 | 2574
e | 50 NB, Heavy Class | Mtrs | 12 | 0 | 343 | 0 | 4116 | 4116
f | 40 NB, Heavy Class | Mtrs | 13.2 | 0 | 274 | 0 | 3616.8 | 3616.8
g | 32 NB, Heavy Class | Mtrs | 14.4 | 0 | 257 | 0 | 3700.8 | 3700.8
h | 25 NB, Heavy Class | Mtrs | 28 | 0 | 206 | 0 | 5768 | 5768
| Sub Total for Sprinkler System |  |  |  |  | 639826 | 210533.6 | 850359.6
[6 empty] | 0 | 0 | 0
VI | WATER LEAK DETECTION SYSTEM |  |  |  |  | 0 | 0 | 0
| (For Server room ,UPS , Battery Room) |  |  |  |  | 0 | 0 | 0
1 | Supply Installation Testing and Commissioning of Water leak detection control panel of 2 zone type consists of features like Auxiliary alarm contacts, Monitored alarm outputs, Open and short circuit line monitoring, Bright LED for indication, and a detection module inbuilt. The panel shall have a lockable enclosure. The panel shall work on 230v AC, have a built-in battery backup and be compatible with the BMS System. | Nos. | 1 | 8059 | 1423 | 8059 | 1423 | 9482
[6 empty] | 0 | 0 | 0
2 | Supply and Laying of Water Leak Cable Sensor: |  |  |  |  | 0 | 0 | 0
a | -Non-conductive cable as detection medium less prone to false alarms. - It shall be suitable for any conducting fluid. - The cable excitation shall be an isolated AC signal which ensures that the detector will not be subject to oxidation or erosion over time. - It shall be capable of detecting leakage along the 20 Mtrs entire length. | Nos. | 3 | 11565 | 949 | 34695 | 2847 | 37542
[6 empty] | 0 | 0 | 0
3 | Supply Installation Testing and Commissioning of Electronic Hooter for water sensing indication. | Nos. | 2 | 1707 | 380 | 3414 | 760 | 4174
[6 empty] | 0 | 0 | 0
4 | Supply and laying of 2 Core 1.0 Sq mm Flexible Cable in 1" FRLS PVC conduit with GI Saddles and spacers at every 0.5 meter and all accessories MS junction/pull boxes, G.I fish wire, fixing accessories etc. | Mtrs | 45 | 101 | 35 | 4545 | 1575 | 6120
| Sub Total for Water Leak Detection System |  |  |  |  | 50713 | 6605 | 57318
[6 empty] | 0 | 0 | 0
VII | RODENT REPELLENT SYSTEM |  |  |  |  | 0 | 0 | 0
| (For Server room ,UPS , Battery Room) |  |  |  |  | 0 | 0 | 0
1 | Supply Installation Testing and Commissioning of Microprocessor-based Master Controller Console with 32 characters LCD DISPLAY, with onboard controls generating frequencies from 20Khz to 60 kHz, complete with all related mounting accessories such as racks, stand brackets, etc. The Master Console shall be able to connect to 24 transducers and be compatible with the BMS System. | Nos. | 1 | 8059 | 1423 | 8059 | 1423 | 9482
[6 empty] | 0 | 0 | 0
2 | Supply Installation Testing and Commissioning of Transducer Satellite Stations capable of Emitting Ultrasonic sound of frequencies 20 kHz and higher, with blinking, LED Indication & shall be capable of covering an area of 250Sq ft in the ceiling and floor voids. | Nos. | 12 | 618 | 144 | 7416 | 1728 | 9144
[6 empty] | 0 | 0 | 0
3 | Supply and laying of 2 Core 1.0 Sq mm Flexible Cable in 1" FRLS PVC conduit with GI Saddles and spacers at every 0.5 meter and all accessories MS junction/pull boxes, G.I fish wire, fixing accessories etc. | Mtrs | 100 | 101 | 35 | 10100 | 3500 | 13600
| Sub Total for Rodent Repellent System |  |  |  |  | 25575 | 6651 | 32226
| TOTAL AMOUNT - Fire & Safety |  |  |  |  | 2437564 | 456771.6 | 2894335.6

## ACS & CCTV
PROJECT | LIFE SAFETY SYSTEM BOQ SUMMARY
SUBJECT | ACCESS CONTROL & CCTV SYSTEM
DATE | 2026-04-01
VERSION | V0
Sl.No. | DESCRIPTION |  | UNIT | QNT | RATE |  | AMOUNT |  |  | Remarks
[5 empty] | Supply | Installation | Supply | Installation | Total
PART-B
I | ACCESS CONTROL | Make / Model
1 | Supply, Installation, Testing & Commissioning of 4 Door & 4 reader Controller (Oryggi 4 door 4 reader controller with encloser & PSU) Intelligent Controller capable of entry & exit control & battery backup to power the controller, EM Locks, Readers, etc. build-in ethernet connection, 32M memory on broad with 300,000 cards capability, 50,000 Log Capacity with TCP IP connectivity. Encloser box for controller Oryggi Controller with Licens |  | Nos | 3 | 41400 | 1500 | 124200 | 4500 | 128700
1 | Supply, Installation, Testing & Commissioning of 2 Door Intelligent Controller capable of entry & exit control & battery backup to power the controller, EM Locks, Readers, etc. build-in ethernet connection, 32M memory on broad with 300,000 cards capability, 50,000 Log Capacity with TCP IP connectivity. |  | Nos | 0 |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
3 | Supply, Installation, Testing & Commissioning of Multi-technology Card Readers as per specification | [5 empty] | 0 | 0 | 0
| The readers shall have the following features:- a) Water resistance, high security, and high durability. b) Mounted directly on metal without affecting performance. c) Suitable for the Wiegand interface. d) Low power consumption. e) Audiovisual indication. f) Internal self-test routine checks and verifies setup configuration. g) Card read time less than .1 sec. h) I Class Smart Card reader (Acs card reader smart I SPR 501) i) Suprema Biometric reader for server room( BIO ENTRY P2) |  | Nos | 7 | 37375 | 1500 | 261625 | 10500 | 272125
[7 empty] | 0 | 0 | 0
4 | Supply Installation Testing and Commissioning of Pinpad + Reader with necessary hardware & accessories. |  | Nos | 1 | 37375 | 1500 | 37375 | 1500 | 38875
[7 empty] | 0 | 0 | 0
5 | Supply & Installation of Electromagnetic Locks with a holding of 600lbs suitable for single door (L bracket 83014090 Make Bel) |  | Nos | 3 | 3000 | 500 | 9000 | 1500 | 10500
[6 empty] | - | 0 | 0 | 0
6 | Supply & Installation of Electromagnetic Locks with a holding for of 600lbs suitable for double door |  | Nos | 2 | 6000 | 500 | 12000 | 1000 | 13000
[7 empty] | 0 | 0 | 0
7 | Supply & Installation of Magnetic Contacts - Flush Mounted/ Surface mounted for alarms with necessary hardware & accessories. |  | Nos | 7 | 450 | 150 | 3150 | 1050 | 4200
[7 empty] | 0 | 0 | 0
8 | Supply & Installation of buzzer with necessary hardware & accessories. |  | Nos | 5 | 350 | 150 | 1750 | 750 | 2500
[7 empty] | 0 | 0 | 0
9 | Supply of Proximity cards of standard size and is thin and flexible. The read ring of the card should be consistent and not affected by body shielding or variable environmental condition. |  | Nos | 0 |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
10 | Supply & Installation of Egress switch / Exit Push Button with necessary accessories & hardware. |  | Nos | 1 | 450 | 200 | 450 | 200 | 650
[7 empty] | 0 | 0 | 0
11 | Supply & Installation of Emergency Door Release switch with necessary accessories & hardware. |  | Nos | 5 | 850 | 200 | 4250 | 1000 | 5250
[7 empty] | 0 | 0 | 0
12 | Supply & Installation of the Panic bar for the Fire exit doors complete with necessary accessories & hardware. |  | Nos | 0 |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
14 | Access software - (SPECIFY NO OF USERS) |  | Nos | 1 | 20700 | 1500 | 20700 | 1500 | 22200
[7 empty] | 0 | 0 | 0
15 | Supply and Laying of 4 Core x 0.75 sq mm multi-strand, ATC, shielded Cable as per specification |  | Mtrs | 300 | 80 | 20 | 24000 | 6000 | 30000
[7 empty] | 0 | 0 | 0
16 | Supply and Laying of 8 Core x 0.75 sq mm multi-strand, ATC, shielded Cable as per specification |  | Mtrs | 300 | 135 | 20 | 40500 | 6000 | 46500
[7 empty] | 0 | 0 | 0
17 | Supply and Laying of 1" GI Conduits on the wall, columns, cable trays false ceiling etc., with GI spacers, saddles including associated civil works (Purple colour). |  | Mtrs | 300 | 60 | 20 | 18000 | 6000 | 24000
[7 empty] | 0 | 0 | 0
18 | Supply and Laying of perforated raceway of below dimensions with necessary supports for ACS & CCTV works | [5 empty] | 0 | 0 | 0
a | 200x50mm |  | Mtrs | 10 | 530 | 120 | 5300 | 1200 | 6500
b | 100x50mm |  | Mtrs |  |  |  | 0 | 0 | 0
c | 50x40mm |  | Mtrs | 0 |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
| Sub Total for Access Control System | [5 empty] | 562300 | 42700 | 605000
[7 empty] | 0 | 0 | 0
II | CCTV | [5 empty] | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
1 | Supply, Installation, Testing & Commissioning of Network video recorder with bundled server machine, Preloaded of Enterprises Software & with remote monitoring facilities | [5 empty] | 0 | 0 | 0
| Protoco:TCP/IP, DHCP, SMTP. Power supply source : 240V, 50Hz, AC. Video output : Monitor - A :- 1 BNC, RCA, VGA.: Monitor - B :- 1 BNC (single / multi) Compression : H.264, MPEG-4 & MJPEG on IP cameras Display resolution : 720 x 480 / 720 x 576 (PAL) Motion based Recording OF 70%(Speed/Resolution) Resolution : a) 720p @ 10fps. H.264 format for 30Days HDD Back:: 90 Days Motion based recording, 70% Motion recording per day. | [5 empty] | 0 | 0 | 0
a | 32 Channel NVR with Hard Disk Make PRAMA |  | Nos | 1 | 40000 | 3500 | 40000 | 3500 | 43500
b | 8 Channel NVR with Hard Disk |  | Nos | 0 |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
2 | Supplly, Installation, Testing & Commissioning of IP Fixed IR indoor type dome camera, 3-4 MP Camera with necessary accessories & hardwares.Make PRAMA |  | Nos | 17 | 4900 | 800 | 83300 | 13600 | 96900
[7 empty] | 0 | 0 | 0
2 | Supplly, Installation, Testing & Commissioning of IP Fixed IR Outdoor type dome camera, 3-4 MP Camera with necessary accessories & hardwares. |  | Nos | 0 |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
3 | Supplly, Installation, Testing & Commissioning of 32 Inch, LED colour monitor suitable for above camers. |  | Nos | 1 | 15000 | 1500 | 15000 | 1500 | 16500
[7 empty] | 0 | 0 | 0
4 | Supply, Installation, Testing & Commissioning of POE 24 port switch, 10/100 Base-T Access Layer 2 Switch includes 1 Gigabit combo (SFP/GT) ports and 2 uplink slots providing, With warranty pack. Also vendor to match the POE switch as per cameras requirement. |  | Nos | 1 | 21250 | 1500 | 21250 | 1500 | 22750
[7 empty] | 0 | 0 | 0
5 | Supply, Installation, Testing & Commissioning of 24 port patch panel |  | Nos | 1 | 2200 | 500 | 2200 | 500 | 2700
[7 empty] | 0 | 0 | 0
6 | Supply & Laying of CAT6 SL Series Patch cords Panel Side |  | Nos | 17 | 315 | 25 | 5355 | 425 | 5780
[7 empty] | 0 | 0 | 0
7 | Supply & Laying of CAT6 SL Series Patch cords Camera Side |  | Nos | 17 | 315 | 25 | 5355 | 425 | 5780
[7 empty] | 0 | 0 | 0
8 | Supply & Installation of adjustable Camera Pole with powder coating with 1mtr adjustable to 1.5 mtr with suitable base for fixing cameras |  | Nos | 17 | 850 | 400 | 14450 | 6800 | 21250
[7 empty] | 0 | 0 | 0
9 | Supply and Laying of 1" GI Conduits, on the wall, columns, cable trays false ceiling etc.,with GI spacers, saddles including associated civil works |  | Mtrs | 1050 | 60 | 20 | 63000 | 21000 | 84000
[7 empty] | 0 | 0 | 0
10 | Supplly and laying of cat-6 cable with shilded and braided for connection b/w the camera and NVR and b/w NVR and monitor ( Video signal cable) |  | Mtrs | 1050 | 46 | 7 | 48300 | 7350 | 55650
[7 empty] | 0 | 0 | 0
11 | Supplying, installing, testing and commissioning of Glass Break Unit / Emergency Door Release Switch for access control system, break-glass type, wall-mounted (flush / surface as specified), suitable for integration with electromagnetic lock / door controller. The unit shall be provided with resettable glass / key-reset mechanism, LED status indication, and NO/NC dry contacts for fail-safe door release during emergency conditions. |  | Nos | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
12 | Supply, installation, testing & commissioning of Dedicated CCTV Recording Server (Rack/Tower type) with minimum Intel Xeon processor, required RAM, RAID supported storage with enterprise-grade HDDs, dual LAN ports, redundant power supply (where required), complete with OS and fully compatible with CCTV VMS software |  | Nos | 1 | 165000 | 5000 | 165000 | 5000 | 170000
[7 empty] | 0 | 0 | 0
13 | Supply, installation & configuration of Licensed Video Management Software (VMS) including camera licenses, live view, recording, playback, user management, motion detection, alarm integration and analytics (if applicable), complete in all respects. |  | Nos | 1 | 25000 | 5000 | 25000 | 5000 | 30000
[7 empty] | 0 | 0 | 0
14 | Supply & installation of Operator Workstation including CPU, monitor(s), keyboard, mouse and VMS client software for live monitoring and playback |  | Nos | 1 | 65000 | 2500 | 65000 | 2500 | 67500
[7 empty] | 0 | 0 | 0
15 | Vendor to integrate the Server based CCTV system with the centralised CCTV system |  | Job | RO |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
| Sub Total for CCTV System | [5 empty] | 553210 | 69100 | 622310
| TOTAL AMOUNT - Security | [5 empty] | 1115510 | 111800 | 1227310