## ELEC-SUMM
BILL OF QUANTITIES FOR ELECTRIFICATION WORKS. -HUL ICE CREAM,13TH FLOOR
SL.NO | DESCRIPTION | Supply | Installation | Total Amount
A | WIRING SYSTEM | 0 | 0 | 0
0
B | POWER SOCKETS | 0 | 0 | 0
0
C | L.T. PANELS | 0 | 0 | 0
0
D | DISTRIBUTION BOARDS | 0 | 0 | 0
0
E | L.T. CABLES | 0 | 0 | 0
0
G | CONDUIT & RACEWAYS FOR NETWORKING & POWER SYSTEM ONLY | 0 | 0 | 0
0
H | EARTHING SYSTEM | 0 | 0 | 0
0
I | MISCELLANEOUS ITEMS | 0 | 0 | 0
| TOTAL | 0 | 0 | 0
J | LGHTING |  |  | 0

## ELEC
PROJECT : TABLE SPACE
| INTERIOR ELECTRICAL WORKS BOQ | [6 empty] | R0
SL. NO | DESCRIPTION |  |  |  |  | RATE - RS. |  | AMOUNT - RS.
|  | UNIT | Common Area | OFFICE | Qty | SUPPLY | INSTALLATION | SUPPLY | INSTALLATION | AMOUNT | ESPL Remarks
A | WIRING SYSTEM
1 | CIRCUIT MAINS
Circuit mains using 1.1kV grade PVC insulated FRLS copper conductor (MSCC) wires / PVC insulated PVC sheathed single core cables drawn in PVCS conduit or in existing raceway. Rates quoted shall include supply of conduits, wires & other conduiting accessories, MS pull / junction boxes, G.I fish wire etc. Colour coding shall be used for conduits to differentiate lighting, RP, UPS, emergency lighting circuits & point wiring. All circuit terminations shall be provided with solder less crimping type copper sockets / lugs, ferrules indicating source code on load side & load code on source side. There shall not be any joints in the circuits, only looping is allowed in terminal blocks & in switches / socket outlets.
NOTE:
1) Conduits running above false ceiling in multiples shall be supported by Slotted GI 'C' channel at distance not more than 0.5mtrs intervals.
2) Accessories shall includes Bends, Collars, junction boxes, Spacers, saddles, screws, Flexibles
3) Conduits shall be ISI marked
4) The number of wires drawn in each conduit shall be as per BIS 694 .
5) No different phases shall be drawn in same conduit
6) Conduit joints shall be done with threading proper accessories only
7) Use colour coding for each UPS & Raw power seperately
8) Black color conduit to be used / As per architect color approval
1.1 | Lighting Circuit:
| Supply & Installation of wiring using 2X2.5 + 1X1.5 sqmm PVC insulated FRLS wire drawn in 2mm thick PVC conduit as lighting circuit. The circuit main shall be measured in running metres from respective distribution board upto first switch point / light point and looping between the switches (further onwards, it shall be deemed to be included in point wiring). (cost of conduit is included) | M | 297 | 2079 | 2376 |  |  | 0 | 0 | 0 | 1.5 is updated to 2.5 for phase & neutral
[5 empty] | 0 |  |  | 0 | 0 | 0
1.2 | Emergency lighting circuit: |  |  |  | 0 |  |  | 0 | 0 | 0
| Supply & Installation of wiring using 2X2.5 + 1X1.5 sqmm PVC insulated FRLS wire drawn in 2mm thick PVC conduit as lighting circuit. The circuit main shall be measured in running metres from respective distribution board upto first switch point / light point and looping between the switches (further onwards, it shall be deemed to be included in point wiring). (cost of conduit is included) | M | 148.5 | 396 | 544.5 |  |  | 0 | 0 | 0
[5 empty] | 0 |  |  | 0 | 0 | 0
1.3 | VAV,FD & ,Convinient ,Security application Circuit : |  |  |  | 0 |  |  | 0 | 0 | 0
| Supply & Installation of wiring using 2X2.5 + 1X1.5 sqmm PVC insulated FRLS wire drawn in 2mm thick PVC conduit for third party services (cost of conduit is included) | M | 148.5 | 396 | 544.5 |  |  | 0 | 0 | 0
[5 empty] | 0 |  |  | 0 | 0 | 0
1.4 | UPS Circuit W/S |  |  |  | 0 |  |  | 0 | 0 | 0
| Supply & Installation of 3 C x 2.5 Sqmm FRLS 1100V unarmoured double insulated flexible multicore cable in white and black colour for UPS & RP circuit respectively in existing conduits/raceways. (Conduit cost is excluded) | M | 200 | 2464 | 2664 |  |  | 0 | 0 | 0
[5 empty] | 0 |  |  | 0 | 0 | 0
1.5 | RP Circuit W/S |  |  |  | 0 |  |  | 0 | 0 | 0
| Supply & Installation of 3 C x 2.5 Sqmm FRLS 1100V unarmoured double insulated flexible multicore cable in white and black colour for UPS & RP circuit respectively in existing conduits/raceways. (Conduit cost is excluded) | M | 200 | 2464 | 2664 |  |  | 0 | 0 | 0
[5 empty] | 0 |  |  | 0 | 0 | 0
1.6 | UPS Circuit - MDF & IDF room rack |  |  |  | 0 |  |  | 0 | 0 | 0
| Supply & Installation of 3 C x 4 Sqmm FRLS 1100V unarmoured double insulated flexible multicore cable in white and black colour for UPS & RP circuit respectively in existing conduits/raceways.(Conduit cost is excluded) | M |  |  | 0 |  |  | 0 | 0 | 0
[5 empty] | 0 |  |  | 0 | 0 | 0
1.7 | UPS Circuit - Server room rack |  |  |  | 0 |  |  | 0 | 0 | 0
| Supply & Installation of 3 C x 6 Sqmm FRLS 1100V unarmoured double insulated flexible multicore cable in white and black colour for UPS & RP circuit respectively in existing conduits/raceways.(Conduit cost is excluded) | M |  | 264 | 264 |  |  | 0 | 0 | 0
[5 empty] | 0 |  |  | 0 | 0 | 0
A.1 | POINT WIRING |  |  |  | 0 |  |  | 0 | 0 | 0
A.1.1 | POINT WIRING - SWITCH CONTROL |  |  |  | 0 |  |  | 0 | 0 | 0
[5 empty] | 0 |  |  | 0 | 0 | 0
| Supply, installation, Testing and Commissioning of point wiring using 3R x1.5Sqmm for Primary & for Secondary wiring FRLS 1100V wire of approved make drawn in 20mm dia PVC conduit including all conduit accessories such as bends, junction boxes etc., complete. The wiring shall be complete with ceiling roses, switches and all consumables. The wiring shall be complete with ceiling roses, switches and all consumables. The rate shall include providing mounting boxes with tapped holes for lights switches, moulded front plates with brass screws earthing of all points using third wire |  |  |  | 0 |  |  | 0 | 0 | 0
| Conduit colour to be black |  |  |  | 0 |  |  | 0 | 0 | 0
[5 empty] | 0 |  |  | 0 | 0 | 0
A.1.2 | PRIMARY LIGHT POINT | Nos. | 50 | 80 | 130 |  |  | 0 | 0 | 0 | Qty to be entered based on light fixtures
| I. Primary light point means wiring from first switch control to the first light outlet. The switch and all necessary accessories would be part of primary point. |  |  |  | 0 |  |  | 0 | 0 | 0
| II. Not to include the incoming lighting circuit from MCB-DB to switch. |  |  |  | 0 |  |  | 0 | 0 | 0
| III. But to include the sub-circuit if it is drawn from adjacent switch box. |  |  |  | 0 |  |  | 0 | 0 | 0
| III. Ceiling flexible conduit shall be included at the drop of light fixture. 3 core PVC transparent clear electrical cable flex wire/cable shall be included at the drop of suspended light fixture as required |  |  |  | 0 |  |  | 0 | 0 | 0
[5 empty] | 0 |  |  | 0 | 0 | 0
A.1.3 | SECONDARY LIGHT POINT | Nos. | 180 | 329 | 509 |  |  | 0 | 0 | 0
[8 empty] | 0 | 0 | 0
| I. Secondary light point means extention of light outlet from existing primary point. Same to be controlled by the existing switch of primary point. | [6 empty] | 0 | 0 | 0
| II. Ceiling flexible conduit shall be included at the drop of light fixture. 3 core PVC transparent clear electrical cable flex wire/cable shall be included at the drop of suspended light fixture as required | [6 empty] | 0 | 0 | 0
| Each LED strip of 5 mtr looping is considered in this line item | [6 empty] | 0 | 0 | 0
[8 empty] | 0 | 0 | 0
| TOTAL CARRIED OVER TO THE SUMMARY | [6 empty] | 0 | 0 | 0
B | POWER SOCKETS
1 | POWER RECEPTACLES
Note all power sockets to be with identification
Contractor to take sample approval for UPS/ RP Sockets for socket colors and switch plate colors from Architect/Consultant/PMC & Clients
Raw power faceplate to be Grey
Minimum Depth of outlet box to be 50mm , All Outlet boxes to be with CRCA sheet with GI plating
1.1 | Supply and installation of 6A, 3 pin, shuttered socket outlet and 6A switch and moulded plastic cover plate,including the termination of wires (WS+VAV+EXIT SIGNAGE) | No | 10 | 40 | 50 |  |  | 0 | 0 | 0
[5 empty] | 0 |  |  | 0 | 0 | 0
1.2 | Supply and installation of 6/16A, combination type shuttered socket outlet controlled by one no. 16A switch and moulded plastic cover plate,including the termination of wires.(HAT +Service+Pantry +EX.FAN+DRAIN P+GENERAL PURPOSE ) | No | 15 | 296 | 311 |  |  | 0 | 0 | 0 | Since HAT is mentioned considered all HAT .
[5 empty] | 0 |  |  | 0 | 0 | 0
1.3 | Supply and installation of 13A, multi intel type switched socket outlet controlled by one no. 16A switch and moulded plastic cover plate,including the termination of wires. | No |  |  | 0 |  |  | 0 | 0 | 0
[5 empty] | 0 |  |  | 0 | 0 | 0
1.4 | Supply and installation of 2 nos. 6/16A,combination type shuttered socket outlet controlled by one no. 16A switch + Type A + C Charger + 1 Data and moulded plastic cover plate, including the termination of wires. | No | 5 | 30 | 35 |  |  | 0 | 0 | 0 | New Item
[5 empty] | 0 |  |  | 0 | 0 | 0
1.5 | Supply and installation of 3 nos. 6/16A,combination type shuttered socket outlet controlled by one no. 16A switch + Type A + C Charger + 1 Data and moulded plastic cover plate, including the termination of wires. | No |  | 6 | 6 |  |  | 0 | 0 | 0 | New Item
[5 empty] | 0 |  |  | 0 | 0 | 0
1.5 | Supply and installation of 4 nos. 6/16A,combination type shuttered socket outlet controlled by one no. 16A switch, + Type A & C Charger + 1 Data and moulded plastic cover plate, including the termination of wires. | No |  | 232 | 232 |  |  | 0 | 0 | 0 | New Item
[5 empty] | 0 |  |  | 0 | 0 | 0
1.6 | Supply and installation of 16/20A industrial type socket in metallic enclosure with plug top D Curve – single phase 240V for hub/serverroom. WithDP MCBs (IP44) | No |  | 29 | 29 |  |  | 0 | 0 | 0
[5 empty] | 0 |  |  | 0 | 0 | 0
1.5 | Supply and installation of 25/32A industrial type socket in metallic enclosure with plug top D Curve – single phase 240V for hub/server room. WithDP MCBs (IP44) | No |  |  | 0 |  |  | 0 | 0 | 0
[5 empty] | 0 |  |  | 0 | 0 | 0
1.7 | Supply and installation of 63A, DP C Curve MCB with IP55 weather proof enclosure for Acs/fans | No | 1 | 1 | 2 |  |  | 0 | 0 | 0
[5 empty] | 0 |  |  | 0 | 0 | 0
1.8 | Supply and installation of 16/20A, TPN, C curve MCB with weather proof enclosure for fresh air fan | No | 1 | 2 | 3 |  |  | 0 | 0 | 0
[5 empty] | 0 |  |  | 0 | 0 | 0
1.9 | Supply and installation of 40A, TP RCBO(300mA) with weather proof enclosure for HVAC | No | 1 | 2 | 3 |  |  | 0 | 0 | 0
[5 empty] | 0 |  |  | 0 | 0 | 0
1.1 | Supply and installation of 63A, TP RCBO(300mA) with weather proof enclosure for HVAC | No | 1 | 2 | 3 |  |  | 0 | 0 | 0
[5 empty] | 0 |  |  | 0 | 0 | 0
1.11 | Supply and installation of 80A, TPN C Curve MCCB with weather proof enclosure | No |  | 1 | 1 |  |  | 0 | 0 | 0
0
1.12 | Supply and installation of 16/20A industrial type socket controlled by 16A DP switch | No | 5 | 5 | 10 |  |  | 0 | 0 | 0 | New Iem
0
1.14 | Supply & Installation of HDMI Port with Box | No |  | 10 | 10 |  |  | 0 | 0 | 0 | New Item
0
1.15 | 2/3 module way MS back box for socket fixing (Service pp & Pantry pp & Hvac pp) | No | 10 | 190 | 200 |  |  | 0 | 0 | 0
[5 empty] | 0 |  |  | 0 | 0 | 0
1.16 | 6 module way MS back box for socket fixing (FOR TV & Other ) | No | 2 | 38 | 40 |  |  | 0 | 0 | 0
[5 empty] | 0 |  |  | 0 | 0 | 0
1.17 | 8 module way MS back box for socket fixing | No | 2 | 38 | 40 |  |  | 0 | 0 | 0
[5 empty] | 0 |  |  | 0 | 0 | 0
1.18 | Prefabricated MS powder coated floor pop up box, MS top cover with 2 sets of 2 nos combination type 6/16A sockets with 2 nos 16A Switch in UPS power. With provision for 2 Data ports - Scope inclusive of chipping and fixing with cement plastering. | No | 5 | 5 | 10 |  |  | 0 | 0 | 0
| TOTAL CARRIED OVER TO THE SUMMARY | [6 empty] | 0 | 0 | 0
C | L.T. PANELS
Supply, installation, testing and commissioning of L.T. distribution boards suitable for 415V, 3 phase, 4 wire, 50Hz distribution system. The panel shall be free standing, floor mounting, sheet metal enclosed, flush front with aluminium busbars, separate earth bus shall be provided throughout the length of the panel. The incoming and the outgoing feeder breakers, switch fuse units, change over switches, indicating lamps, meters etc. shall be accommodated in a modular multi tier arrangement. A minimum of 400mm clearance shall be given from the floor level to the bottom most termination point. The painting shall be done in conformity with IS code. Adequate size cable alley shall be provided all round the panel and at the back for easy bending and terminations. The outgoing feeders inside the panel shall be connected through solid busbars. Flexible cable links are not acceptable. Busbars shall be provided with PVC heat shrinkable sleeves or heat resistant insulated paint. The panels shall be suitable for cable entry from top / bottom. The copper earth strip of 25mm x 3mm shall run throught out the perimeter of the bottom of the panel. The panel shall be fabricated only after the approval of fabrication drawings by the consultant.
All Panel's to be of FORM-3B type
MS stand with 2 Coats enamel painted, with primer coated Floor Stands and other accessories to mount the panel to be considered in scope and costing. Breaker and panels tobe with LOTO features.
All panel sub division doors to be with Polycarbonate Black handle
Finger Proof Power Terminals for UPS Panels (SPT Type ELMEX )
Special type Uninyvin Cables (with Braided Copper) for MCCB Power Cables.
Panels Frame shall be with 45 Degree Bending To achieve IP Protection.
MCB Viewing Window Shall be with Polycarbonte Sheet.
Panel Illumination for Cable Alley along with Door Limit Switch.
Retaining washer for BBC Doors to be provided to avoid the falling of Washers
Electrical vendor to provide a laminated SLD of suitable panels in A3 Sheets on panel
Electrical licensed electrical contractor should be mentioned in BOQ. Panels to be in compliant with state guidelines.
Note: Panel manufacturing should be as per state standards
1 | UPS INPUT PANEL | No |  |  | 0 |  |  | 0 | 0 | 0
[5 empty] | 0 |  |  | 0 | 0 | 0
2 | WORKSTATION UPS OUTPUT PANEL | No | 1 |  | 1 |  |  | 0 | 0 | 0
[5 empty] | 0 |  |  | 0 | 0 | 0
3 | FLOOR LT PANEL | No | 1 |  | 1 |  |  | 0 | 0 | 0
[5 empty] | 0 |  |  | 0 | 0 | 0
4 | SERVER RACK OUTPUT PANEL | No | 1 |  | 1 |  |  | 0 | 0 | 0
[8 empty] | 0 | 0 | 0
| TOTAL CARRIED OVER TO THE SUMMARY | [6 empty] | 0 | 0 | 0
D | DISTRIBUTION BOARDS
Supply, Installation, testing and commissioning of MCB DB- 3 Phase or Single Phase DBs, 415V/230V ,50 Hz, Factory Fabricated, assembly of MCBs at Site , DBs with copper busbars for phases, neutral and suitable earth linking. Per phase isolation kit is compulsory for 3 phase DBs.
DB Enclosure to be CRCA -1.2mm,Powder coated,IP 43 Protection, Single/Double Door, Cable entry top/bottom.
DB Board should have integrated door earthing
DB Board should have fully insulated busbar and shrouded neutral links for better protection
DB Board should have identification of bus bars
DB Board should have removal knockouts on bottom, top and side for cable insertions
ELCB for UPS application to be harmonic resistant SI/HI Series. SC rating of MCBs - 10kA.. SPN DB with DP main incomers
Electrical contractor to ensure atleast 2 Spare per phase for TPN DB are provisioned
Electrical vendor to include DB SLD in A4 Sheet with lamination
Electrical licensed electrical contractor should be mentioned in BOQ. Panels to be in compliant with state guidelines.
All UDBs with Double Neutral link
1 | Lighting DB : TPN type DB (4 tier) | No |  | 2 | 2 |  |  | 0 | 0 | 0
| LDB comprises: |  |  |  | 0 |  |  | 0 | 0 | 0
| One (1) - Incomer having |  |  |  | 0 |  |  | 0 | 0 | 0
| One (1) - 63A, 4P, MCB of 'C' Curve |  |  |  | 0 |  |  | 0 | 0 | 0
| Outgoing feeders: |  |  |  | 0 |  |  | 0 | 0 | 0
| Three (3) - Outgoing feeders having |  |  |  | 0 |  |  | 0 | 0 | 0
| One (1) - 40A, 2pole, RCCB (30mA) - Each per phase |  |  |  | 0 |  |  | 0 | 0 | 0
| Fourteen (12) - 10A, SP, 10kA, MCB per phase |  |  |  | 0 |  |  | 0 | 0 | 0
[5 empty] | 0 |  |  | 0 | 0 | 0
2 | UPSDB : TPN type DB (4 tier) | No |  | 2 | 2 |  |  | 0 | 0 | 0
| UPSDB comprises: (all MCBs suitable for computer application/D Curve)- |  |  |  | 0 |  |  | 0 | 0 | 0
| One (1) - Incomer having |  |  |  | 0 |  |  | 0 | 0 | 0
| One (1) - 63A, 4P, 10kA, MCB |  |  |  | 0 |  |  | 0 | 0 | 0
| Outgoings : |  |  |  | 0 |  |  | 0 | 0 | 0
| Three (3) - Outgoing feeders having |  |  |  | 0 |  |  | 0 | 0 | 0
| One (1) - 40A, 2pole, RCCB 300mA - Each per phase |  |  |  | 0 |  |  | 0 | 0 | 0
| Fourteen (12) - 16A, SP, 10kA, MCB per phase |  |  |  | 0 |  |  | 0 | 0 | 0
[5 empty] | 0 |  |  | 0 | 0 | 0
3 | RPDB : TPN type DB (4 tier) | No |  | 2 | 2 |  |  | 0 | 0 | 0
| One (1) - Incomer having |  |  |  | 0 |  |  | 0 | 0 | 0
| One (1) - 63A, 4P, 10kA, MCB |  |  |  | 0 |  |  | 0 | 0 | 0
| Outgoing feeders: |  |  |  | 0 |  |  | 0 | 0 | 0
| Three (3) - Outgoing feeders having |  |  |  | 0 |  |  | 0 | 0 | 0
| One (1) - 40A, 2pole, RCCB 100mA - Each per phase |  |  |  | 0 |  |  | 0 | 0 | 0
| Fourteen (12) - 16A, SP, 10kA, MCB per phase |  |  |  | 0 |  |  | 0 | 0 | 0
[5 empty] | 0 |  |  | 0 | 0 | 0
4 | SERVER DB - TPN DB | No |  | 2 | 2 |  |  | 0 | 0 | 0
| UPSDB comprises: (all MCBs suitable for computer application/D Curve)- |  |  |  | 0 |  |  | 0 | 0 | 0
| One (1) - Incomer having |  |  |  | 0 |  |  | 0 | 0 | 0
| One (1) - 63A, 4P, 10kA, MCB |  |  |  | 0 |  |  | 0 | 0 | 0
| Outgoings : |  |  |  | 0 |  |  | 0 | 0 | 0
| Three (3) - Outgoing feeders having |  |  |  | 0 |  |  | 0 | 0 | 0
| One (1) - 20A, 2pole,MCB - Each per phase |  |  |  | 0 |  |  | 0 | 0 | 0
| Four (4) - 20A, DP, 10kA, MCB per phase |  |  |  | 0 |  |  | 0 | 0 | 0
[5 empty] | 0 |  |  | 0 | 0 | 0
5 | HUB ROOM DB - SPN DB | No |  |  | 0 |  |  | 0 | 0 | 0
| ELDB DB comprises: (all MCBs 'D' Curve) |  |  |  | 0 |  |  | 0 | 0 | 0
| One (1) - Incomer having |  |  |  | 0 |  |  | 0 | 0 | 0
| One (1) -32A, DP, 10KA 'D' CURVE MCB |  |  |  | 0 |  |  | 0 | 0 | 0
| Outgoings : |  |  |  | 0 |  |  | 0 | 0 | 0
| Four (4) - 20A,DP,10KA, MCB 'D' Curve (TYP) |  |  |  | 0 |  |  | 0 | 0 | 0
[5 empty] | 0 |  |  | 0 | 0 | 0
6 | EMERGENCY LIGHTING DB - SPN TYPE DB | No | 1 | 1 | 2 |  |  | 0 | 0 | 0
| ELDB DB comprises: (all MCBs 'C' Curve) |  |  |  | 0 |  |  | 0 | 0 | 0
| One (1) - Incomer having |  |  |  | 0 |  |  | 0 | 0 | 0
| One (1) -40A, DP,RCBO, 30mA |  |  |  | 0 |  |  | 0 | 0 | 0
| Outgoings : |  |  |  | 0 |  |  | 0 | 0 | 0
| Ten (12) - 10A, SP, 10kA, MCB |  |  |  | 0 |  |  | 0 | 0 | 0
[5 empty] | 0 |  |  | 0 | 0 | 0
7 | ACDB : TPN type DB (4 tier) | No |  | 1 | 1 |  |  | 0 | 0 | 0
| One (1) - Incomer having |  |  |  | 0 |  |  | 0 | 0 | 0
| One (1) - 63A, 4P, 10kA, MCB |  |  |  | 0 |  |  | 0 | 0 | 0
| Outgoing feeders: |  |  |  | 0 |  |  | 0 | 0 | 0
| Three (3) - Outgoing feeders having |  |  |  | 0 |  |  | 0 | 0 | 0
| One (1) - 40A, 2pole, RCCB 100mA - Each per phase |  |  |  | 0 |  |  | 0 | 0 | 0
| Eight (8) - 16A, SP, 10kA, MCB per phase |  |  |  | 0 |  |  | 0 | 0 | 0
[5 empty] | 0 |  |  | 0 | 0 | 0
8 | MAIN ELDB - TPN TYPE | No |  | 1 | 1 |  |  | 0 | 0 | 0
| DB comprises: (all MCBs 'C' Curve) |  |  |  | 0 |  |  | 0 | 0 | 0
| One (1) - Incomer having |  |  |  | 0 |  |  | 0 | 0 | 0
| One (1) -40A, DP,MCB |  |  |  | 0 |  |  | 0 | 0 | 0
| Outgoings : |  |  |  | 0 |  |  | 0 | 0 | 0
| Ten (5) - 10A, DP, 10kA, MCB per phase |  |  |  | 0 |  |  | 0 | 0 | 0
[5 empty] | 0 |  |  | 0 | 0 | 0
9 | LIGHTING DB - SPN TYPE DB | No | 1 |  | 1 |  |  | 0 | 0 | 0 | new Item
| LDB DB comprises: (all MCBs 'C' Curve) |  |  |  | 0 |  |  | 0 | 0 | 0
| One (1) - Incomer having |  |  |  | 0 |  |  | 0 | 0 | 0
| One (1) -40A, DP,RCBO, 30mA |  |  |  | 0 |  |  | 0 | 0 | 0
| Outgoings : |  |  |  | 0 |  |  | 0 | 0 | 0
| Ten (12) - 10A, SP, 10kA, MCB |  |  |  | 0 |  |  | 0 | 0 | 0
0
10 | RPDB DB - SPN TYPE DB | No | 1 |  | 1 |  |  | 0 | 0 | 0 | new Item
| RPDB DB comprises: (all MCBs 'C' Curve) |  |  |  | 0 |  |  | 0 | 0 | 0
| One (1) - Incomer having |  |  |  | 0 |  |  | 0 | 0 | 0
| One (1) -40A, DP,RCBO, 100mA |  |  |  | 0 |  |  | 0 | 0 | 0
| Outgoings : |  |  |  | 0 |  |  | 0 | 0 | 0
| Ten (12) - 16A, SP, 10kA, MCB |  |  |  | 0 |  |  | 0 | 0 | 0
0
11 | UPSDB DB - SPN TYPE DB | No | 1 |  | 1 |  |  | 0 | 0 | 0 | new Item
| UPSDB DB comprises: (all MCBs 'D' Curve) |  |  |  | 0 |  |  | 0 | 0 | 0
| One (1) - Incomer having |  |  |  | 0 |  |  | 0 | 0 | 0
| One (1) -40A, DP,RCBO, 300mA |  |  |  | 0 |  |  | 0 | 0 | 0
| Outgoings : |  |  |  | 0 |  |  | 0 | 0 | 0
| Ten (12) - 16A, SP, 10kA, MCB |  |  |  | 0 |  |  | 0 | 0 | 0
| TOTAL CARRIED OVER TO THE SUMMARY | [6 empty] | 0 | 0 | 0
E | L.T. CABLES
1 | Providing, laying, testing and commissioning of 1100V grade XLPE insulated and sheathed steel wire/ tape armoured aluminium conductor cable for mains and sub mains as per specifications and drawings. The cables shall be laid in concrete trenches or buried directly underground or on cable trays. The concrete trenches will be measured separate. The cost of the cable trays or ladders, excavation and back filling of trenches will be measured separate. the unit cost of the cable shall include clamps, fasteners etc. as required for proper installation.
[8 empty] | 0 | 0 | 0
1.1 | 3.5C x 240sqmm A2XFY cable | Rm | 90 |  | 90 |  |  | 0 | 0 | 0
[5 empty] | 0 |  |  | 0 | 0 | 0
1.2 | 3.5C x 185sqmm A2XFY cable | Rm |  | RO | 0 |  |  | 0 | 0 | 0
[5 empty] | 0 |  |  | 0 | 0 | 0
1.3 | 4C x 25 sqmm A2XFY cable | Rm |  | 100 | 100 |  |  | 0 | 0 | 0
[5 empty] | 0 |  |  | 0 | 0 | 0
1.4 | 4C x 16 sqmm A2XFY cable | Rm |  | 220 | 220 |  |  | 0 | 0 | 0
[5 empty] | 0 |  |  | 0 | 0 | 0
1.5 | 4C x10 sqmm A2XFY cable | Rm | 50 |  | 50 |  |  | 0 | 0 | 0
[5 empty] | 0 |  |  | 0 | 0 | 0
1.6 | 4C x 4 sqmm A2XFY cable | Rm | 100 |  | 100 |  |  | 0 | 0 | 0
[5 empty] | 0 |  |  | 0 | 0 | 0
1.7 | 3C x2.5 sqmm A2XFY cable | Rm | 50 |  | 50 |  |  | 0 | 0 | 0
[5 empty] | 0 |  |  | 0 | 0 | 0
1.8 | 3C x 6 sqmm A2XFY cable | Rm | 49.5 |  | 49.5 |  |  | 0 | 0 | 0 | New Item - incomer for Common are DBs
[5 empty] | 0 |  |  | 0 | 0 | 0
1.9 | 4C x16 sqmm Copper Armoured Cable | Rm |  | 100 | 100 |  |  | 0 | 0 | 0
[5 empty] | 0 |  |  | 0 | 0 | 0
1.11 | 4C x10 sqmm Copper Armoured Cable | Rm |  | 50 | 50 |  |  | 0 | 0 | 0
[5 empty] | 0 |  |  | 0 | 0 | 0
1.12 | 3C X 10 sqmm Copper Armoured Cable | Rm |  | 100 | 100 |  |  | 0 | 0 | 0
[5 empty] | 0 |  |  | 0 | 0 | 0
1.13 | 3C X 6 sqmm Copper Armoured Cable | Rm | 20 | 100 | 120 |  |  | 0 | 0 | 0
[5 empty] | 0 |  |  | 0 | 0 | 0
1.14 | 1C x 4 sqmm Copper Unarmoured Cable ( YY) | Rm |  |  | 0 |  |  | 0 | 0 | 0
[5 empty] | 0 |  |  | 0 | 0 | 0
1.15 | 1C x 6 sqmm Copper Unarmoured Cable ( YY) | Rm | 253.5 |  | 253.5 |  |  | 0 | 0 | 0
[5 empty] | 0 |  |  | 0 | 0 | 0
1.16 | 1C x 10 sqmm Copper Unarmoured Cable ( YY) | Rm |  |  | 0 |  |  | 0 | 0 | 0
[5 empty] | 0 |  |  | 0 | 0 | 0
1.17 | 1C x 70sqmm Copper Unarmoured Cable ( YY) | Rm | 148.5 |  | 148.5 |  |  | 0 | 0 | 0
[5 empty] | 0 |  |  | 0 | 0 | 0
1.18 | 1C x 50sqmm Copper Unarmoured Cable ( YY) | Rm |  |  | 0 |  |  | 0 | 0 | 0
[5 empty] | 0 |  |  | 0 | 0 | 0
1.19 | 3C X 4 sqmm Cu. Flexible Cable | Rm |  | 50 | 50 |  |  | 0 | 0 | 0
[5 empty] | 0 |  |  | 0 | 0 | 0
1.2 | 3C X 6 sqmm Cu. Flexible Cable | Rm |  | 50 | 50 |  |  | 0 | 0 | 0
[5 empty] | 0 |  |  | 0 | 0 | 0
2 | Provide and install cable terminations for the above cables including single compression type chrome plated brass glands and lugs(crimping type), or PVC glands for unarmoured cable as required and with all accessories complete. Scope includes gland earthing with copper terminals around gland, Armoured cable above 70 Sqmm should have doucble compression glands |  |  |  | 0 |  |  | 0 | 0 | 0
[5 empty] | 0 |  |  | 0 | 0 | 0
1.1 | 3.5C x 240sqmm A2XFY cable | No | 4 |  | 4 |  |  | 0 | 0 | 0
0
1.2 | 3.5C x 185sqmm A2XFY cable | No |  | RO | 0 |  |  | 0 | 0 | 0
[5 empty] | 0 |  |  | 0 | 0 | 0
1.3 | 4C x 25 sqmm A2XFY cable | No |  | 4 | 4 |  |  | 0 | 0 | 0
[5 empty] | 0 |  |  | 0 | 0 | 0
1.4 | 4C x 16 sqmm A2XFY cable | No |  | 4 | 4 |  |  | 0 | 0 | 0
[5 empty] | 0 |  |  | 0 | 0 | 0
1.5 | 4C x10 sqmm A2XFY cable | No | 4 |  | 4 |  |  | 0 | 0 | 0
[5 empty] | 0 |  |  | 0 | 0 | 0
1.6 | 4C x 4 sqmm A2XFY cable | No | 4 |  | 4 |  |  | 0 | 0 | 0
[5 empty] | 0 |  |  | 0 | 0 | 0
1.7 | 3C x2.5 sqmm A2XFY cable | No | 2 |  | 2 |  |  | 0 | 0 | 0
[5 empty] | 0 |  |  | 0 | 0 | 0
1.8 | 3C x 6 sqmm A2XFY cable | Rm | 6 |  | 6 |  |  | 0 | 0 | 0 | New Item - incomer for Common are DBs
[5 empty] | 0 |  |  | 0 | 0 | 0
1.9 | 4C x16 sqmm Copper Armoured Cable | No |  | 4 | 4 |  |  | 0 | 0 | 0
[5 empty] | 0 |  |  | 0 | 0 | 0
1.11 | 4C x10 sqmm Copper Armoured Cable | No |  | 2 | 2 |  |  | 0 | 0 | 0
[5 empty] | 0 |  |  | 0 | 0 | 0
1.12 | 3C X 10 sqmm Copper Armoured Cable | No |  | 4 | 4 |  |  | 0 | 0 | 0
[5 empty] | 0 |  |  | 0 | 0 | 0
1.13 | 3C X 6 sqmm Copper Armoured Cable | No | 2 | 4 | 6 |  |  | 0 | 0 | 0
[5 empty] | 0 |  |  | 0 | 0 | 0
1.14 | 1C X 4 sqmm Copper Armoured Cable | No |  |  | 0 |  |  | 0 | 0 | 0
[5 empty] | 0 |  |  | 0 | 0 | 0
1.15 | 1C x 6 sqmm Copper Unarmoured Cable ( YY) | No | 36 |  | 36 |  |  | 0 | 0 | 0
[5 empty] | 0 |  |  | 0 | 0 | 0
1.16 | 1C x 10 sqmm Copper Unarmoured Cable ( YY) | No |  |  | 0 |  |  | 0 | 0 | 0
[5 empty] | 0 |  |  | 0 | 0 | 0
1.17 | 1C x 70sqmm Copper Unarmoured Cable ( YY) | No | 20 |  | 20 |  |  | 0 | 0 | 0
[5 empty] | 0 |  |  | 0 | 0 | 0
1.18 | 1C x 50sqmm Copper Unarmoured Cable ( YY) | No |  |  | 0 |  |  | 0 | 0 | 0
[5 empty] | 0 |  |  | 0 | 0 | 0
1.19 | 3C X 4 sqmm Cu. Flexible Cable | No |  | 4 | 4 |  |  | 0 | 0 | 0
[5 empty] | 0 |  |  | 0 | 0 | 0
1.2 | 3C X 6 sqmm Cu. Flexible Cable | No |  | 4 | 4 |  |  | 0 | 0 | 0
| TOTAL CARRIED OVER TO THE SUMMARY | [6 empty] | 0 | 0 | 0
G | CONDUIT & RACEWAYS FOR NETWORKING & POWER SYSTEM ONLY
1 | CABLE TRAYS & RACEWAYS FOR POWER /NETWORK
1.1 | Perforated type cable tray
Supply & Installation undermentioned sizes of 1.6mm,GI galvanised perforated type of following sizes, suspended from ceiling or fixed vertically on wall / column as per route directed at site, including requisite supports, hardware etc.
[5 empty] | 0 |  |  | 0 | 0 | 0
1.1.1 | 450 x 50mm Size | Mts. | 50 |  | 50 |  |  | 0 | 0 | 0
1.1.2 | 300 x 50mm Size | Mts. | 70 |  | 70 |  |  | 0 | 0 | 0
1.1.3 | 200 x 50mm Size | Mts. | 50 | 50 | 100 |  |  | 0 | 0 | 0
1.1.4 | 150 x 50mm Size | Mts. |  | 50 | 50 |  |  | 0 | 0 | 0
1.1.5 | 100 x 50mm Size | Mts. |  | 200 | 200 |  |  | 0 | 0 | 0
[5 empty] | 0 |  |  | 0 | 0 | 0
1.2 | Ladder |  |  |  | 0 |  |  | 0 | 0 | 0
| Supply & Installation undermentioned sizes of 1.6mm,GI galvanised perforated type of following sizes, suspended from ceiling or fixed vertically on wall / column as per route directed at site, including requisite supports, hardware etc. |  |  |  | 0 |  |  | 0 | 0 | 0
1.2.1 | 600 x 50mm Size | Mts. |  |  | 0 |  |  | 0 | 0 | 0
1.2.2 | 450 x 50mm Size | Mts. | 50 |  | 50 |  |  | 0 | 0 | 0
1.2.3 | 300 x 50mm Size | Mts. | 20 |  | 20 |  |  | 0 | 0 | 0
1.2.4 | 200 x 50mm Size | Mts. |  |  | 0 |  |  | 0 | 0 | 0
1.2.5 | 150 x 50mm Size | Mts. |  |  | 0 |  |  | 0 | 0 | 0
[5 empty] | 0 |  |  | 0 | 0 | 0
1.3 | Floor Raceways |  |  |  | 0 |  |  | 0 | 0 | 0
| Supply & Installation of following size GI raceway / wire way with cover, made out of 16 SWG GI for body and 14 SWG GI for cover |  |  |  | 0 |  |  | 0 | 0 | 0
[5 empty] | 0 |  |  | 0 | 0 | 0
| GI Raceway / Trunking |  |  |  | 0
1.4.1 | 550 X 38/40 X 1.2 mm size | Mtrs |  |  | 0 |  |  | 0 | 0 | 0
1.4.2 | 450 X 38/40 X 1.2 mm size | Mtrs |  | 4 | 4 |  |  | 0 | 0 | 0
1.4.3 | 350 X 338/40 X 1.2 mm size | Mtrs |  | 5 | 5 |  |  | 0 | 0 | 0
1.4.4 | 300 X 38/40 X 1.2 mm size | Mtrs |  | 5 | 5 |  |  | 0 | 0 | 0
1.3.1 | 250 X 38/40 X 1.2 mm size | Mtrs |  | 5 | 5 |  |  | 0 | 0 | 0
1.3.2 | 200 X 38/40 X 1.2 mm size | Mtrs |  | 20 | 20 |  |  | 0 | 0 | 0
1.3.3 | 150 X 38/40 X 1.2 mm size | Mtrs |  | 40 | 40 |  |  | 0 | 0 | 0
1.3.4 | 100 X 38/40 X 1.2 mm size | Mtrs | 25 | 50 | 75 |  |  | 0 | 0 | 0
1.3.5 | 80 X 38/40 X 1.2 mm size | Mtrs | 50 | 100 | 150 |  |  | 0 | 0 | 0
[5 empty] | 0 |  |  | 0 | 0 | 0
1.4 | Junction Box |  |  |  | 0 |  |  | 0 | 0 | 0
1.4.1 | 550 X 550 X 50mm Size | Nos |  |  | 0 |  |  | 0 | 0 | 0
1.4.2 | 450 X 450 X 50mm Size | Nos |  | 1 | 1 |  |  | 0 | 0 | 0
1.4.3 | 350 X 350 X 50mm Size | Nos |  | 1 | 1 |  |  | 0 | 0 | 0
1.4.4 | 300 X 300 X 50mm Size | Nos |  | 2 | 2 |  |  | 0 | 0 | 0
1.4.5 | 250 X 250 X 50mm Size | Nos |  | 2 | 2 |  |  | 0 | 0 | 0
1.4.6 | 200 X 200 X 50mm Size | Nos |  | 10 | 10 |  |  | 0 | 0 | 0
1.4.7 | 150 X 150 X 50mm Size | Nos | 7 | 38 | 45 |  |  | 0 | 0 | 0
1.4.7 | 100X 100 X 50mm Size | Nos | 10 | 80 | 90 |  |  | 0 | 0 | 0
[5 empty] | 0 |  |  | 0 | 0 | 0
1.5 | PVC Conduit |  |  |  | 0 |  |  | 0 | 0 | 0
| Supply & Laying of following size 2mm thick rigid / Flexible PVC conduits & accessories fixing in concealed wall / Ceiling / Floor. |  |  |  | 0 |  |  | 0 | 0 | 0
1.5.1 | 20 mm Rigid Conduit | Mts. | 100 | 200 | 300 |  |  | 0 | 0 | 0
1.5.2 | 25 mm Rigid Conduit | Mts. | 160 | 1971.2 | 2131.2 |  |  | 0 | 0 | 0
1.5.3 | 32 mm Rigid Conduit | Mts. | 100 | 100 | 200 |  |  | 0 | 0 | 0
0
1.6 | Ceiling raceway |  |  |  | 0
| Supply & Installation of following size GI raceway / wire way with cover, made out of 16 SWG GI for body and 14 SWG GI for coveralong with complete accenssores |  |  |  | 0
1.6.1 | 600 x 50mm | M |  |  | 0 |  |  | 0 | 0 | 0
1.6.2 | 450 x 50mm | M |  |  | 0 |  |  | 0 | 0 | 0
1.6.3 | 400 x 50mm | M |  | 5 | 5 |  |  | 0 | 0 | 0
1.6.4 | 300x 50mm | M |  | 15 | 15 |  |  | 0 | 0 | 0
1.6.5 | 200 x 50mm | M |  | 20 | 20 |  |  | 0 | 0 | 0
1.6.6 | 150 x 50mm | M |  | 25 | 25 |  |  | 0 | 0 | 0
1.6.7 | 100 x 50mm | M |  | 35 | 35 |  |  | 0 | 0 | 0
1.6.8 | 80 x 50mm | M |  | 100 | 100 |  |  | 0 | 0 | 0
1.6.9 | 500 x 200mm Size floor | M |  |  | 0 |  |  | 0 | 0 | 0
0
1.7 | Supply & Installation of following size raceway / wire way with cover, made out of 16 SWG GI/MS for body and 14 SWG GI/MS for cover.The shade shall be as per site approval |  |  |  | 0
[5 empty] | 0 |  |  | 0 | 0 | 0
1.7.4 | 100 x 100mm Size(DB Cabinet) | M |  | 20 | 20 |  |  | 0 | 0 | 0
1.7.6 | 150 x 100mm Size(HUB ROOM) | M |  | 10 | 10 |  |  | 0 | 0 | 0
[5 empty] | 0 |  |  | 0 | 0 | 0
[8 empty] | 0 | 0 | 0
| TOTAL CARRIED OVER TO THE SUMMARY | [6 empty] | 0 | 0 | 0
0
H | EARTHING SYSTEM
0
1 | Providing and laying earthing conductors of GI strip/wire including necessary accessories, clamping to walls, cables etc. as required and interconnection between lengths as per specifications and as per good installation practice. The rate shall include all supports, accessories and hardware necessary for proper installation. |  |  |  | 0
[5 empty] | 0 |  |  | 0 | 0 | 0
1.1 | 50 x 6mm G.I strip | Rm |  |  | 0 |  |  | 0 | 0 | 0
[5 empty] | 0 |  |  | 0 | 0 | 0
1.2 | 25 x 6mm G.I strip | Rm | 300 | 300 | 600 |  |  | 0 | 0 | 0
[5 empty] | 0 |  |  | 0 | 0 | 0
1.3 | 25 x 3mm G.I strip | Rm | 50 | 150 | 200 |  |  | 0 | 0 | 0
[5 empty] | 0 |  |  | 0 | 0 | 0
1.4 | 8 SWG G.I wire | Rm | 20 | 30 | 50 |  |  | 0 | 0 | 0
[5 empty] | 0 |  |  | 0 | 0 | 0
2 | Providing and laying earthing conductors of copper strip/wire including necessary accessories, clamping to walls, cables etc. as required and interconnection between lengths as per specifications and as per good installation practice. The rate shall include all supports, accessories and hardware necessary for proper installation.Quoted rate also includes termination |  |  |  | 0 |  |  | 0 | 0 | 0
[5 empty] | 0 |  |  | 0 | 0 | 0
2.1 | 1C x 4 sq.mm PVC insulated copper wire | Rm | 50 | 100 | 150 |  |  | 0 | 0 | 0
0
2.2 | 1C x 6 sq.mm PVC insulated copper wire | Rm |  |  | 0 |  |  | 0 | 0 | 0
[5 empty] | 0 |  |  | 0 | 0 | 0
2.3 | 1C x 10 sq.mm PVC insulated copper wire | Rm | 300 | 300 | 600 |  |  | 0 | 0 | 0
[5 empty] | 0 |  |  | 0 | 0 | 0
2.4 | 1C x 16 sq.mm PVC insulated copper wire | Rm | 50 | 150 | 200 |  |  | 0 | 0 | 0
[5 empty] | 0 |  |  | 0 | 0 | 0
2.5 | 1C x 25 sq.mm PVC insulated copper wire | Rm |  |  | 0 |  |  | 0 | 0 | 0
[5 empty] | 0 |  |  | 0 | 0 | 0
2.6 | 1C x 70 sq.mm PVC insulated copper wire | Rm | 50 |  | 50 |  |  | 0 | 0 | 0
[5 empty] | 0 |  |  | 0 | 0 | 0
2.7 | 1C x 50sq.mm PVC insulated copper wire | Rm |  |  | 0 |  |  | 0 | 0 | 0
[5 empty] | 0 |  |  | 0 | 0 | 0
2.8 | 1C x 185sq.mm PVC insulated copper wire | Rm |  |  | 0 |  |  | 0 | 0 | 0
[5 empty] | 0 |  |  | 0 | 0 | 0
3 | Providing and laying of heavy gauge GI conduit with all conduit accessories GI junction/pull boxes, G.I fish wire, fixing accessories etc as required for telephone , Power (UPS/Raw)and data networking complete. The rates shall include chasing of walls, floors etc & plastering the chased portion as required. |  |  |  | 0 |  |  | 0 | 0 | 0
[5 empty] | 0 |  |  | 0 | 0 | 0
3.1 | 25mm dia | Rm |  |  | 0 |  |  | 0 | 0 | 0
[5 empty] | 0 |  |  | 0 | 0 | 0
4 | Providing, installing, testing and commissioning of copper earthing station using 600x600x3mm copper plates including excavation, back filling, construction of inspection chamber, chamber with charcoal and salt, for 10 feet length GI pipe of Dia 50mm cover (C.I) with funnel set , disconnecting link with test link etc. as per specifications and in conformity with NEC. | Nos |  | RO | 0 |  |  | 0 | 0 | 0
[5 empty] | 0 |  |  | 0 | 0 | 0
5 | Providing, installing, testing and commissioning of chemical maintenance free copper bonded tripod earthing, complete with boring and suitable ancillaries and in conformity with NEC. Scope also includes back filling and installing a MS plate over earth pit. | Nos | 4 |  | 4 |  |  | 0 | 0 | 0
[5 empty] | 0 |  |  | 0 | 0 | 0
6 | Copper Earth bus bar with 25x6mm flat - 0.5mtr with necessary holes & bus bar supports with MS powder coated enclosure | Nos | 2 | 4 | 6 |  |  | 0 | 0 | 0
| TOTAL CARRIED OVER TO SUMMARY | [6 empty] | 0 | 0 | 0
0
I | MISCELLANEOUS ITEMS
1 | Providing and fixing in position the best quality danger boards of approved shape and size as specified by the local electrical authorities written in English and Local Language | No | 1 |  | 1 |  |  | 0 | 0 | 0
[5 empty] | 0 |  |  | 0 | 0 | 0
2 | Supply and fixing of approval make, 11kV grade, rubber gloves. | No | 3 |  | 3 |  |  | 0 | 0 | 0
[5 empty] | 0 |  |  | 0 | 0 | 0
3 | Providing and fixing in position approved shock treatment chart written in English and Local Language. The chart shall be framed in Teakwood and covered with glass & First aid kit. | No | 1 |  | 1 |  |  | 0 | 0 | 0
[5 empty] | 0 |  |  | 0 | 0 | 0
4 | Providing and fixing in position 1.8m x 0.9m, 2mm thick 11kV grade, rubber mat of approved make and as required by local electrical authorities | No | 10 |  | 10 |  |  | 0 | 0 | 0
[5 empty] | 0 |  |  | 0 | 0 | 0
5 | Floor cutting using concrete cutting machine and replastering using cement concrete mix approved by the architect for the required depth and dimensions as instructed by the architects / consultants. For conduiting only. | Cum | 100 |  | 100 |  |  | 0 | 0 | 0
[5 empty] | 0 |  |  | 0 | 0 | 0
6 | Temporary power for construction with necessary safety ELCbs in distribution board with neat wiring and power tapoff, lighting to be around 150 lux around work area at night and 30 power sockets. Power is provided at one point of the floor on chargable basis. | Lot | 1 |  | 1 |  |  | 0 | 0 | 0
[5 empty] | 0 |  |  | 0 | 0 | 0
7 | Charges towards getting necessary CEIG inspection done with approvals from government body for entire inetrior electrical installation with drawing submissions to get the NOC , Total amount shall be released on submission of final clearance certificate from CEIG as per Local norms. | Lot | 1 |  | 1 |  |  | 0 | 0 | 0
[5 empty] | 0 |  |  | 0 | 0 | 0
8 | MS square pipe (25mmx25mmx3mm thick) works with a coat of primer and 2 coats of enamel for supporting trays and raceways & lights | Kgs | 100 |  | 100 |  |  | 0 | 0 | 0
[5 empty] | 0 |  |  | 0 | 0 | 0
9 | Supply, installation, testing and commissioning of wireless scene selector keypad with all the necessary unit (PSU, CU, etc) along with the remote for controlling the luminaires (4 loops - upto 8 light fixtures per loop) including DALI wiring. 10PAX meeting Room | Nos |  |  | 0 |  |  | 0 | 0 | 0
[5 empty] | 0 |  |  | 0 | 0 | 0
10 | SITC of 7.5KVA INV, 230 /VOLTS , 1 phase, 3 Wire , maintained type emergency lighting inverter unit comprising of : ) automatic battery charger. 90min backup battery bank (sealed lead acid type ) controls, overload & short circuit protective gear, internal wiring etc.,16 SWG PVC enclosure to house all the components.-Complete Set | Nos |  |  | 0 |  |  | 0 | 0 | 0
[5 empty] | 0 |  |  | 0 | 0 | 0
11 | Painting of exposed GI perforated ceiling raceway with one coat of primer and 2 coats of enamel in hand roller , color and shade subject to consultant & architect approval | Sqm | 1 |  | 1 |  |  | 0 | 0 | 0
[5 empty] | 0 |  |  | 0 | 0 | 0
12 | EB meter as per Power norms in the name of client to be added in existing builder main panel where the builder has provided MCCB breaker (CT WITH METER AS PER EB NORMS). Liasioning charges to get the metering connection to be considered | Lot |  |  | 0 |  |  | 0 | 0 | 0
[8 empty] | 0 | 0 | 0
| TOTAL CARRIED OVER TO SUMMARY | [6 empty] | 0 | 0 | 0
[8 empty] | 0 | 0 | 0

## UPS BOQ
Project | : TABLE SPACE
Consultants | : E Sollutions Consultancy Pvt Ltd
Subject | : UPS BOQ
Date | : 30.04.2026
Sl. No | Descirption | Unit | Total Qty | Unit Rate
|  |  |  | Supply | Installation
A | UPS & BATTERY RELATED WORKS
I | EQUIPMENT | [5 empty] | 0
A | UPS
1 | Design, manufacture, assembly, supply, installation, testing, delivery and commissioning of 100-kVA Frame size Modular UPS with 25 kVA X 3 modules in each frame with hot swapable Continuous rating, online, double conversion operating modular type 3 ph input and 3 ph output Modular UPS system with IGBT rectifier as per technical specifications. The UPS Module Cabinet shall consist of a Breaker & breaker cabinet, rectifier / charger, a three-phase inverter, static transfer switch, Maintenance Bi-pass Switch, logic, synchronizing equipment, protective devices and accessories as required for proper operation.The Modular system is selected in N+1 configuration. Routine tests needs to be done at factory & test reports need to be submitted. - The UPS System to be provided with Dual Input Card for both Modus Monitoring in BMS system and IP Monitoring over Network parallely including Parallel working configuration required accessories. | No | 1 |  |  | 0
0
2 | Supply, Installation, Testing and commissiong of required Ah of Valve regulated lead–acid (VRLA) Batteries of approved make suitable for 3x25 kVA sets @0.9PF to give minimum 15 minutes backup. The rate shall include bankwise battery monitoring system. Battery monitoring PC should be located in BMS room. | Set | 1 |  |  | 0
|  |  |  | 0 | 0 | 0
3 | CABLING SYSTEM |  |  | 0 | 0 | 0
|  |  |  | 0 | 0 | 0
3.1 | Supply, installation, testing and commissioning of 1100V grade multistrand, copper conductor, Uni Nyvin, unarmoured flexible cable of requisite size for interconnection between battery, battery breakers and the respective 3x25 kVA UPS Units. The cable shall conform to IS-694 | LS | 1 |  |  | 0
|  |  |  | 0 | 0 | 0
3.2 | Supply, installation and commissioning of 1100V grade multistrand, copper conductor, Uni Nyvin, unarmoured flexible cable termination with Single compression cable gland, Ring type copper lugs and necessary steel bolts for interconnection between battery, battery breakers and the respective 3x25 kVA UPS Units. | LS | 1 |  |  | 0
|  |  |  | 0 | 0 | 0
3.3 | Supply, installation and commissioning of 1100V grade multistrand, copper conductor, FRLS insulated, 4C x 1.5 Sq.mm unarmoured flexible cable & termination with Single compression cable gland, Ring type copper lugs and necessary steel bolts for interconnection between UPS & Battery breaker. | LS | 1 |  |  | 0
|  |  |  | 0 | 0 | 0
4 | MS SUPPORTING STRUCTURES |  |  | 0 | 0 | 0
|  |  |  | 0 | 0 | 0
4.1 | Supply & installation of fabricated MS frame approximately 600mm height suitable for 3x25 KVA UPS. MS Supports should be factory fabricated with Anticorrosive powder coating. The design of stool shall ensure uniform distribution of weight less than 400kg/Sq.m | No | 1 |  |  | 0
|  |  |  | 0 | 0 | 0
4.2 | Supply & installation of fabricated MS frame approximately 600mm height suitable for 3x25 KVA UPS Battery Bank. MS Supports should be factory fabricated with Anticorrosive powder coating. The design of stool shall ensure uniform distribution of weight less than 400kg/Sq.m | No | 1 |  |  | 0
|  |  |  | 0 | 0 | 0
5 | REMOTE ALARM PANEL |  |  | 0 | 0 | 0
|  |  |  | 0 | 0 | 0
5.1 | Supply, installation, testing and commissioning of Remote Alarm Panel with buzzer and display for 1 Nos 3x25 kVA UPS unit as required with interconnecting signal cables drawn in MS conduit and flexible MS conduits, fixing of conduit with necessary accessories, supports etc. Complete as per technical specification. The quoted rate shall be inclusive of metal conduits, flexible metal conduits and necessary fixing accessories, supports etc. Remote Alarm Panel with hooter and cable till BMS room need to be considered for monitoring of UPS units. | No | 1 |  |  | 0
|  |  |  | 0 | 0 | 0
6 | LOAD TESTING |  |  | 0 | 0 | 0
|  |  |  | 0 | 0 | 0
6.1 | Site testing of 3x25 kVA online, double conversion UPS systems including load testing with all necessary cables, Load bank of resistive Load @ site for testing etc. complete for UPS System | LS | 1 |  |  | 0
| TOTAL - UPS - WORK STATION |  |  |  |  | 0
B | Conventional UPS - Emegency Lighting
1 | Design, manufacture, assembly, supply, installation, testing, delivery and commissioning of 6 kVA Conventional UPS Continuous rating, online, double conversion operating modular type 1 ph input and 1 ph output UPS system with IGBT rectifier as per technical specifications. The UPS Cabinet shall consist of a Breaker & breaker cabinet, rectifier / charger, a three-phase inverter, static transfer switch, Maintenance Bi-pass Switch, logic, synchronizing equipment, protective devices and accessories as required for proper operation.The UPS system is selected in N configuration. Routine tests needs to be done at factory & test reports need to be submitted. - The UPS System to be provided with Dual Input Card for both Modus Monitoring in BMS system and IP Monitoring over Network parallely including Parallel working configuration required accessories. | No | 1 |  |  | 0
|  |  |  | 0 | 0 | 0
2 | Supply, Installation, Testing and commissiong of required Ah of Valve regulated lead–acid (VRLA) Batteries of approved make suitable for 6 kVA sets to give minimum 90 minutes backup. The rate shall include bankwise battery monitoring system. Power factor 0.93 to be considered for battery sizing. | Set | 1 |  |  | 0
|  |  |  | 0 | 0 | 0
3 | CABLING SYSTEM |  |  | 0 | 0 | 0
|  |  |  | 0 | 0 | 0
3.1 | Supply, installation, testing and commissioning of 1100V grade multistrand, copper conductor, Uni Nyvin, unarmoured flexible cable of requisite size for interconnection between battery, battery breakers and the respective 6 kVA UPS Units for Above given configuration. The cable shall conform to IS-694. | LS | 1 |  |  | 0
|  |  |  | 0 | 0 | 0
3.2 | Supply, installation and commissioning of 1100V grade multistrand, copper conductor, Uni Nyvin, unarmoured flexible cable termination with Single compression cable gland, Ring type copper lugs and necessary steel bolts for interconnection between battery, battery breakers and the respective 7.5 kVA UPS Units. For Above given configuration | LS | 1 |  |  | 0
|  |  |  | 0 | 0 | 0
3.3 | Supply, installation and commissioning of 1100V grade multistrand, copper conductor, FRLS insulated, 4C x 1.7.5 Sq.mm unarmoured flexible cable & termination with Single compression cable gland, Ring type copper lugs and necessary steel bolts for interconnection between UPS & Battery breaker. For Above given configuration (7.5 kVA UPS) | LS | 1 |  |  | 0
|  |  |  | 0 | 0 | 0
4 | MS SUPPORTING STRUCTURES |  |  | 0 | 0 | 0
|  |  |  | 0 | 0 | 0
| MS frame to be factory made, powder coated with approved colour and to have anti corrosive coating |  |  | 0 | 0 | 0
|  |  |  | 0 | 0 | 0
4.1 | Supply & installation of fabricated MS frame approximately 600mm height suitable for 6 KVA UPS. MS Supports should be factory fabricated with Anticorrosive powder coating. The design of stool shall ensure uniform distribution of weight less than 400kg/Sq.m | No | 1 |  |  | 0 | 8.75
|  |  |  | 0 | 0 | 0
4.2 | Supply & installation of fabricated MS frame approximately 600mm height suitable for 6 KVA UPS Battery Bank. MS Supports should be factory fabricated with Anticorrosive powder coating. The design of stool shall ensure uniform distribution of weight less than 400kg/Sq.m | No | 1 |  |  | 0
|  |  |  | 0 | 0 | 0
5 | REMOTE ALARM PANEL |  |  | 0 | 0 | 0
|  |  |  | 0 | 0 | 0
5.1 | Supply, installation, testing and commissioning of Remote Alarm Panel with buzzer and display for 6KVA UPS unit as required with interconnecting signal cables drawn in MS conduit and flexible MS conduits, fixing of conduit with necessary accessories, supports etc. Complete as per technical specification. The quoted rate shall be inclusive of metal conduits, flexible metal conduits and necessary fixing accessories, supports etc. Remote Alarm Panel with hooter and cable till BMS room need to be considered for monitoring of UPS units. | No | 1 |  |  | 0
|  |  |  | 0 | 0 | 0
6 | LOAD TESTING |  |  | 0 | 0 | 0
|  |  |  | 0 | 0 | 0
7.1 | Site testing of 6 kVA online, double conversion UPS systems including load testing with all necessary cables, Load bank of resistive Load @ site for testing etc. complete for UPS System | No | 1 |  |  | 0
| TOTAL - Conventional UPS -Emergency lighting loads |  |  |  |  | 0
C | Conventional UPS - Server loads
1 | Design, manufacture, assembly, supply, installation, testing, delivery and commissioning of 10 kVA Conventional UPS Continuous rating, online, double conversion operating modular type 3 ph input and 3 ph output UPS system with IGBT rectifier as per technical specifications. The UPS Cabinet shall consist of a Breaker & breaker cabinet, rectifier / charger, a three-phase inverter, static transfer switch, Maintenance Bi-pass Switch, logic, synchronizing equipment, protective devices and accessories as required for proper operation.The UPS system is selected in N configuration. Routine tests needs to be done at factory & test reports need to be submitted. - The UPS System to be provided with Dual Input Card for both Modus Monitoring in BMS system and IP Monitoring over Network parallely including Parallel working configuration required accessories. | No | 1 |  |  | 0
|  |  |  | 0 | 0 | 0
2 | Supply, Installation, Testing and commissiong of required Ah of Valve regulated lead–acid (VRLA) Batteries of approved make suitable for 10 kVA sets to give minimum 15 minutes backup. The rate shall include bankwise battery monitoring system. Power factor 0.93 to be considered for battery sizing. | Set | 1 |  |  | 0
|  |  |  | 0 | 0 | 0
3 | CABLING SYSTEM |  |  | 0 | 0 | 0
|  |  |  | 0 | 0 | 0
3.1 | Supply, installation, testing and commissioning of 1100V grade multistrand, copper conductor, Uni Nyvin, unarmoured flexible cable of requisite size for interconnection between battery, battery breakers and the respective 10 kVA UPS Units for Above given configuration. The cable shall conform to IS-694. | LS | 1 |  |  | 0
|  |  |  | 0 | 0 | 0
3.2 | Supply, installation and commissioning of 1100V grade multistrand, copper conductor, Uni Nyvin, unarmoured flexible cable termination with Single compression cable gland, Ring type copper lugs and necessary steel bolts for interconnection between battery, battery breakers and the respective 10 kVA UPS Units. For Above given configuration | LS | 1 |  |  | 0
|  |  |  | 0 | 0 | 0
3.3 | Supply, installation and commissioning of 1100V grade multistrand, copper conductor, FRLS insulated, 4C x 1.5 Sq.mm unarmoured flexible cable & termination with Single compression cable gland, Ring type copper lugs and necessary steel bolts for interconnection between UPS & Battery breaker. For Above given configuration (10 kVA UPS) | LS | 1 |  |  | 0
|  |  |  | 0 | 0 | 0
4 | MS SUPPORTING STRUCTURES |  |  | 0 | 0 | 0
|  |  |  | 0 | 0 | 0
| MS frame to be factory made, powder coated with approved colour and to have anti corrosive coating |  |  | 0 | 0 | 0
|  |  |  | 0 | 0 | 0
4.1 | Supply & installation of fabricated MS frame approximately 600mm height suitable for 10 KVA UPS. The design of stool shall ensure uniform distribution of weight less than 400kg/Sq.m | No | 1 |  |  | 0
|  |  |  | 0 | 0 | 0
4.2 | Supply & installation of fabricated MS frame approximately 600mm height suitable for 10 KVA UPS Battery Bank. The design of stool shall ensure uniform distribution of weight less than 400kg/Sq.m | No | 1 |  |  | 0
|  |  |  | 0 | 0 | 0
5 | REMOTE ALARM PANEL |  |  | 0 | 0 | 0
|  |  |  | 0 | 0 | 0
5.1 | Supply, installation, testing and commissioning of Remote Alarm Panel with buzzer and display for 10 KVA UPS unit as required with interconnecting signal cables drawn in MS conduit and flexible MS conduits, fixing of conduit with necessary accessories, supports etc. Complete as per technical specification. The quoted rate shall be inclusive of metal conduits, flexible metal conduits and necessary fixing accessories, supports etc. Remote Alarm Panel with hooter and cable till BMS room need to be considered for monitoring of UPS units. | No | 1 |  |  | 0
|  |  |  | 0 | 0 | 0
6 | LOAD TESTING |  |  | 0 | 0 | 0
|  |  |  | 0 | 0 | 0
6.1 | Site testing of 10 kVA online, double conversion UPS systems including load testing with all necessary cables, Load bank of resistive Load @ site for testing etc. complete for UPS System | No | 1 |  |  | 0
| TOTAL - Conventional UPS - Server / Hub room loads |  |  |  |  | 0
| Sub Total - 1 (Work station UPS) |  |  |  |  | 0
| Sub Total - 2 (Emergency UPS) |  |  |  |  | 0
| Sub Total - 3 (Server / Hub room UPS) |  |  |  |  | 0
| GRAND TOTAL |  |  |  |  | 0 | 0