## Summary
SNO | DESCRIPTION | TOTAL
1 | HVAC LOW SIDE | 1818545.2
2 | CSU UNIT | 980800
| TOTAL | 2799345.2
GST EXTRA

## low side
Project Name : ALORICA
Location Address : 10F @ ALORICA-BHARTIYA CITY
Subject: HVAC Low side Works
SL No. | DESCRIPTION | UOM | QTY | sup rate | inst rate | TOTAL
`
1 | AIR DISTRIBUTION
1.1 | Supply, fabrication, installation and testing of factory fabricated GSS ducts (120 GSM ) with flanges in accordance with the approved shop drawings and as per specifications.
Note: The entire ducts should be fabricated at factory and delivered to site in assembled condition. The contractors should include the transportation charges and necessary handling charges. The contractor should use only Hitec supports and full threaded rods to support the ducts as per the specification. After erection of the duct the entire duct should be tested for Duct leakage pressure test. The contractor should arrange the pressure test machine and the costing for the same to be included in the ducting price.
a) | 24 gauge galvanized sheet steel (0.63mm) (0-750mm) | Sqm | 40 | 880 | 240 | 44800
b) | 22 gauge galvanized sheet steel (0.80mm) (751-1200mm) | Sqm | 30 | 970 | 240 | 36300
c) | 20 gauge galvanized sheet steel (1.00mm)(1201-1800mm) | Sqm | 30 | 1060 | 240 | 39000
d) | 18 gauge galvanized sheet steel (1.25mm)(1801-above) | Sqm |  |  |  | 0
0
0
2 | Factory made Eliptical ducting with Hitech rope rope GSS Ducting (120 GSM).The duct should be internally insulated with 9mm thick nitrile rubber(costed seperatly). The ducts to be factory fabricated & two coats of spray paint (Interior scope)at site level as per the Architects colour specifications., Necessary bends should be made as per the drawing, two support & connecting rings should be considered for the same.After erection of the duct the entire duct should be tested for Duct leakage light test . The contractor should arrange the Smoke/light test machine and the costing for the same to be included in the ducting price. Costing should also include black /transparent rubber tube for entire rope & rope to be painted as per the Architects colour specifications. |  |  |  |  | 0
| Please note that all elliptical duct should be delivered to the site with zinc cromate primer & required H frames for the elliptical duct connections, cost should be included in the same ducting cost. |  |  |  |  | 0
| Noted : Duct internal insulated should be done @ duct factory. Insulation at site level is not acceptable. |  |  |  |  | 0
a) | 24 gauge galvanized sheet steel (0.63mm) (0"-24") | Sqm | 89 | 1395 | 280 | 149075
b) | 22 gauge galvanized sheet steel (0.8mm) (25"-48") | Sqm | 190 | 1505 | 280 | 339150
c) | 20 gauge galvanized sheet steel (1.0 mm) (49"-60") | Sqm | 45 | 1625 | 280 | 85725
d) | 20 gauge galvanized sheet steel (1.0 mm) (67"-70") | Sqm |  |  |  | 0
0
2.1 | Open Sprial Round ducting system- (Supply and installation of Factory fabricated GI sheet metal duct ( costing should include two coats of spray paint at site level as per the Architects colour specifications) ,gripple support,adjustable volume control split dampers,guide vanes with necessary flexible connections).A sample of same should be sumbitted for approval before proceeding. Costing should also include black /transparent rubber tube for entire rope & rope to be painted as per the Architects colour specifications. |  |  |  |  | 0
a) | 24 G (200Ø) | Rmt |  |  |  | 0
0
2.2 | Supply /Modification of Factory fabricated, powder coated plenum with Double skin AHU construction of 45mm thick PUF insulation. Appropriate cutout to be made to connecte the branch ducts with dampers as per approved drawing. 0.8 thick inner & 0.8 thick outer skin. The price quoted shall include MS supporting arrangement for suspending the plenum from the ceiling slab | Sqm | 40 | 3335 | 375 | 148400
0
2.3 | Supply, fabrication, installation and testing of the flexible connections constructed out of fire resistant double canvas sleeve as per the approved shop drawings.It should be factory fabricated. | rmt | 4 | 1800 | 800 | 10400
0
2.4 | Supply, installation and testing of GSS construction of 16G opposed blade volume control dampers within ducts to be provided with suitable links, levers and quadrants for manual control of volume of air flow.The end flanges should be of TDF. | Sqm | 2 | 6525 | 1350 | 15750
0
3 | Supply, installation and testing of GSS construction of opposed blade volume control dampers with in elliptical & spiral ducts to be provided with suitable links, levers and quadrants for manual control of volume of air flow. Note: Elliptical VCD gague should be one gauge higher than duct. | Sqm | 8 | 10005 | 1350 | 90840
0
3.01 | Supply, installation, testing & commissioning of multi blade, motorised fire & smoke dampers with spring return actuator. The damper shall be of atleast 120mins. fire rating with 450 mm duct sleeve it should be with TDF Flanges. The damper shall be as per UL Listed & CBRI Approved. The damper shall be constructed out of 16G galvanised sheet steel. It shall be complete with control panel, actuator, sensor and inter-locking / wiring / connection for tripping of AHU fan motor. (for AHU rooms / UPS rooms / battery room / electrical rooms). all actuotors should have potential free contact to know the status of the actuator through the BMS. 10 / 15 Nm Torque should be considred. |  |  |  |  | 0
| Note: Each Fire Damper Control Panel (Electronic Type) should control upto 10 Motorised Dampers with the following features. a) Control Panel should trip upon the input from Temperature Sensor @ 72 deg C (to be provided with the panel), Smoke Detector, External Fire panel / BMS with Auto Reset option, AHU door opening. b) Interlocking of AHU’s with timer for Reset and 2 additional equipment’s (Hooters, Electrical Panels). c) Control panel should show the status (Open / close) of individual fire damper. d) Each damper is considered with single Actuator only. The damper Torque to be selected accordingly. |  |  |  |  | 0
a) | Fire dampers | Sqm | 3 | 12500 | 1000 | 40500
b) | Actuators | Nos. | 6 | 9570 | 1500 | 66420
c) | Control Panel . ( control 4 Motorised Dampers) | Nos. | 1 | 16800 | 1500 | 18300
e) | Small Control Panel(for Hub Room ). ( control upto 2 Motorised Dampers) | Nos. |  |  |  | 0
f) | Small Control Panel(for Battery Room). ( control upto 1 Motorised Dampers) | Nos. |  |  |  | 0
0
3.02 | Supply,installation,testing and balancing of square type extruded aluminium powder coated diffusers for supply air required as per the approved shop drawings. Diffuser shall be with spring loaded removable core type distribution grid (tegular type) |  |  |  |  | 0
| Extruded Aluminium diffusers powder coated: |  |  |  |  | 0
a) | 450x450 (Neck size) overall size 596x596 | Nos. |  |  |  | 0
b) | 375x375 (Neck size) overall size 596x596 | Nos. |  |  |  | 0
c) | Round diffusers(380dia)300 neck with OBD | Nos. |  |  |  | 0
d) | Round diffusers(330dia)250 neck with OBD | Nos. |  |  |  | 0
0
3.03 | Supply,installation,testing and balancing of square type extruded aluminium powder coated diffusers for Return air required as per the approved shop drawings. Diffuser shall be with spring loaded removable core type distribution grid . (Plate type) |  |  |  |  | 0
| Extruded Aluminium diffusers powder coated : |  |  |  |  | 0
a) | 450x450 (Neck size) overall size 596x596 | Nos. |  |  |  | 0
b) | 375x375 (Neck size) overall size 596x596 | Nos. |  |  |  | 0
c) | Round diffusers regular type(380dia) | Nos. |  |  |  | 0
0
3.04 | Supply,installation,testing & balancing of continuous linear fixed bar extruded aluminium powder coated return air grilles normal flow 45° / 15°/0° one way/two way deflection with all sides flanged without dampers. Colour of the same need to be as per the Architects colour specification. |  |  |  |  | 0
a) | 100mm high | RM |  |  |  | 0
b) | 200mm high | RM |  |  |  | 0
c) | 250mm high | RM |  |  |  | 0
d) | 500mm high @ 45 Degree Deflection | RM |  |  |  | 0
e) | linear Grille(various sizes as per drawing) | sqmt | 5 | 5000 | 500 | 27500
f) | 600x600 mm grille ( with collar damper) | Nos |  |  |  | 0
g) | 600x600 mm grille | Nos |  |  |  | 0
h) | 750x150 mm Curved grille | Nos | 45 | 1300 | 150 | 65250
i) | 450x450 Grille for Z type & L type speech privacy duct | Nos |  |  |  | 0
j) | 250x250 Grille for Z type & L type speech privacy duct | Nos |  |  |  | 0
K | 750x100 mm grille with Collar damper | Nos |  |  |  | 0
L | Light test of thewntire duct after completed of connection main duct before cutting the duct for curve grill fixing. | Nos | 1 |  | 3500 | 3500
0
3.05 | Supply & installation of Aluminium.Collar damper | Sqm | 7 | 5000 | 500 | 38500
0
3.06 | Supply & installation of 150 mm dia flexible duct with fire retardent Al.foil sheet.Metailzed polyester is not acceptable. Note: Universal clamp should be provided to fix the flexible duct in the spigots and covered with tape. If the flexible duct length is beyond 1000 mm, then cirucar clip with chain to be provided to support the flexible duct. Flexible duct insulation to be with duct tape. 3M Aluminium Duct tape costing also to be considered for flexible to butterfly damper & plenum fixing. | RM | 20 | 350 | 100 | 9000
0
3.07 | Supply & installation of 300 mm dia flexible duct with fire retardent Al.foil sheet.Metailzed polyester is not acceptable. Note: Universal clamp should be provided to fix the flexible duct in the spigots and covered with tape. If the flexible duct length is beyond 1000 mm, then cirucar clip with chain to be provided to support the flexible duct. Duct tape costing also to be considered for flexible to butterfly damper & plenum fixing. | RM |  |  |  | 0
0
3.08 | Supply & installation of 150 mm dia Spigot & Butterfly damper. It should be of 20G. | Nos. | 12 | 700 | 150 | 10200
0
3.09 | Supply & installation of 150mm disc valve damper. It should be of 20G. | Nos. | 12 | 650 | 100 | 9000
0
3.1 | Supply & installation of factory fabricated mixing Chamber of 600 X 600 X 400 size . Note: The mixing Box to be properly supported with chain and should be erected as per our drawing.it has to be fabricated at factory and delivered to site and Mixing Box gauge should be 24 G. Mixing Box should have two inlet for connecting 2 Nos of Flexible duct. | Nos. | 1 | 844.8 | 230.4 | 1075.2
0
3.11 | Supply & installation of factory fabricated mixing Chamber of500 X 500 X 400 size for Diffuser neck size 450x450. Note: The mixing Box to be properly supported with chain and should be erected as per our drawing.it has to be fabricated at factory and delivered to site Mixing Box gauge should be 24 G. | Nos. |  |  |  | 0
0
3.12 | Supply & installation of factory fabricated mixing Chamber of 450 X 450 X 400 size for Diffuser neck size 375x375. Note: The mixing Box to be properly supported with chain and should be erected as per our drawing.it has to be fabricated at factory and delivered to site Mixing Box gauge should be 24 G. | Nos. |  |  |  | 0
0
3.13 | Supply & installation of factory fabricated mixing Chamber of 450 X 450 X 400 size for Diffuser neck size DIA 300. Note: The mixing Box to be properly supported with chain and should be erected as per our drawing.it has to be fabricated at factory and delivered to site Mixing Box gauge should be 24 G. | Nos. |  |  |  | 0
0
3.14 | Supply & installation of factory fabricated mixing Chamber of 950 X 150 X 400 size . Note: The mixing Box to be properley supported with chain and should be erected as per our drawing.it has to be fabricated at factory and delivered to site Mixing Box gauge should be 24 G. | Nos. |  |  |  | 0
0
3.15 | Supply & installation of factory fabricated mixing Chamber of 1050 X 200 X 400 size . Note: The mixing Box to be properley supported with chain and should be erected as per our drawing.it has to be fabricated at factory and delivered to site Mixing Box gauge should be 24 G. | Nos. |  |  |  | 0
0
3.16 | Supply & installation of factory fabricated mixing Chamber of 1250 X 150 X 400 size . Note: The mixing Box to be properley supported with chain and should be erected as per our drawing.it has to be fabricated at factory and delivered to site Mixing Box gauge should be 24 G. | Nos. |  |  |  | 0
0
3.17 | Supply & installation of factory fabricated mixing Chamber of 800 X 150 X 400 size . Note: The mixing Box to be properley supported with chain and should be erected as per our drawing.it has to be fabricated at factory and delivered to site Mixing Box gauge should be 24 G. | Nos. |  |  |  | 0
0
3.18 | 300Dia Dropper of length 150mm for round diffuser connection . Its should of 24G and Match Elliptical duct color. | Nos. |  |  |  | 0
0
3.19 | Motorized Damper |  |  |  |  | 0
| Supply, installation and testing of GSS construction of 16G opposed Aerofoil blade volume control dampers within ducts to be provided with suitable links, levers and quadrants for manual control of volume of air flow.The end flanges should be of TDF. 10 / 15 Nm Torque should be considered. |  |  |  |  | 0
a) | Dampers | Sqm |  |  |  | 0
b) | Actuator | Nos |  |  |  | 0
0
3.2 | Supply and installation of Z section speech privacy duct (as per drawing) with 15 mm thk acoustic open cell nitrail rubber.Size : 450X250X1900 (L). Z section gauge should be 24 G. |  |  |  |  | 0
a) | Z Piece Size : 450X450X1900 (L). | Nos |  |  |  | 0
b) | Z Piece Size : 250X250X1900 (L). | Nos |  |  |  | 0
0
3.21 | Supply, installation, testing & commissioning of slot diffuser. The slot diffuser should be of vertical discharge type. |  |  |  |  | 0
a) | 150 mm wide 3 slot. | RM |  |  |  | 0
a) | Hit & Miss damper ( for 3 slot) | RM |  |  |  | 0
0
3.22 | Air balancing for the entire office space. The vendor need to arrange the third party agency & submit the report for consultant's approval. Air balancing needs to be done pre & post Occupancy. | Lot | 1 |  | 18000 | 18000
| NOTE- The Air balancing need to be done with calibrated digitl flow meter & hood |  |  |  |  | 0
0
3.23 | Associated civil works such as wall opening to take the duct & chw. pipes and closing of the same in proper manner. After erection of the S/A & R/A duct, the balance gaps need to sealed by using brick & morter in all the AHU Room. The AC vendor is responsible for the same. C angle to be considered to close the wall opening above the fire dampers. Required fire sealent also need to be quantified as part of wall Closed. Please study the Tender layout & visit site before quoting. | Lot |  |  |  | 0
0
3.24 | Supply & installation of 300 mm dia round duct. It should be of 24G. | Rmts |  |  |  | 0
0
3.25 | Supply & installation of 250 mm dia round duct. It should be of 24G. | Rmts |  |  |  | 0
0
3.26 | Supply & installation of Disc valves 150 dia | Nos |  |  |  | 0
0
3.27 | Supply & installation of 150dia AL. rigid flexible duct | Rmts |  |  |  | 0
0
3.28 | Supply & installation of 150 dia butterfly damper | Nos |  |  |  | 0
0
3.29 | Supply & installation of 100dia AL. rigid flexible duct | Rmts |  |  |  | 0
0
3.3 | Supply & installation of Fusible link fire dampers | Sqm |  |  |  | 0
0
| FRESH AIR FAN |  |  |  |  | 0
4 | Supply & installation of 600 CFM Duct Inline/ Cabinet type fan with pre filter ( Merv-8) section of the following capacity & static pressure. The noise level of the fan should be less than 45dBA just beneath the fan. | Nos |  |  |  | 0
0
| EXHAUST AIR FANS |  |  |  |  | 0
5 | Supply & installation of Low noise Cabinet type exhaust fan along with 2 speed regulator of the following capacity & static pressure. The noise level of the fan should be less than 45dBA just beneath the fan. |  |  |  |  | 0
a) | 1500 CFM @30mm static ( without 2 speed regulator) | Nos | 1 | 28000 | 2500 | 30500
0
| Battery room exhaust fans |  |  |  |  | 0
6 | Supply & installation of 200 CFM Duct Inline fan with H2 sensor , timer & hooter with 30 mm static pressure, requried panel & electrical works to be included in the same line item. Should generate an alarm if the H2 LEVEL in the room temperature goes beyond the set point . | Nos |  |  |  | 0
0
6.01 | 24 Gauge Mesh for the exhaust duct cowl. | sqmt |  |  |  | 0
0
6.02 | Non return damper ( Al) | sqmt |  |  |  | 0
0
6.03 | supply & installaton of thermo well to provide Immersion type temperature sensor to monitor the chilled water temperature for supply Line. Vendor should consider removing water & filling water along with water balancing post installation of thermowell along with the required insulation & cladding costing while quoting. Vendor should visit the site before quoting for the line item. | Nos |  |  |  | 0
0
6.04 | Supply & installation of Extruded aluminium powder coated exhaust air louver with bird screen and 30 mm flange width. The total structure is to be weather proof and blades are to be inclined downwards. | sqmt |  |  |  | 0
0
7 | Supply & Installation of Sound Attenuators for Return air Duct |  |  |  |  | 0
| Air Duct leaving AHU Rooms (Used for Supply air duct & Cross Talk Attenuator) |  |  |  |  | 0
| COMPUTER SELECTION SHOULD BE ATTACHED |  |  |  |  | 0
| Sound Attenuators of Baffle type to be provided on the Return air duct entering the AHU Room.(It should designed at 25 dB.) |  |  |  |  | 0
| Sound Attenuators shall consist of outer casing, sound absorbing material and internal baffles, splitters and supports as explained in the technical specifications. |  |  |  |  | 0
| Casing shall be of galvanized steel of not less than 20G in thickness. Casings shall be tested to 150mmwg and shall show no leakage or distortion in this condition. |  |  |  |  | 0
| Sound absorbing material shall be high density fiber glass held in place with at least 5% compression to prevent voids due to settling. Absorption material density shall be minimum 48 kg/cum. Fiberglass faced with minimum 26 g perforated galvanized sheet metal of minimum 40% open area. Combustion ratings shall be as explained in the tender specifications | Sqm |  |  |  | 0
0
7.01 | Floor Flushout : As per LEED requirement each Floor Flushing to be done with temporary exhaust fan. LEED requires a building flush to be executed by supplying a total air volume of 14,000 cubic feet of outdoor air per square foot of floor area. Cost of arranging Temporary exhaust fan & related electrical cable requirement is part of the cost. | Lot |  |  |  | 0
0
8 | Supply & Installation of Display type CO2 Sensor with control panel cum starter panel to measure the return air CO2 level in the AHU room & give comment to Fresh air FAN to SWITCH ON/OFF. Costing should include all the required installation accessories. | Nos |  |  |  | 0
0
8.01 | Supply & installation of Room Type Temperature Sensors with all duct mounting accessories.(for Supply air). The cost should also include integration of return air temperature sensor along with two way modulating valve. | Nos |  |  |  | 0
0
8.02 | Cable and Conduit |  |  |  |  | 0
a) | 4 Core 1.0 SQ. MM, unarmoured ATC conductor multistranded, Shielded cable. | Rmt | 80 | 78 | 20 | 7840
b) | 2 core 1.5 SQ. MM, unarmoured ATC conductor multistranded Shielded twisted pair cable | Rmt |  |  |  | 0
c) | 2 Core 1.0 SQ. MM, unarmoured ATC conductor multistranded, Shielded cable. | Rmt | 20 | 44 | 10 | 1080
d) | 4 Core 10 SQ. MM, unarmoured ATC conductor multistranded, UnShielded cable. | Rmt | 30 | 540 | 60 | 18000
e) | 4 Core 6.0 SQ. MM, unarmoured ATC conductor multistranded, UnShielded cable. | Rmt | 40 | 403 | 30 | 17320
f) | PVC- FRLS complete with all fittings and accessories - 25mm | Rmt | 80 | 60 | 20 | 6400
0
A | SUB TOTAL VALUE FOR AIR DISTRIBUTION SYSTEM |  |  | 110939.8 | 35305.4 | 1347825.2
0
9 | INSULATION (Please note that insulation should be with anti-microbial properties ) |  |  |  |  | 0
0
9.1 | Supply and installation of acoustic lining within supply air ducts, as per the approved shop drawings / specifications. |  |  |  |  | 0
a) | 10 mm thk Open cell nitrile rubber insulation .The insulation should be of Class '1' material. | Sqm |  | 860 | 180 | 0
0
9.2 | Supply and installation of External thermal insulation on ducts as per the approved shop drawings/ specifications. |  |  |  |  | 0
a) | 9mm thick closed cell elastomeric nitrile rubber insulation with adhesives. The insulation should be of Class 'O' material. Please note that the VOC limit for the duct insulation adhesive should meet leed requirement. | Sqm | 20 | 360 | 160 | 10400
0
b) | Supply & installation of under deck thermal insulation of exposed roof with 19 mm thick 'closed cell elastomeric nitrile rubber insulation with self adhesives. | Sqm |  |  |  | 0
0
c) | Supply & installation of under deck thermal insulation of exposed roof with 19 mm thick 'closed cell elastomeric nitrile rubber insulation with self adhesives, covered with factory finished fibre glass cloth to be painted as per Architect color specification. | Sqm |  |  |  | 0
0
| RECTIFICATION OF AHU Room Acoustic Insulation |  |  |  |  | 0
9.3 | Supply, installation, testing & commissioning of AHU room accoustic insulation with 25mm thick opn cell nitrile rubber as per drawings and specifications, mounted on a suitable GI channel frame work with 24 Gauge Al perforated sheet. | LOT | 1 | 3000 | 400 | 3400
0
B | SUB TOTAL VALUE FOR INSULATION |  |  | 4220 | 740 | 13800
0
| DX UNIT RE INSTALLTION |  |  |  |  | 0
0
10 | REMOVAL OF CASSETTE UNIT | Nos | 2 |  | 1500 | 3000
11 | REMOVAL OF SPLIT UNIT | Nos | 2 |  | 800 | 1600
12 | REFIXN OF CASSETTED UNIT | Nos | 2 |  | 3500 | 7000
13 | REFIXNING OF SPLIT UNIT | Nos | 1 |  | 1500 | 1500
14 | SITC OF SPLIT UNIT 2.5TR | Nos | 1 | 48500 | 1800 | 50300
15 | TIMER PANLE FOR SPLIT UNIT | Nos | 1 | 5500 | 800 | 6300 | quoted for timer
16 | COPPER PIPING CASSETTED UNIT | rmt | 40 | 1240 | 200 | 57600
17 | COPPER PIPING split unit | rmt | 160 | 1100 | 200 | 208000
18 | cable tray 450mm | rmt | 50 | 870 | 255 | 56250
19 | 1 " dia PVC conduit | RM | 90 | 60 | 20 | 7200
20 | Refrigerent Gas | kg | 20 | 850 | 350 | 24000
21 | Cable end termination | Lot | 1 | 1000 | 250 | 1250
22 | stand for split and casetted unit | nos | 3 | 1250 | 250 | 4500
23 | PVCA &Cu Conductor Control Cabling |  |  |  |  | 0
24 | 2 C X 1.5 Sqm. | RM |  |  |  | 0
25 | 4 C X 1.5 Sqm. | RM | 80 | 111 | 20 | 10480
26 | 3 C X 1.5 Sqm. | RM | 40 | 85 | 20 | 4200
27 | 6 C X 1.5 Sqm. | RM |  |  |  | 0
28 | 5 C X 1.0 Sqm. | RM | 90 | 106 | 20 | 11340
0
29 | Earthing |  |  |  |  | 0
a) | 25 X 6 GI flat | RM |  |  |  | 0
b) | 8 SWG GI wire | RM | 30 | 60 | 20 | 2400
0
| SUB TOTAL VALUE FOR DX UNIT RE INSTALLTION |  |  |  |  | 456920
| GRAND TOTAL FOR LOW SIDE WORKS |  |  |  |  | 1818545.2

## csu unit
SI. No | Description | Unit | Qty | SUP.Rate | INST. | Amount
RATE
1 | Supplying, installing, testing, and commissioning a complete chilled water-based AHU (AIR HANDILING SYSTEM) FLOOR -mounted/double-skin air handling unit (30 TR) 15000 CFM suitable for comfort cooling in . Each AHU shall be constructed with 25 mm PUF insulated double-skin panels, DIDW centrifugal fans (forward or backward curved) driven by TEFC motors (3-phase, IP55, Class F), 6/8-row copper tube-aluminium finned chilled water cooling coils with 1¼” and 1” BSPM pipe connections respectively, insulated SS-304 sloped drain pans, G4 washable synthetic filters, and fitted with 2-way motorized modulating control valves with actuators.The unit shall be controlled using wall-mounted digital thermostats and include flexible connections, drain traps, and air vents. The system shall be connected to a chilled water pumping arrangement as per basebuilder Details. All associated valve sets including butterfly valves (lever-operated, wafer type, CI with EPDM seat), Y-strainers, forged brass/CI ball valves, non-return valves, air vents, and drain valves shall be provided for operational flexibility and maintenance. Chilled water distribution piping shall be of MS Class B, threaded/screwed type up to 65 mm dia, including all required elbows, tees, reducers, unions, and insulated using closed-cell nitrile rubber (19 mm for ≤50 mm pipe dia and 25 mm for >50 mm), with vapour barrier and adhesive fixing. The condensate drain piping shall be PVC 32/40 mm with 9 mm thick insulation and proper U-traps. Electrical cabling from power panel to all motors and controls, using copper armored power and shielded control cables with earthing, lugs, and saddling, shall be included. The entire system shall be installed with proper supports, clamps, anchors, tested for leaks and performance, flushed, insulated, and commissioned in accordance with IS and ASHRAE standards, complete in all respects as per approved drawings and site conditions.
A | 15000 cfm | NOS | 1 | 680000 | 20000 | 700000
B | 2400 cfm | NOS | 0 |  |  | 0
2 | INSULATED CHILLED WATER PIPING : Supply, Installation, Testing and Commissioning of factory pre-insulated MS 'C' class schedule 40 pipes with PUF Insulation of 20 kg/m3 density and PUF saddle of 40 kg/m3 and 26 G GI cladding. (Conforming to IS 1239 for 150 mm dia, 8 mm wall thick for pipe size beyond 150 mm dia). Use 30 mm thick insulation up to 100 mm pipe dia and 50 mm thick insulation for 125 mm dia. For Higher sizes, please pvide 75 mm thick insulation. Vendor shall consider the cost for pipe supports and accessories. All the pipe elbows, bends, T-s, reducers, flow thugh branches shall be considered in this line item. Please refer technical specification for quote. chilled water pipes shall be painted with standard colors. cost of painting shall be included. |  |  |  |  | 0
a | 50 mm dia with 30 mm insulation | MTR | 2 | 1170 | 400 | 3140
b | 65 mm dia with 30 mm insulation | MTR | 12 | 1520 | 490 | 24120
c | 32 mm dia with 30 mm insulation | MTR | 0 | 870 | 280 | 0
d | 25 mm dia with 30 mm insulation | MTR | 0 | 750 | 230 | 0
3 | INSULATED BUTTERFLY VALVES (CHW PIPING) : Supply, Installation, Testing & Commissioning of pre insulated butterfly valves with 1000 kPa working pressure, 30 °C maximum operating temperature, Cast in body for DN 50 to 300, Ductile in body for DN 350 plus, EPDM Seal, Stainless Steel 416 Shaft material, Nylon coated ductile in, extended stem, lever lock handle and wafer style for installation between flanges and confirming to IS:13095. Use Table “E” Flanges for connections with GI bolt nuts. The complete valve assembly shall be insulated with similar insulation of chilled water piping and insulated with 26 G GI cladding.
a | 50/65 mm dia | NOS | 2 | 2360 | 480 | 5680
4 | INSULATED Y-STRAINER (CHW PIPING) : Supply, Installation, Testing & Commissioning of pre insulated Y-strainer with 1000 kPa working pressure; cast-in body, flanged ends for DN65 and larger, threaded connections for DN 50 and smaller, bolted cover, perforated stainless-steel basket, and bottom drain connection. Use CS Hot dip Galvanized lab joint flanges conforming to IS 2062 to suit SS stub ends. SS stub ends conforming to ASTM A 403 Gr. WP 304-S, short neck with 125 AARH face finish to suit ANSI150 Lap joint flanges. The bolt length shall be suitable for fixing lock nut`. The complete valve assembly shall be insulated with similar insulation of chilled water piping and insulated with 26 G GI cladding.
a | 65/50mm dia | NOS | 1 | 5500 | 800 | 6300
5 | THERMAL LOAD METER BTU METER (ULTRASONIC TYPE) : Supply, Installation, Testing and Commissioning of clamp-on type ultrasonic BTU meter with display unit complete with supply and return water temperature sensors; The price shall include the power supply modules for the BTU meter. The BTU meter shall communicate to third party BMS thugh both analog input (4-20mA) and BACnet over MS/TP ptocol.
a | 50 mm dia, 8 CMH | NOS | 2 | 50500 | 2500 | 106000
6 | Motorised two way valve : Supply, Installation, Testing and Commissioning of pressure independent balancing & contl valve (PIBCV) of 400 kPa close-off rating, spring return type as per specifications, with modulating type actuator with insulation similar to CHW pipe. Diaphragm type is preffered. The complete valve assembly shall be insulated with similar insulation of chilled water piping as per Specification and insulated with 26 G GI cladding. The actuator shall have Analog Input/Analog Output for BMS connectivity. The necessary contl/power cables, plug and MS conduits to be considered.
a | 50 mm dia, | NOS | 1 | 45000 | 2500 | 47500
7 | PRESSURE GAUGES : Supply, Installation, Testing and Commissioning of Indicating-dial type, 100-mm Dial Size, white backgund with black marking, Case & Bezel: SS304, Bayonet type bezel, weatherpof to IP-67 as per IS 13947, Shatterpof Glass windows; SS316 Bourdon, SS316 Socket, SS304 Movement, 0 – 10 kg/cm³ Range, 1% F.S.D Accuracy, 130% FSD Over Range, Ze Reset Mic pointer (Internal), Blow Out Disc pvided (Neoprene) on the top of case, chemical Seal Unit, Top Flange SS316, Diaphragm SS316+PTFE, Bottom Flange SS316+PTFE, Connection 25-mm ANSI 150#RF in SS316, 125 AARH, Filling Fluid Silicone Oil with SS Tag Plate, Stainless Steel U-Siphon and 13mm Brass body ball valve with weldable MS coupling. | NOS | 2 | 3400 | 400 | 7600
8 | DIAL TYPE THERMOMETER : Supply, Installation, Testing and commissioning of Indicating-dial type Stainless steel Case & Stem; Sensing element with Bi-metal strip coiled, IP 65 Ptection, Dial with Aluminium black graduation on white backgund, Pointer with Aluminium black coloured Slotted ze adjustable, Window with Sheet Glass and of length to suit installation, Neoprene Gasket material, Accuracy with Plus or minus 1 percent of range or plus or minus 1 scale division to maximum of 1.5 percent of range, Measuring range 0-50 deg C and Stainless Steel U-Siphon and 13mm Brass body ball valve with weldable MS coupling. | NOS | 2 | 2200 | 250 | 4900
9 | ALUMINIUM CLADDING : Supply, Installation, Testing and Commissioning of 0.45 mm Thick aluminium sheet metal as cladding as shown in appved design drawings. Please refer Specifications for more details. | SQM | 0
10 | ELECTRICALPANEL WITH VFD SUTAIBEL FOR 15000 CFM : | NOS | 1 | 63500 | 3000 | 66500
a | 4 Core x 6 Sq. mm Cu. AR. Cable | MTR | 20 | 423 | 30 | 9060
b | 4 Core x 4 Sq. mm Cu. AR. Cable | MTR | 0 | 423 | 30 | 0
11 | COMMUNICATION CABLE : Supply, Laying, Termination, Testing and Commissioning of communication cable between PAC indoor and outdoor units, VRF indoor and outdoor units with all necessary supports and accessories. Cable size shall be as per respective item OEM recommendations. The quoted price shall incude the cost of GI conduits, lugs and all necessary accessories and supports. | MTR | 0
12 | Panel for CSUunit : Supply, Termination and Commissioning of the electrical panel for r CSU units.
| Total Amount of Supply and Installation |  |  |  |  | 980800
Taxes Extra as Applicable

## make
MAKES OF MATERIALS
Sl No | Description | Make
1 | Rectangular Duct Sheets | Zeco / Vedha/ DEV Duct /Seven star/CoolFreez
2 | Elliptical duct | GP SPIRA/ SPIROTUBE/ DEV Duct/CoolFreez
3 | MS Duct | Vedha / DEV Duct
4 | Plenum | Zeco / EDGETEK/Urjas/ Vayhan / Airtech Controls/Vedha
5 | volume control dampers | Airtech Controls / Airmaster / System air/Vedha
6 | Motorized Fire dampers | System air / Greenheck/ Airmaster
7 | Fire dampers control panel | SEWTRONICS /MAPRO / THITTANIX
8 | H2 SENSOR +PANEL | SEWTRONICS /MAPRO / THITTANIX / Transmonk
9 | CO2 SENSOR +PANEL | SEWTRONICS /MAPRO / THITTANIX / Transmonk
10 | Flexible duct | ATCO / Airmaster / Seven star/ UP Twiga
11 | Butterfly damper /Collar damper/back draft damper | Airtech Controls / Airmaster / System air /Vedha
12 | Mixing box | Airtech Controls / Airmaster / System air /Vedha
13 | Diffuser & Grille | Airtech Controls / Airmaster / System air /Vedha
14 | Slot diffuser | Airtech Controls / Airmaster / System air /Vedha
15 | Duct Inline fan | System air / Kruger /caryaire / Air Maskin
16 | SISW Fan with AHU Construction | GREENHECK / KRUGER (FAN) + Vayhan /VTS ( AHU Construction) / Air Maskin
17 | Acoustic Insulation - Open Cell | Armaflex / KFLEX / ALP
18 | Wall insulation | Armaflex / KFLEX / ALP
19 | Thermal Insulation | Armaflex / KFLEX / ALP
20 | Z Piece | Zeco / Vedha/ DEV Duct /Seven star/CoolFreez
21 | VRV Units | Bluestar /Daikin
22 | Cable tray | Cabletech /Classic / HBS
23 | Drain Pipe | Ashirvad / Astral/ Supreme
24 | Cables | Powerflex/Polycab
25 | 1 " dia CPVC FRLS conduit | VIP or equal
26 | Drain Tank & Pump | Aspen / Microdam
27 | AUTO SEQUENTIAL PANEL | Thittanix /Mapro/Microcon/ Swetronics
28 | Hitec supports and full threaded rods | Hilti/Fisher
29 | Rope support | Gripple / GPL
30 | Copper pipes | Rajco / Mandev / Mexflow/ Parasmani
31 | Heater bank | SEWTRONICS / THITTANIX
32 | Vibration isolators | Dunlop / Resistoflex / easyflex
33 | Sound attenuators | System Air / Air mastrer
34 | PVC/HDPE pipe for Drain | Finolex / Supreme / Kissan
35 | Adhesive for Duct insulation | SR998 / SR505 / Polygrip / K flex /Equivalent
36 | CAT 6 / 5 cables | D link / Molex
37 | VAV boxes | Vedha/ Dynacraft
38 | VAV actuators & controllers | Belimo/JCI/ Neptronics
39 | VAV Bacnet integrator in enclosed panel | Field server/ protoconverter / Santeliqip - Enclosed panel ( Mapro/ SEWTRONICS)
40 | Pressure reducing Valve | Audco / Leader / Zoloto/ Flowserve
41 | Ball Valve | Audco / Leader / Zoloto/ Flowserve
42 | T & RH Sensor | Johnson Controls /Dwyer / Greystone/Omicron
43 | DP Switch | Johnson Controls /Dwyer / Greystone/Omicron
44 | DP Sensor | Johnson Controls /Dwyer / Greystone/Omicron
45 | Duct type temp sensors | Johnson Controls /Dwyer / Greystone/Omicron
46 | Room type T & RH sensor | Johnson Controls /Dwyer / Greystone/Omicron
47 | Co2 sensors | Johnson Controls /Dwyer / Greystone/Omicron
48 | CAT 6 cables | D link / Molex
49 | cables | Varsha / deepanjali or equivalent.
50 | HUB Switch | D Link or equalant make
51 | Vibration isolators | Dunlop / Resistoflex / easyflex
52 | Adhesive for Duct insulation | SR998 / SR505 / Polygrip / K flex /Equivalent
53 | Chilled Water CSU | VTS/ Edgetech/ Luftek
54 | MS pipes | Jindal / Tata / Sail
55 | Ball Valves | ITAB /kits/ Advance / Saunders/Sant
56 | Balancing Valves | ADVANCE /HONEYWELL
57 | Butterfly Valves | Audco / Advance / Saunders
58 | y-strainers | Sant/DS Engineers/Emerald
59 | Thermometers/pressure gauges | KI /Waaree/H. Guru
60 | PIBC | Belimo / sauter / danfos
61 | Motorized valves | Oventrop/Hattersly/Johnson/Honeywell/Siemens
62 | flowmeter | ABB / Siemens /kamstrup
63 | BTUH Meter | Kamstrup / Landish & JYR
64 | AHU Filters | American Air filters/Spectrum/Metair / Freudenberg