## Assumptions & Exclusions
HVAC WORKS FOR MORGAN STANLEY CO-WRKS
CLIENT | : MORGAN STANLEY
ARCHITECTS | : CO-WRKS
PMC | :
DATE / REV NO. | : 09.03.2026 / R1
CONSULTANTS | : E SOLLUTIONS
SUBJECT | : ASSUMPTIONS & EXCLUSIONS
ASSUMPTIONS & EXCLUSIONS
1 | Quantities are derived based on the available drawings Dated on 09.03.2026
2 | The scope is limited to Hvac works which are part of BOQ only.
3 | ODU Location Considered in the Balcony and Basement.
4 | Dismantling & Dumping / handing over of duct, Grilles, VAV works considered.

## SUMMARY-HVAC
HVAC WORKS FOR MORGAN STANLEY CO-WRKS
CLIENT | : MORGAN STANLEY
ARCHITECTS | : CO-WRKS
PMC | :
DATE / REV NO. | : 09.03.2026 / R1
CONSULTANTS | : E SOLLUTIONS
SUBJECT | : SUMMARY
BILL OF QUANTITIES - SUMMARY
SL.NO. | DESCRIPTION | AMOUNT IN INR
|  | SUPPLY | INSTALLATION | TOTAL
1 | VARIABLE REFRIGERANT FLOW SYSTEM | 2804304 | 328400 | 3132704
2 | LOWSIDE WORKS | 1230920 | 183100 | 1414020
3 | ADDITIONAL WORKS | 0 | 90000 | 90000
| TOTAL EXCLUDING TAX |  |  | 4636724

## VRF System
HVAC WORKS FOR MORGAN STANLEY CO-WRKS
CLIENT | : MORGAN STANLEY
ARCHITECTS | : CO-WRKS
PMC | :
DATE / REV NO. | : 09.03.2026 / R1
CONSULTANTS | : E SOLLUTIONS
SUBJECT | : VRF SYSTEM BOQ
SL. NO. | DESCRIPTION | UNIT | QTY |  | TOTAL QTY | RATE IN INR |  |  | AMOUNT IN INR
|  |  | L1 | L2 |  | SUPPLY | INSTALLATION | TOTAL | SUPPLY | INSTALLATION | TOTAL
The contractor / vendor should read the specifications thoroughly and quote the price for each item. The BOQ should read in-conjunction with specification, drawing & equipment schedule. The cost shall include the cost of the material, transportation, taxes, duties, lifting, shifting, storing, handling, installation, testing and commissioning.All the items should be with performance guarantee of minimum 1 year.
1 | VARIABLE REFRIGERANT FLOW UNITS :
Outdoor Unit :
Air Cooled Outdoor Condensing Unit consisting of high performance, low noise, complete Inverter driven scroll compressors with a COP of minimum 3.33 upto 10 TR and COP of Minimum 3.28 for all equipments above 10 TR at full load performance at ARI conditions, condenser coil, condenser fan, fan motor, microprocessor panel with display, with weekly timed scheduler. The complete assembly shall be enclosed in a powder coated sheet metal casing, controlling the supplied indoor units. The unit shall have high static condenser fan suitable for ducting condenser air discharge. The unit shall have provision for control & monitoring from a central location with BACNET / LONWORKS protocol, all enclosed in a powder coated sheet metal casing, supporting stand, coil protection mesh, vibration isolation pads, etc. to be installed on terrace as shown in the drawing.
The cost of the unit shall include the cabling, gland, cable tray and breaker (if required) to distribute power from single source provided near the unit around a distance of 5m and also factory testing, packing, air freight, insurance, Excise duty, CVD, VAT, Surcharge & Cess, Testing, Commissioning & Handing Over .
The Condensing unit (Outdoor Unit) shall deliver the required capacity at the ambient conditions of 43°C, if the condensing units need to be resized for the proposed temperature. The Indoor temperature shall be maintained at 23°C. The contractor shall size the condensing units based on the required difference in temperature between the Indoor & Outdoor unit.
The rate quoted shall include the cost of hot air discharge cowl fabricated out of 1.2 mm thick powder coated sheet metal, exhaust louver of approved colour.
| The rate quoted shall include the cost of Electrical brakers / isolators & necessary cable , terminations & cable tray to distribute power to multiple VRF condensing units from a single source of power provided by other agencies at a distance of 5m from the condensing units. | [10 empty] | Quoted for DAIKIN
The equipment shall be Supplied with MS stand the contractor shall ensure that the existing water-proofing of the terrace shall not be damaged by the proposed supporting system.
1.1 | 5 TR at 36°C ambient & 24°C indoor (Bangalore Conditions) | Sets | 1 | 0 | 1 | 152400 | 6000 | 158400 | 152400 | 6000 | 158400 | 6HP | 152400
1.2 | 8 TR at 36°C ambient & 24°C indoor (Bangalore Conditions) | Sets | 0 | 1 | 1 | 227520 | 10000 | 237520 | 227520 | 10000 | 237520 | 10HP | 227520
1.3 | 12 TR at 36°C ambient & 24°C indoor (Bangalore Conditions) | Sets | 1 | 1 | 2 | 305400 | 14000 | 319400 | 610800 | 28000 | 638800 | 14HP | 305400
2 | VRF CONTROLLERS:
The controller shall be microprocessor based, BMS compatible, web access, in-built software, emergency interlock, multi language real time clock, power pack, relays, connectors, port for connecting portable operator terminal, etc., completely housed in sheet metal enclosures. The controller shall be capable of controlling all VRF equipments in the proposed BOQ with following functions:
CONTROLLING:
On/Off command
Operation mode setting
Fan speed setting
Lock setting
Air flow setting
Zonal Control
Scheduled Time on/off (Timer)
MONITORING & REPORTS:
On/Off
Operation mode
Fan speed
Lock
Air flow
Ambient & Set temp.
Current space temp.
Error
Graphs
The cost of the controller shall also include control cabling.
| VRF Controler should be capable of multiple outdoor units and multiple indoor units as shown in schematic. | Lot | 0 | 1 | 1 | 250000 | 5000 | 255000 | 250000 | 5000 | 255000
3 | CEILING MOUNTED 4WAY CASSETTE UNITS:
Decorative ceiling mounted type Evaporator Units (Room Units) consisting of evaporator coil, evaporator fan, fan-motor, rough filters, supply air deflecting type outlet grille with 4 way throw, built-in drain pump for automatic draining of condensate water, etc. all housed in a decorative casing complete suitable for ceiling mounting. The units shall supplied with cordless remote control unit. The capacity of the unit indicated are at design operating conditions.
The rate quoted shall include power cable (5 m approx.) 'between socket (located adjacent to the unit) & AC unit.
3.1 | 3 TR, 1200 cfm | Sets | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
3.2 | 2.5 TR, 1000 cfm | Sets | 7 | 5 | 12 | 51600 | 4000 | 55600 | 619200 | 48000 | 667200
3.3 | 2 TR, 600 cfm | Sets | 0 | 4 | 4 | 48576 | 4000 | 52576 | 194304 | 16000 | 210304
3.4 | 1.5 TR, 600 cfm (Compact Type ) | Sets | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
3.5 | 1 TR, 400 cfm (Comapact Type ) | Sets | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
3.6 | 0.8 TR,320 cfm ( Compact Type ) | Sets | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
3 | CEILING MOUNTED 1 WAY CASSETTE UNITS:
Decorative ceiling mounted type Evaporator Units (Room Units) consisting of evaporator coil, evaporator fan, fan-motor, rough filters, supply air deflecting type outlet grille with 1 way throw, built-in drain pump for automatic draining of condensate water, etc. all housed in a decorative casing complete suitable for ceiling mounting. The units shall supplied with cordless remote control unit. The capacity of the unit indicated are at design operating conditions.
The rate quoted shall include power cable (5 m approx.) 'between socket (located adjacent to the unit) & AC unit.
3.1 | 3 TR, 1200 cfm | Sets | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
3.2 | 2 TR, 800 cfm | Sets | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
4 | WALL MOUNTED UNIT:
Decorative Wall mounted evaporative unit (Room unit) shall consist of evaporator coil, evaporator fan, fan-motor, rough filters, supply air deflecting type outlet grille, built-in drain pump for automatic draining of condenser water etc. all housed in a decorative casing suitable for wall mounting. The units shall be supplied with cordless remote control unit with digital display.
The rate quoted shall include power cable (5 m approx.) between socket (located adjacent to the unit) & AC unit.
4.1 | 2.5 TR, 1000 cfm | Sets | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
4.2 | 2 TR, 800 Cfm | Sets | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
4.3 | 1.5 TR, 600 Cfm | Sets | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
4.4 | 1.0 TR, 400 Cfm | Sets | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
4.5 | 0.8 TR,320 cfm | Sets | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
5 | FAN COIL UNIT: ( HGH STATIC )
All sheet metal (G¦) Circular In Line Centrifugal Fans for use as Exhaust Air Unit. The unit shall be complete with circular casing, fixing bracket, fan motor asembly, power cabling of around 3 m length from the unit to power socket provided by other agencies etc.. suitable for operation through on 220 V, 1 Ph, 50 Hz AC supply. The unit shall be installed as shown in the drawing. The units shall be supplied with cordless remote control unit with digital display.
The rate quoted shall include power cable (5 m approx.) between socket (located adjacent to the unit) & AC unit.
5.1 | 03 TR, 1200 cfm 4 mm | Sets | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
5.2 | 2.5 TR, 1000 cfm 3 mm | Sets | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
5.3 | 2 TR, 600 cfm, 3 mm | Sets | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
5.4 | 1.5 TR, 600 cfm, 2 mm | Sets | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
5.5 | 1 TR, 400 cfm, 2 mm | Sets | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
5.6 | 0.8 TR,320 cfm , 2 mm | Sets | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
6 | DUCTABLE CEILING MOUNTED INDOOR UNITS:
Indoor Ceiling Mounted Ductable Evaporative units complete with evaporator coil, evaporator fan suitable for 15 mm external static, built in drain pump pre-filter, all housed in a powder coated sheet metal casing complete with vibration isolators suitable for suspending from ceiling slab. The units shall incorporate electronic control unit with Cordless remote control pad suitable for single phase, 230 ± 10% V, 50 Hz. electric supply. Capacity of the units required :
The capacity of the units indicated are at design operating conditions:
The rate quoted shall include the cost of drain pump,
6.1 | 4 TR, 1600 Cfm 10 mm | Sets | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
6.2 | 5 TR, 2400 Cfm 10 mm | Sets | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
6.3 | 8 TR, 3200 Cfm 10 mm | Sets | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
7 | DUCTABLE OUTSIDE AIR UNIT UNITS:
Indoor Ceiling Mounted OUTSIDE AIR UNITcomplete with evaporator coil, evaporator fan suitable for 15 mm external static, built in drain pump pre-filter, all housed in a powder coated sheet metal casing complete with vibration isolators suitable for suspending from ceiling slab. The units shall incorporate electronic control unit with Cordless remote control pad suitable for single phase, 230 ± 10% V, 50 Hz. electric supply. Capacity of the units required :
The capacity of the units indicated are at design operating conditions:
The rate quoted shall include the cost of drain pump,
7.1 | 3 TR, 500 Cfm 8 mm | Sets | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
7.2 | 5 TR, 750 Cfm 10 mm | Sets | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
7.3 | 7 TR, 1000 Cfm 10 mm | Sets | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
8 | REFRIGERANT PIPING
Insulated Refrigerant piping between the indoor units and the outdoor units with minimum pipe thickness of 1.6 mm. The Route length of Refrigerant piping between the outdoor units & Indoor units shall be as per the drawings furnished. The price quoted shall include liquid receiver, on-line accumulator, oil separator & other safety devices for required for total nos of circuits, if required for long distance and first charge of refrigerant & oil for the complete system including piping length required.
All refrigerant pipes shall be of hard drawn pipes in straight lengths shall be used. Wall thickness of all piping shall be 16 guage, 1.6 mm thick
The refrigerant pipes to be laid in a ladder type cable tray. The price quoted shall also include the cost of the cable tray and the supporting arrangement from the truss at 15m (as per site condition) for the cable tray.
Class 'O' Nitrile rubber insulation should be used to insulate the refrigerant pipes .
The price quoted shall include cost of refnets, refrigerant & oil, necessary supports, supporting tray, pressure testing, vaccumization & commissioning, etc.
8.1 | Piping with 1 Set 5 TR Outdoor Units & multiple Indoor Units. | Rmt | 40 | 0 | 40 | 1100 | 490 | 1590 | 44000 | 19600 | 63600
8.2 | Piping with 1 Set 6 TR Outdoor Units & multiple Indoor Units. | Rmt | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
8.3 | Piping with 1 Set 8TR Outdoor Units & multiple Indoor Units. | Rmt | 0 | 60 | 60 | 1360 | 490 | 1850 | 81600 | 29400 | 111000
8.4 | Piping with 1 Set 12 TR Outdoor Units & multiple Indoor Units. | Rmt | 136 | 136 | 272 | 1900 | 520 | 2420 | 516800 | 141440 | 658240
8.5 | Piping with 1 Set 14 TR Outdoor Units & multiple Indoor Units. | Rmt | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
8.6 | Piping with 1 Set 15 TR Outdoor Units & multiple Indoor Units. | Rmt | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
8.7 | Piping with 1 Set 16TR Outdoor Units & multiple Indoor Units. | Rmt | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
8.8 | Piping with 1 Set 30 TR Outdoor Units & multiple Indoor Units. | Rmt | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
8.9 | Piping with 1 Set 32 TR Outdoor Units & multiple Indoor Units. | Rmt | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
9 | Piping with 1 Set 36 TR Outdoor Units & multiple Indoor Units. | Rmt | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
9 | Control cabling between the indoor unit, outdoor unit. The cables shall be armoured copper cable and shall be clamped to the wall / truss heavy duty GI clamps.
9.1 | Piping with 1 Set 5 TR Outdoor Units & multiple Indoor Units. | Rmt | 72 | 0 | 72 | 113 | 26 | 139 | 8136 | 1872 | 10008
9.2 | Piping with 1 Set 6 TR Outdoor Units & multiple Indoor Units. | Rmt | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
9.3 | Piping with 1 Set 8TR Outdoor Units & multiple Indoor Units. | Rmt | 0 | 105 | 105 | 113 | 26 | 139 | 11865 | 2730 | 14595
9.4 | Piping with 1 Set 12 TR Outdoor Units & multiple Indoor Units. | Rmt | 167 | 156 | 323 | 113 | 26 | 139 | 36499 | 8398 | 44897
9.5 | Piping with 1 Set 14 TR Outdoor Units & multiple Indoor Units. | Rmt | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
9.6 | Piping with 1 Set 15 TR Outdoor Units & multiple Indoor Units. | Rmt | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
9.7 | Piping with 1 Set 16TR Outdoor Units & multiple Indoor Units. | Rmt | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
9.8 | Piping with 1 Set 30 TR Outdoor Units & multiple Indoor Units. | Rmt | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
9.9 | Piping with 1 Set 32 TR Outdoor Units & multiple Indoor Units. | Rmt | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
10 | Piping with 1 Set 36 TR Outdoor Units & multiple Indoor Units. | Rmt | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
|  |  | 0 | 0 | 0
10 | DRAIN PIPING
Supply, and installation insulated CPVC medium class Condensate drain piping with 8 kg/cm2 density, cut to required lengths and installed with all solvent joints, providing and fixing the necessary fittings like flanges,elbows tees, reducers, etc. Supporting arrangements as per site conditions.
The rate quoted shall include the cost of nitrile rubber insulation for pipes running in unconditioned space.
10.1 | 50 mm dia | M | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
10.2 | 40 mm dia | M | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
10.3 | 32 mm dia | M | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
10.4 | 25 mm dia | M | 78 | 89 | 167 | 180 | 40 | 220 | 30060 | 6680 | 36740
10.5 | 18 mm dia | M | 54 | 78 | 132 | 160 | 40 | 200 | 21120 | 5280 | 26400
11 | CONDENSATE DRAIN TANK
Condensate drain tank of minimum 4 ltrs., capacity complete with twin pump to lift water up to 10 meters, synchronizing arrangement, water level controller, alarm & other accessories for pumping out the drain water from the Unit to the nearest drain point.
The rate quoted shall include the cost of all accessories to communicate to Building Management System for status, water level, alarm, failure of any pump etc.
| The successful contractor shall furnish the sample for approval before ordering. | Lots | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
12 | AUTO SYNCHORINIZATION PANEL
Synchoronization Panel capable of sychronizing DX / VRF Indoor Units to Operate based on the set number of hours, switch ON / OFF in the event of rise in temperature, failure of equipment, schedule change-over. The panel shall be installed in the existing BMS room.
| The rate quoted shall included the cost of BMS connectivity with RS-485 port. | Lots | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
| TOTAL | [7 empty] | 2804304 | 328400 | 3132704

## Lowside
HVAC WORKS FOR MORGAN STANLEY CO-WRKS
CLIENT | : MORGAN STANLEY
ARCHITECTS | : CO-WRKS
PMC | :
DATE / REV NO. | : 09.03.2026 / R1
CONSULTANTS | : E SOLLUTIONS
SUBJECT | : LOWSIDE WORKS BOQ
SL NO | DESCRIPTION | UNIT | QTY |  | TOTAL QTY | RATE IN INR |  |  | AMOUNT IN INR
|  |  | L1 | L2 |  | SUPPLY | INSTALLATION | TOTAL | SUPPLY | INSTALLATION | TOTAL
The contractor / vendor should read the specifications thoroughly and quote the price for each item. The BOQ should read in-conjunction with specification, drawing & equipment schedule. The cost shall include the cost of the material, transportation, taxes, duties, lifting, shifting, storing, handling, installation, testing and commissioning.All the items should be with performance guarantee of minimum 1 year.
1 | DOUBLE SKIN PLENUM:
Supply Installation of Factory Fabricated double skin SA plenum with dampered outlet Main framework shall be extruded aluminium structural section with 48+2 mm thick thermos-acoustic panel. Thermo-acoustic panel shall be compromising of 23+2mm thick thermal insulation of 40kg/cum density PU foam injected between 0.6mm pre coated GI outer sheet & 0.6mm plain GI intermediate sheet, followed by laminated tissue paper glass wool insulation of 25+2mm thickness having 70-80 kg/cum density sandwiched between intermediate sheet and inner skin of 0.8mm perforated sheet.
| The price is inclusive of fire rated 0.63 mm thick canvas required to connect AHU & plenum, access door and also supporting arrangement for suspending the plenum from the ceiling slab. | Sqm. | 0 | 0 | 0 | 3500 | 500 | 4000 | 0 | 0 | 0
2 | DUCT MOUNTED RECTANGULAR IN LINE FAN UNIT:
All sheet metal Double Skin Rectangular In Line Centrifugal Fans fabricated out of 1 mm thick Galvanized Steel for use as Exhaust/Outside Air Unit. The unit shall be complete with flanged connection on either side, fixing bracket, fan motor assembly, power cabling with required plug of around 5m length from the unit to power socket provided by other agencies etc.. suitable for operation through on 220 V, 1 Ph, 50 Hz AC supply.
The noise from Inline Fan shall not exceed 50 dbA
The external static pressure of the fan should not be less than 15 mm for fans up to 750 lps & 20 mm for fans above 751 lps.
The cost of the Inline Fan also includes DOL Starter and 3-speed step regulator. Fresh Air fan s should be with filters.
The rate quoted includes all required accessories to communicate to Building Management System. Fresh Air fan s , Fresh air fans should be with filter.
2.1 | ILFU - I: 2500 CFM , 25mm ESP | Nos. | 0 | 0 | 0 | 75000 | 8000 | 83000 | 0 | 0 | 0
2.2 | ILFU - II: 2000 Cfm , 20mm ESP | Nos. | 0 | 0 | 0 | 65000 | 8000 | 73000 | 0 | 0 | 0
2.3 | ILFU - I: 1500 Cfm , 20mm ESP | Nos. | 0 | 0 | 0 | 60000 | 8000 | 68000 | 0 | 0 | 0
2.4 | ILFU - II: 1000 Cfm , 20mm ESP | No. | 0 | 0 | 0 | 45000 | 8000 | 53000 | 0 | 0 | 0
2.5 | ILFU - III: 500 Cfm 20mm ESP | No. | 0 | 0 | 0 | 35000 | 8000 | 43000 | 0 | 0 | 0
3 | BATTERY ROOM EXHAUST FAN
All sheet metal (GI) Explosion Proof In Line Centrifugal Fans fabricated out of 1 mm thick Galvanized Steel for use as Battery Room Exhaust Air Unit. The unit shall be complete with flanged connection on either side, fixing bracket, fan motor assembly, power cabling with required plug of around 5 m length from the unit to power socket provided by other agencies etc.. suitable for operation through on 220 V, 1 Ph, 50 Hz AC supply. The unit shall be installed as shown in the drawing.
The rate quoted shall include 1 no., Hydrogen sensor for each fan, the control arrangement to switch On the fan automatically based on the input from hydrogen sensor.
The cost of the Inline Fan should also include DOL Starter and 3-speed step regulator.
The rate quoted shall include the cost of all accessories to communicate (soft Integration )to Building Management System through RS485 port for status, fan speed , failure . etc.
a | BR-ILFU-1: 500 Cfm , 30 mm static | No. | 0 | 0 | 0 | 110000 | 15000 | 125000 | 0 | 0 | 0
4 | AIR DISTRIBUTION SYSTEM
4.1 | SHEET METAL WORK:
Factory fabricated Sheet Metal Ducting out of GSS Sheets with TDF / TDC flanges (supplied by duct manufacturer), built-in sealant with low VOC, gaskets, Electro-galvanized bolts, nuts & Washers, Stiffner rods, anchor grip bolts, supports for ducts, guide vanes for all bends. All civil works like wall opening, plastering, finishing, etc.
The ducts shall be supplied in box shape only.
The ducts to be stored in a clean space with Torpolin sheet wrapped on both open sides & cleaned before errection. During the time of errection, if any of the ends are not connected, the contractor to ensure that the open ends are covered with Torpolin sheets.
Air Balancing of each individual supply & Exhaust air outlet to within +10% or -5% of the design air quantity and tabulating the same in a form of report and also the final air balancing figures to be indicated against each measured outlets in the as built drawings. Balancing also includes balancing of return air, supply air and outdoor fresh air quantity. Air flow hoods to be used for measuring the air flow across the square diffusers. Cost shall be included in the ducting cost.
Marking, cutting, chipping and finishing the AHU room walls /shafts / partitions around the HVAC duct, pipe, cable tray etc
The rate quoted shall include the cost of Pressure Testing & Documentation for 100% of the total ducting.
Stiffner rods shall be provided for all ducts above 1m.
GSS Ducting :
a | 1.2 mm thick | Sqm. | 0 | 0 | 0 | 1320 | 180 | 1500 | 0 | 0 | 0
b | 1.0 mm thick | Sqm. | 0 | 0 | 0 | 1144 | 156 | 1300 | 0 | 0 | 0
c | 0.8 mm thick | Sqm. | 0 | 450 | 450 | 1000 | 150 | 1150 | 450000 | 67500 | 517500
d | 0.63 mm thick | Sqm. | 180 | 200 | 380 | 950 | 150 | 1100 | 361000 | 57000 | 418000
4.2 | GSS ELIPTICAL DUCTING
GSS Eliptical duct ( test pressure shall be 250 pascal ) as per below specs.
Sheet Metal Work using Slip on Flanges for all sizes of the duct using Lock Former Machine. Fabrication as per IS Standards & attached technical specification. Galvanizing shall be 120 gsm coating of zinc, with factory test certificates. The cost shall include ducting supports using gripple supports, gasket, anchor fastener & GI nut, bolt etc. complete.
a | 1.0 mm thick | Sqm. | 0 | 0 | 0 | 1672 | 228 | 1900 | 0 | 0 | 0
b | 0.8 mm thick | Sqm. | 0 | 0 | 0 | 1320 | 180 | 1500 | 0 | 0 | 0
c | 0.63 mm thick | Sqm. | 0 | 0 | 0 | 1144 | 156 | 1300 | 0 | 0 | 0
4.3 | FLEXIBLE DUCTS
Metallized core fire rated flexible ducts with totally encapsulated helically wound spring wire. The flexible duct shall consists of outer and inner jacket with 16 kg/cum density, 25 mm thick TF rated fibre glass insulation in the middle with a K-value of 0.033 W/mk at 20°C. The flexible ducts shall be supported from the supporting grid / slab using hanging straps of at least 25 mm width and the strap shall cover a minimum of half the circumference.
Flexible Ducting :
a | 250 mm dia | M | 0 | 0 | 0 | 300 | 40 | 340 | 0 | 0 | 0
b | 150 mm dia | M | 0 | 0 | 0 | 220 | 30 | 250 | 0 | 0 | 0
4.3a | SEMI RIGID FLEXIBLE DUCTS
Semi rigid flexible duct made out of corrugated aluminium with water tight lock seams suitable for operating pressures upto 250 mmwg Shall be fixed to diffuser box using universal GI clamp with required fixing supports & termination clamps.
NOTE: The sample should be approved before finalizing the order.
a | 150 mm dia | M | 0 | 0 | 0 | 300 | 40 | 340 | 0 | 0 | 0
b | 100 mm dia | M | 0 | 0 | 0 | 250 | 40 | 290 | 0 | 0 | 0
4.4 | CIRCULAR CLAMPS
Circular Clamps for fixing flexible duct to GI ducts and diffuser box.
a | 250 mm dia | Nos. | 0 | 0 | 0 | 275 | 40 | 315 | 0 | 0 | 0
b | 150 mm dia | Nos. | 0 | 0 | 0 | 220 | 30 | 250 | 0 | 0 | 0
c | 100 mm dia | Nos. | 0 | 0 | 0 | 200 | 30 | 230 | 0 | 0 | 0
4.5 | BUTTERFLY DAMPERS
20 gauge Butterfly Dampers with SA round collars & flanges to connect rigid / flexible ducts. The Butterfly Damper shall have the required contour (groove) to hold the clamp & flexible duct.
a | 250 mm dia | Nos. | 0 | 0 | 0 | 750 | 100 | 850 | 0 | 0 | 0
b | 150 mm dia | Nos. | 0 | 0 | 0 | 660 | 90 | 750 | 0 | 0 | 0
c | 100 mm dia | Nos. | 0 | 0 | 0 | 660 | 90 | 750 | 0 | 0 | 0
4.6 | VOLUME CONTROL DAMPERS
Low leakage Volume Control Dampers with 30 mm deep TDF flanges suitable for connecting the ducts on both sides, complete with factory - made, aerofoil design of aluminium interlocking blades, 1.6 mm thick frame, channels for duct mounting, nylon bushes, vision indicator to indicate percentage of opening. The VCD shall be suitable to operate through a actuator if required. Whereas, shall be supplied with a operating knob with provision to lock at required position.
| The pressure drop across the dampers shall not exceed 1.5 mmwg at 1500 fpm for the cross section area of 1 sqm. | Sqm. | 0 | 0 | 0 | 11000 | 1500 | 12500 | 0 | 0 | 0
4.6.1 | Volume control Damper for Elliptiacl duct with Handle & Sleeves to connect supply air duct . | Sqm. | 0 | 0 | 0 | 8000 | 800 | 8800 | 0 | 0 | 0
4.7 | MOTORIZED ON/OFF DAMPER
a | Low leakage Motorized on/off Damper with flanges suitable for connecting the ducts complete with factory - made, 1.6 mm thick aerofoil design of Aluminium interlocking blades, 1.2mm thick frame for duct mounting, gears, nylon bushes, vision indicator to indicate percentage of opening. The Damper shall be suitable to operate through a actuator if required. Whereas, shall be supplied with a operating knob with provision to lock at required position. | Sqm | 0 | 0 | 0 | 7300 | 1000 | 8300 | 0 | 0 | 0
b | Actuator with required torque to open / close the damper with required control mechanism (both hardware & software), cabling. The actuator is capable to communicate with Building Management System.
| The actuator shall be suitable for outdoor installation when installed externally. | Nos. | 0 | 0 | 0 | 8540 | 1200 | 9740 | 0 | 0 | 0
4.7a | MOTORIZED MODULATING DAMPER
a | Low leakage Motorized Modulating Damper with flanges suitable for connecting the ducts complete with factory - made, 1.6 mm thick aerofoil design of Aluminium interlocking blades, 1.2mm thick frame for duct mounting, gears, nylon bushes, vision indicator to indicate percentage of opening. The Damper shall be suitable to operate through a actuator if required. Whereas, shall be supplied with a operating knob with provision to lock at required position. | Sqm | 0 | 0 | 0 | 7300 | 1000 | 8300 | 0 | 0 | 0
b | Actuator with required torque to open / close the damper with required control mechanism (both hardware & software), cabling. The actuator is capable to communicate with Building Management System.
| The actuator shall be suitable for outdoor installation when installed externally. | Nos. | 0 | 0 | 0 | 8540 | 1200 | 9740 | 0 | 0 | 0
4.8 | FIRE DAMPERS
a | UL Approved 180 minutes Fire damper with shaft extension to suit factory fitted actuator with 400 mm long GSS sleeve with 30 mm TDF flanges. The leakage class shall be class-1 with 3V blade construction.
The pressure drop across the dampers shall not exceed 1.5 mm of wg at 1500 fpm for the cross section area of 1 sqm.
| The rate quoted is inclusive of duct smoke detector | Sqm | 0 | 0 | 0 | 16280 | 2220 | 18500 | 0 | 0 | 0
b | UL Approved Spring loaded Actuator of required torque assembled in factory with required accessories to operate fire damper, step-down transformer, auxiliary switch, controller, necessary wiring & mounting arrangement. The actuator shall be equipped for 230V AC operation. The actuator also operates based on the input from BMS & pass on the status output to BMS and communicate to BMS System with an RS 485 port. | Nos. | 0 | 0 | 0 | 12760 | 1740 | 14500 | 0 | 0 | 0
a | Master Controller loop up to 8 Dampers | Nos | 0 | 0 | 0 | 15180 | 2070 | 17250 | 0 | 0 | 0
b | Master Controller loop up to 4 Dampers | Nos | 0 | 0 | 0 | 13420 | 1830 | 15250 | 0 | 0 | 0
c | Master Controller loop up to 2 Dampers | Nos | 0 | 0 | 0 | 13420 | 1830 | 15250 | 0 | 0 | 0
4.9 | FIRE DAMPER WITH FUSIBLE LINK
a | 90 minutes Fire damper with 400 mm long GSS sleeve with 30 mm deep TDF flanges. The leakage class shall be class-1 with 3V blade construction.
| The pressure drop across the dampers shall not exceed 1.5 mm of wg at 1500 fpm for the cross section area of 1 sqm. | Sqm | 0 | 0 | 0 | 9856 | 1344 | 11200 | 0 | 0 | 0
b | Fusible link with linkage, spring and operating handle | Nos. | 0 | 0 | 0 | 836 | 114 | 950 | 0 | 0 | 0
5 | AIR TERMINALS
5.1 | SUPPLY AIR DIFFUSERS
Powder coated, extruded aluminium, removable centre core type, supply air diffusers of following neck sizes to be installed in gypsum or grid false ceiling. The price includes necessary factory fabricated GI acoustically treated plenum boxes with side entry collars with required contour (groove) to hold the clamp & flexible duct.
The noise from the diffuser will not be more than 36 dba.
The diffuser shall be supported at all four corners using chain links.
a | 375 x 375 mm neck size, 595 x 595 mm outer size, Tegular type (up to 400 cfm) | Nos. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
b | 375 x 375 mm neck size, 595 x 595 mm outer size, Tegular type (up to 300 cfm) plaque type | Nos. | 0 | 0 | 0 | 3100 | 415 | 3515 | 0 | 0 | 0
c | 450 x 450 mm neck size, 595 x 595 mm outer size, Tegular type (up to 450 cfm) plaque type | Nos. | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
d | 300 mm dia Round Diffuser (up to 300 cfm) with collar damper. | Nos. | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
e | 400 mm dia Round Diffuser (up to 450 cfm) with collar damper. | Nos. | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
5.2 | RETURN AIR DIFFUSERS
Powder coated, extruded aluminium, removable centre core type, return air diffusers of following neck sizes to be installed in gypsum or grid false ceiling.
The diffuser is supported at all four corners using chain links.
a | 375 x 375 mm neck size, 595 x 595 mm outer size, Tegular type (up to 400 cfm) | Nos. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
b | 375 x 375 mm neck size, 595 x 595 mm outer size, Tegular type (up to 300 cfm) plaque type | Nos. | 0 | 0 | 0 | 1230 | 200 | 1430 | 0 | 0 | 0
c | 450 x 450 mm neck size, 595 x 595 mm outer size, Tegular type (up to 450 cfm) plaque type | Nos. | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
d | 400 mm dia Round Diffuser (up to 450 cfm) | Nos. | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
e | 295 x 1195 mm outer size, Tegular type (up to 400 cfm) | Nos. | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
6 | GRILLES
6.1 | CONTINUOUS GRILLES
Powder coated Extruded aluminium continuous grilles with 25 mm wide & 18 mm deep frame, 5 mm thick blades spaced at a distance of 12.5 mm.
The rate quoted include the cost of supporting arrangement.
a | 150 mm | M | 0 | 0 | 0 | 880 | 120 | 1000 | 0 | 0 | 0
b | 100 mm | M | 0 | 0 | 0 | 750 | 120 | 870 | 0 | 0 | 0
6.2 | RETURN AIR GRILLE
| Return Air Grille without collar damper and plenum box to collect return air from the space | Sqm | 33 | 23 | 56 | 5020 | 700 | 5720 | 281120 | 39200 | 320320
6.3 | CURVED GRILLES
Curved Grilles suitable for fixing in Sprial ducts, the grille surface radius shall be as per duct radius.
| The rate quoted shall includes the cost of splitters (guide veins), dampers etc., | Sqm | 0 | 0 | 0 | 15180 | 2070 | 17250 | 0 | 0 | 0
6.4 | AIR TERMINATION BOX FOR CONTINUOUS GRILLE
Air temination box fabricated out of 0.63 mm thick galvanized sheet with comb type collar damper to ensure zero leak at all four sides of box & grille termination.
The Supply Air Termination Box is acoustically treated with 6 mm thick open cell nitrile rubber.
The noise from the grille should not be more than 36 dba.
| The termination box is supported at all four corners using chain links. (the area furnished is cross section area of grille) | Sqm. | 0 | 0 | 0 | 4230 | 600 | 4830 | 0 | 0 | 0
6.5 | DISCRETE GRILLE
Powder coated Extruded aluminium Discrete grilles with 25 mm wide & 18 mm deep frame on all four sides, 5 mm thick blades spaced at a distance of 12.5 mm, the blade angle is as per detail engineering. The price includes necessary Shoe tapping, multiple guide vanes, collar damper with blade adjustable from face of the grille.
| The noise from the grille should not be more than 36 dba. | Sqm. | 10 | 0 | 10 | 11880 | 1620 | 13500 | 118800 | 16200 | 135000
6.6 | Spec same as above, but size of 600 x 600 suitable to fix in false ceiling. | Nos. | 0 | 0 | 0 | 4950 | 675 | 5625 | 0 | 0 | 0
7 | SLOT DIFFUSER
Powder coated extruded aluminium continuous slot diffusers suitable for fixing in false ceiling working in conjuction with Variable Air Volume Units complete with end cap, hit & miss damper, slide in flanges. All the visible surfaces are powder coated to the required colour. The price includes necessary factory fabricated GI plenum boxes with side entry collars with required contour (groove) to hold the clamp & flexible duct.
The Supply Air Termination Box shall be acoustically treated with 6 mm thick open cell nitrile rubber.
The noise from the grille should not be more than 36 dba.
The termination box is supported at all four corners using chain links.
a | 3 Slot Linear diffuser | M | 0 | 0 | 0 | 2640 | 360 | 3000 | 0 | 0 | 0
b | 1 m wide insulated Supply air terminal with required dampers | Nos. | 0 | 0 | 0 | 1050 | 150 | 1200 | 0 | 0 | 0
8 | TOILET DISC VALVE
Powder coated, aluminium Exhaust Disc Valve with four piece construction, rotatable plate to control the air volume, supporting arrangement etc. The price includes necessary factory fabricated GI plenum boxes with side entry collars with required contour (groove) to hold the clamp & flexible duct.
The Disc Valve is supported at diagonally opposite two corners using chain links.
a | 150 mm dia, 75 cfm | Nos. | 0 | 0 | 0 | 925 | 130 | 1055 | 0 | 0 | 0
9 | EXTERNAL WALL LOUVERS
| Extruded aluminium aerofoil blade rain protection louvers installed on external wall opening on the roof for OA intake & exhaust. | Sqm. | 0 | 0 | 0 | 8350 | 1150 | 9500 | 0 | 0 | 0
10 | INSULATION & ACOUSTICS
10.1 | DUCT INSULATION
UL Class O rated /FM Global approved, Thermal insulation for duct insulation (Both Internal & External) using non-fibrous, CFC free, closed cell, elostomeric nitrile rubber foamed insulation in pre-formed sheets with thermal conductivity of not more than 0.035 W/(m.k) at 0°C. Insulation is fire rated and high resistant to water absorption. The material used are in rolls. The insulation sheet joints shall be sealed using self adhesive black tapes of 3 mm thick & 50 mm width.
The adhesive shall be with low VOC contents & fire rated.
The contractor should clean the surface of the duct before laying the Thermal Insulation.
The adhesive & the black tape to be supplied by the insulation manufacturer only.
The adhesive shall be with low VOC contents & Class 'O' fire rated.
The adhesive to be supplied by the acoustic manufacturer only.
The adhesive shall be with low VOC contents & Class 'O' fire rated.
Glass cloth of approved color supplied by insullation manufacturer
a | 32 mm thick insulation | Sqm. | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
b | 25 mm thick insulation | Sqm. | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
c | 15 mm thick insulation for outside air | Sqm. | 0 | 0 | 0 | 450 | 50 | 500 | 0 | 0 | 0
d | 10 / 12 mm thick insulation Lining internal / external | Sqm. | 0 | 0 | 0 | 450 | 100 | 550 | 0 | 0 | 0
e | Mechanical protection by heavy duty and ultra tough multi-layered composite aluminium foil with puncture resistance of >400N as per ASTM D4833 | Sqm | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
f | Glass cloth of approved color supplied by insullation manufacturer | Sqm. | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
10.2 | ACOUSTIC LINING FOR DUCTS
UL Class I rated Acoustic Lining for ducting using non-fibrous, CFC free, open cell, elostomeric nitrile rubber foamed insulation in pre-formed sheets with sound absorption. Acoustic lining is fire rated and high resistant to water absorption. The material used are in rolls. The acoustic lining shall be stuck to the inner surface of the duct and revetted at regular interval of not more than 200 mm.
The adhesive shall be with low VOC contents & fire rated.
| 10 / 12 mm thick Acoustic Lining | Sqm. | 0 | 0 | 0 | 400 | 50 | 450 | 0 | 0 | 0
10.3 | ACOUSTIC LINING FOR AHU ROOMS
Acoustic Lining for Walls of AHU Rooms using non-fibrous, CFC free, open cell, elostomeric nitrile rubber foamed insulation in pre-formed sheets with sound absorption . Class 1 fire rated, high resistant to water absorption. The material used shall be in rolls. The acoustic lining shall be sticked to the inner surface of the AHU Room Wall within the euqally sized grid of not more than 900 x 900 mm fabricated using 3 mm thick smooth cornered aluminium strips.
The contractor should clean the surface of the AHU Room Wall before sticking the Acoustic Lining.
The adhesive to be supplied by the acoustic manufacturer only.
The adhesive shall be with low VOC contents & Class 'O' fire rated
The acoustic lining should be FM global approved.
a | 19 / 20 mm thick Acoustic Lining | Sqm. | 0 | 0 | 0 | 5000 | 500 | 5500 | 0 | 0 | 0
10.4 | CROSS-TALK ATTENUATORS
Cross-talk attenuators fabricated out of high density glasswool panel with outer surface consisting of aluminum + reinforced glass fibre mesh + kraft. The glasswool is not health hazardous and is fire rated, baffle to be provided internally for the total length of the Attenuator.
The Cross-talk attenuator should be in 'Z' shape
The true length of the attenuator should not be less than 1.5 m.
The Cross-Talk Attenuator shall be supported at all four corners using chain links.
a | 300mm x 300 mm | Nos. | 2 | 2 | 4 | 5000 | 800 | 5800 | 20000 | 3200 | 23200
b | 600 mm x 300 mm | Nos. | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
11 | SUPPLY & RETURN AIR DUCT SILENSORS
Silencers made out of GSS steel with duct mounted absorbent splitters arranged with air-flow passages between them, acoustic fills of density not less than 48 Kg/cum covered with RP tissue & protected with 26 gauge perforated aluminium sheets. The splitters have smooth entry & exit nose to minimize pressure drop, complete with heavy duty termination, 30 mm deep TDF flanges. The joints are sealed using duct sealing compound. The silencers are supported from the supporting from ceiling.
| The pressure drop across the dampers shall not exceed 2.5 mm of wg at 1500 fpm for the cross section area of 1 sqm. | Cum | 0 | 0 | 0 | 30000 | 3000 | 33000 | 0 | 0 | 0
12 | UNDERDECK INSULATION
Insulation for the underdeck of the exposed slab using non-fibrous, CFC free, closed cell, elastomeric nitrile rubber foamed insulation in pre-formed sheets with thermal conductivity of not more than 0.035 W/(m.k) at 0°C. Insulation is fire rated, high resistant to water absorption. The material used are in rolls. FM global approved.
The adhesive shall be with low VOC contents & fire rated
a | 9/10 mm thick insulation | Sqm | 0 | 0 | 0 | 400 | 50 | 450 | 0 | 0 | 0
13 | WALL MOUNTD PROPELLER FAN
Industrial purpose exhaust fan with back draught shutter, low noise wall mounted, easy maintenance suitable for industry. The rate quoted shall also include cabling between the fan and power socket provided adjacent to the fan by other agencies.
a | 500 CFM | Nos. | 0 | 0 | 0 | 5000 | 500 | 5500 | 0 | 0 | 0
b | 1000 CFM | Nos. | 0 | 0 | 0 | 8000 | 500 | 8500 | 0 | 0 | 0
| TOTAL | [7 empty] | 1230920 | 183100 | 1414020

## Additional work
HVAC WORKS FOR MORGAN STANLEY CO-WRKS
CLIENT | : MORGAN STANLEY
ARCHITECTS | : CO-WRKS
PMC | :
DATE / REV NO. | : 09.03.2026 / R1
CONSULTANTS | : E SOLLUTIONS
SUBJECT | : Additional Works
SL. NO. | DESCRIPTION | UNIT | QTY |  | TOTAL QTY | RATE IN INR |  |  | AMOUNT IN INR
|  |  | L1 | L2 |  | SUPPLY | INSTALLATION | TOTAL | SUPPLY | INSTALLATION | TOTAL
The contractor / vendor should read the specifications thoroughly and quote the price for each item. The BOQ should read in-conjunction with specification, drawing & equipment schedule. The cost shall include the cost of the material, transportation, taxes, duties, lifting, shifting, storing, handling, installation, testing and commissioning.All the items should be with performance guarantee of minimum 1 year.
1 | Modification works as per site condition to match the proposed requirement.
Dismantling & Dumping / handing over of duct, Grilles, VAV within the campus as shown by Clients. Additional modification works needs to be considered here.
Inlcuding required Air balancing activity.
| The vendors should study the site condition & quantify the amount of work before furnishing the commercial offer. | Lot | 1 | 1 | 2 |  |  | 40000 | 0 | 0 | 80000
Air balancing of Existing system after compleation of proposed modification works & Recalibration of VAV modified area served VAV
| The vendors should study the site condition & quantify the amount of work before furnishing the commercial offer. | No | 1 | 0 | 1 |  |  | 10000 | 0 | 0 | 10000
[9 empty] | 0 | 0 | 90000