## Gerenal Notes
GENERAL NOTES
1 | The items given in this schedule are provisional. The Tenderer shall be paid for the actual quantity of work executed as measured at the site at the rates tendered. The Client reserves the right to increase or decrease any of the quantities, or to ommit totally any item of work. Any claim by the Tenderer on these accounts will not be entertained.
2 | All the items of work given in this schedule of quantities shall be executed strictly in accordance with the latest Indian Standard Specifications and the requirements of the Electricity Supply Authority read in conjunction with the relevant drawings and Specifications.
3 | The Tenderer shall visit the site and shall satisfy himself as to the conditions under which the work is to be performed. He shall also check and ascertain the location of any existing structure or equipment or any other situation which may affect the work. No extra claim as a consequence of ignorance or on ground of insufficient description will be allowed at a later date.
4 | All equipment and material shall be IS approved.
5 | All approvals shall be obtained from Client / Consultant
6 | All equipment and material shall be inspected at manufacturer’s works as per relevant IS by the Client or his representative before despatch to site.
7 | All vendor drawings shall be approved by the Client /Consultant before fabrication work starts.
8 | All Testing and Commissioning shall be as per relevant IS for equipment and S:732:1999 and amendanent upto date, for the installation. All testing records are to be maintained and submitted for Client’s representative. The rate shall include the wastage on material & Labour..
9 | No alteration whatsoever is to be made to the text or quantities of this Schedule unless such alteration is authorised in writing by Services Consultant or Client. Any such alterations, notes or additions shall, unless authorized in writing, be disregarded when tender documents are considered.
10 | In the event of an error occurring in the amount of the Schedule, as a result of wrong extension of the unit rate and quantity, the unit rate quoted by the tenderer shall be regarded as firm and the extensions shall be amended on the basis of rates.
11 | Any error in totaling in the amount column and in carrying forward total shall be corrected. Any error, in description or in quantity, omission of items from this Schedule shall not vitiate this Contract but shall be corrected and deemed to be variation required by the Services Consultant/Project Manager.
A. | CIRCUIT CUM POINT WIRING
The rates for all point wiring items shall also include supplying and fixing of the following:
1 | Conduits, conduit specials, brass bushes and other fittings.
2 | Approved GI saddles and grouting the same for exposed conduit work.
3 | 1.2 mm thick Outlet boxes and junction box.
4 | All fixing accessories such as clips, brass screws etc.
5 | All work necessary for wiring a point circuit of any length from the Final Distribution Board to connector via switch and shall include the circuit wiring also except where identified.
6 | Embedding conduits and accessories in walls and floors etc. during construction and / or cutting chases (with chase cutting machine) and making good the same as necessary in the case of concealed conduit work.
7 | Switch, socket outlet and necessary blank plates wherever required.
8 | FRLS copper conductor stranded flexible FRLS wire of Green colour or Green colour with yellow band for earthing of fixtures, outlet boxes and third pin of socket outlet.
9 | Repainting of outlet boxes and juction boxes where ever damaged.
10 | All wires shall be IS approved, 1100 volt grade, stranded flexible FRLS.
11 | All sockets shall be shuttered type with earth terminal.
12 | Suitable rating of plugs top shall also be provided within the quoted rates for all metal clad splash proof socket outlets.
13 | Separate neutral and earthing wire shall be provided for each circuit.
14 | Lighting and power circuit to be kept separate.

## SUMMARY
INTERNAL ELECTRICAL WORKS, KSM 66 OFFICE, HYDERABAD
S. No. | Description | Amount (In Rupees)
A | CIRCUIT CUM POINT WIRING | 0
B | CABLES & CABLE TRAYS | 0
C | FINAL DISTRIBUTION BOARDS | 0
D | UPS SYSTEM | 0
E | EARTHING SYSTEM | 0
F | LIGHTNING PROTECTION SYSTEM | 0
G | INSTALLATION OF EXTERNAL/ LANDSCAPE LIGHTING | 0
H | ELECTRIC VEHICLE CHARGER | 0
I | HV INSTALLATION | 0
J | SUPPLY & INSTALLATION OF LT PANELS | 0
K | EXTERNAL PIPE WORK | 0
| TOTAL | 0
Exclusion
1 | Supply of external light fixtures
2 | Supply of Internal lighting fixtures
3 | Elevators
4 | eLV/ CCTV/ ACS / AV system
5 | Civil work

## ELECT BOQ
DETAILED BOQ FOR INTERNAL ELECTRICAL WORKS
S. No. | Description | Unit | Qty. | Rate | Amount
1 | INTERNAL ELECTRICAL WORK
A | CIRCUIT CUM POINT WIRING
1 | Wiring for the following light/ceiling fan/exhaust fan points with 1.5 sq.mm (including circuit wiring) PVC insulated FRLS copper conductor 1100 volts grade stranded flexible wires of approved make in concealed/ surface 25 mm dia heavy duty PVC conduit including providing and fixing of 6 amps single pole rocker operated flush mounted modular switch of approved quality, colour, make and design in 1.2 mm thick GI box and earthing of fixtures and the outlet box with 1.5 sq.mm PVC insulated FRLS copper conductor stranded flexible wire.
a | Primary points | Pts | 30 |  | 0
b | Loop points | Pts | 10 |  | 0
0
2 | Wiring for the following dimmer module controlled light points with 1.5 sq.mm (including circuit wiring) PVC insulated FRLS copper conductor 1100 volts grade stranded flexible wires of approved make in concealed/surface FRLS heavy duty PVC conduit with approved quality, colour, make and design and earthing of fixtures 1.5 sq.mm PVC insulated FRLS copper conductor stranded flexible wire. (Includes DALI and analogue circuits) | Pts | RO
0
3 | Wiring for following 250 volts single phase and neutral 20 amps switched socket outlet and one light point (bulkhead) for lift shafts with 4 sq.mm PVC insulated FRLS copper conductor 1100 volts grade stranded flexible wires in concealed 25 mm dia stove enamled black MS conduit including providing and fixing of 16 amps 3 pin switched socket of approved make and design in 1.2 mm thick GI boxes with grid plates and earthing of third pin of socket outlet and GI box with 4 sq.mm PVC insulated FRLS copper conductor stranded flexible wire for following sets(point for lift shaft): (Cost of MCB/ bulk head light fixture not to be included) |  |  |  | 0
a | Three sets of above controlled by one 20 A SP MCB in DB | Pts. | 2 |  | 0
b | Four sets of above controlled by one 20 A SP MCB in DB | Pts. | 2 |  | 0
0
4 | Wiring for light point as in item No. A-1 above but controlled by SPMCB provided in the DB. (Cost of MCB not to be included here). |  |  |  | 0
a | Primary points | Pts | 30 |  | 0
b | Loop points | Pts | 300 |  | 0
0
5 | Wiring for the twin control light points with 1.5 sq. mm PVC insulated FRLS copper conductor 1100 volts grade stranded flexible wires in concealed 25mm dia heavy duty PVC conduit including providing and fixing 2 No. 6 amps 2 way rocker operated flush mounted modular switches of approved quality & colour make and design in 1.2 mm thick GI box and earthing of fixture & the outlet box with 1.5 Sq.mm PVC insulated FRLS copper conductor stranded flexible wire. |  |  |  | 0
a | Primary point | Pts. | RO
b | Loop point | Pts. | RO
0
6 | Wiring for 250 volt single phase and neutral 6 amps switch socket outlet with 2.5 sq.mm PVC insulated FRLS copper conductor 1100 volts grade stranded flexible wires in concealed/ surface 25 (including circuit wiring) mm dia heavy duty PVC conduit, including providing and fixing of 6 amps 3 pin switched socket of approved make colour and design in 1.2 mm thick GI box with grid plate and earthing of third pin of the socket outlet and the GI box with 2.5 Sq.mm FRLS copper conductor stranded flexible wire. | Pts. | 90 |  | 0
0
7 | Wiring for 250 volt single phase and neutral 6/13 amps universal switch socket outlet with 2.5 sq.mm PVC insulated FRLS copper conductor 1100 volts grade stranded flexible wires in concealed/ surface 25 (including circuit wiring) mm dia heavy duty PVC conduit, including providing and fixing of 6 amps 3 pin switched socket of approved make colour and design in 1.2 mm thick GI box with grid plate and earthing of third pin of the socket outlet and the GI box with 2.5 Sq.mm FRLS copper conductor stranded flexible wire. | Pts. | 275 |  | 0
0
8 | Wiring for 250 volts single phase and neutral 6/16 amps switched socket outlet with 4 sq.mm (including circuit wiring) PVC insulated FRLS copper conductor 1100 volts grade stranded flexible wires in concealed/ surface 25 mm dia heavy duty PVC conduit, including providing and fixing of 6/16 amps 5 pin switched socket of approved make and design in 1.2 mm thick GI boxes with grid plates and earthing the third pin of socket outlet with 2.5 Sq. mm PVC insulated FRLS copper conductor stranded flexible wire. | Pts. | 26 |  | 0
0
9 | Wiring for 250 volts single phase and neutral 6/16 amps weather proof switched socket outlet with 4 sq.mm (including circuit wiring) PVC insulated FRLS copper conductor 1100 volts grade stranded flexible wires in concealed/ surface 25 mm dia heavy duty PVC conduit, including providing and fixing of 6/16 amps 5 pin switched socket of approved make and design in 1.2 mm thick GI boxes with grid plates and earthing the third pin of socket outlet with 2.5 Sq. mm PVC insulated FRLS copper conductor stranded flexible wire. | Pts. | 2 |  | 0
0
10 | Wiring for 250 volts single phase and neutral 16 amps switched socket outlet with 4 sq.mm (including circuit wiring) PVC insulated FRLS copper conductor 1100 volts grade stranded flexible wires in concealed/ surface 25 mm dia heavy duty PVC conduit, including providing and fixing of 16 amps 3 pin switched socket of approved make and design in 1.2 mm thick GI boxes with grid plates and earthing the third pin of socket outlet with 2.54 Sq. mm PVC insulated FRLS copper conductor stranded flexible wire. Switch to be installed at +1050mm FFL and socket to be provided at +2200mm FFL. (For AC Split unit) | Pts. | 2 |  | 0
0
11 | Wiring for 250 volts single phase and neutral 16 amps switched socket outlet with 4 sq.mm (including circuit wiring) PVC insulated FRLS copper conductor 1100 volts grade stranded flexible wires in concealed/ surface 25 mm dia heavy duty PVC conduit, including providing and fixing of 16 amps 3 pin switched socket of approved make and design in 1.2 mm thick GI boxes with grid plates and earthing the third pin of socket outlet with 2.5 Sq. mm PVC insulated FRLS copper conductor stranded flexible wire. . | Pts. | 38 |  | 0
0
12 | Wiring for 250 volts single phase and neutral 20 amps Industrial type polycarbonate switched socket outlet with 4 sq.mm (including circuit wiring) PVC insulated FRLS copper conductor 1100 volts grade stranded flexible wires in concealed/ surface 25 mm dia heavy duty PVC conduit/ cable tray/ raceway, including providing and fixing of 20 amps 3pin switched socket of approved make and design in 1.2 mm thick GI boxes with grid plates and earthing the third pin of socket outlet with 2.5 Sq. mm PVC insulated FRLS copper conductor stranded flexible wire. (For EV charger for 2 wheelers) | Pts. | 7 |  | 0
0
13 | Wiring for 250 volts single phase and neutral 25 amps Industrial type polycarbonate switched socket outlet with 6 sq.mm (including circuit wiring) PVC insulated FRLS copper conductor 1100 volts grade stranded flexible wires in concealed/ surface 25 (including circuit wiring) mm dia heavy duty PVC conduit, including providing and fixing of 25 amps 3pin switched socket of approved make and design in 1.2 mm thick GI boxes with grid plates and earthing the third pin of socket outlet with 4 Sq. mm PVC insulated FRLS copper conductor stranded flexible wire. (For IT main Server Rack) | Pts. | 4 |  | 0
0
14 | Supply, installation, testing and commissioning of following PVC insulated FRLS copper conductor 1100 volt grade stranded flexible wire in heavy duty PVC conduit for circuit wiring including providing and fixing of conduits concealed or surface mounted including green colour with yellow band copper wire for earthing and making connections complete. (Submain/Circuit wiring required other than the items mentioned in BOQ) |  |  |  | 0
a | 2 X 1.5 sq. mm + 1 X 1.5 sq. mm earth wire | RM | RO
b | 2 X 2.5 sq. mm + 1 X 1.5sq. mm earth wire | RM | RO
c | 2 X 4 sq. mm + 1 X 2.5sq. mm earth wire | RM | 150 |  | 0
d | 2 X 6 sq. mm + 1 X 4 sq. mm earth wire | RM | RO
e | 4 X 6 sq. mm + 2 X 4sq. mm earth wire | RM | RO
0
15 | Supply, installation, testing and commissioning of surface/pendant mounted motion sensor along with suitable mounting accessories, IP20 with a 360 degree detection pattern and detection area of 7m at a mounting height of 2.8m. The sensor shall work on advanced sensing Technology with adjustable off delay timing of 1-90min through IR remote. It shall be suitable for maximum system load of 10A and supply voltage 230V AC±10%, 50 Hz having facility to by-pass the auto switch system and operate mannualy with necessary sensor control wiring. | Nos. | RO
0
16 | Supplying & installation of following MCB/ RCCB's in polycarbonate encloser, IP 20 with ON indication lamp :- |  |  |  | 0
a | 63A FP RCCB For Lift | Nos. | 2 |  | 0
0
17 | Providing and fixing in position the following heavy duty PVC conduit concealed or exposed as called for including all accessories i.e bends, junction boxes, outlet boxes with cover plates of approved make and design. |  |  |  | 0
a | 20mm dia PVC conduit | RM | RO
b | 25mm dia PVC conduit | RM | RO
c | 32mm dia PVC conduit | RM | RO
0
18 | Supply, laying & testing of following PVC flexible conduit to drop down the circuit in false ceiling areas (For Light circuits) |  |  |  | 0
a | 20mm dia | RM | RO
b | 25mm dia | RM | 600 |  | 0
0
19 | Supplying and fixing modular blanking plate on the existing modular plate & switch box excluding modular plate as required. | Nos. | 5 |  | 0
0
20 | Supply and fixing 3pin, 5 amp ceiling rose on the existing junction box/ wooden block including connection etc. as required for exhaust fan. | Nos. | RO
0
21 | S/F Modular Type Electronic Fan Regulator : Supplying and fixing stepped type, 2 module electronic fan regulator on the existing modular plate & switch box including connections but excluding modular plate etc. as required. | Nos. | 1 |  | 0
0
22 | Ceiling Fan : Supplying of BLDC technology based 1200 mm sweep ceiling fan complete with blades, shakle, hanging rod etc. with high breeze, low speed for operation on 230V, 50 Cy, low power consumption , low noise and in-built AC to DC supply converter from approved make in colour as per interior designer. Single phase A.C. supply confirming to IS 374-1979. The fan shall be star rated with 5 star as per BEE norms. (Contractor shall submit the fan models for approval to client before procurement) | Nos. | 1 |  | 0
| TOTAL CARRIED OVER TO SUMMARY |  |  |  | 0
B | CABLES & CABLE TRAYS
The rate shall also include the following :
1 | Providing and fixing junction boxes with covers including painting where ever required.
2 | Providing all fixing accessories such as clAing devices nuts, bolts and screws.
3 | Wherever the cables are of aluminium and bus bars of copper bimetallic lugs shall be used.
4 | All cable shall be laid with one diameter gap.
5 | All cables shall be IS approved.
6 | Double compression glands with earthing provision.
7 | Fire retardent paint one meter on both side of wall penetration and at termination as per specifications.
8 | Burried LT cables to be laid atleast 750 mm below ground.
Cables and Cable Trays
1 | Supply & laying of following 1100 volt grade XLPE FRLS inner sheathed PVC aluminium/copper conductor armoured cables (Confirming To IS:7098 Part-I) as per specification in existing trenches, cable trays, ducts, over bed of sand, clad to wall with suitable clamp including, saddles fixing bolts, connecting testing and commissioning.
a | 3.5 Core 300 sq. mm | meter | 275 |  | 0
b | 3.5 Core 185 sq. mm | meter | 175 |  | 0
c | 3.5 Core 150 sq. mm | meter | RO
d | 3.5 Core 50 sq. mm | meter | 60 |  | 0
e | 3.5 Core 35 sq. mm | meter | 215 |  | 0
f | 4 Core 25 sq. mm | meter | 70 |  | 0
g | 4 Core 16 sq. mm | meter | 650 |  | 0
h | 4 Core 10 sq. mm (Cu cable) | meter | 300 |  | 0
i | 4 Core 6 sq. mm (Cu cable) | meter | 575 |  | 0
j | 4 Core 4 sq. mm (Cu cable) | meter | 215 |  | 0
0
2 | Supply & laying of following 1100 volt grade XLPE sheathed copper conductor multi-strand flexible confirming to IS 694 unarmoured cable as per specification in existing trenches, cable trays ducts over bed of sand, clad to wall with suitable clamp, including fixing bolts, connecting testing and commissioning. |  |  |  | 0
a | 1 core 70 sq.mm copper cable | meter | 300 |  | 0
b | 4 core 6 sq.mm copper cable | meter | 300 |  | 0
c | 3 core 6 sq.mm copper cable | meter | 350 |  | 0
0
3 | Cable end termination of the following XLPE aluminium/copper conductor armoured/Unarmoured cables of 1100 volt grade including supplying and fixing of bimettalic crimping lugs, double compression glands with earthing. |  |  |  | 0
a | 3.5 Core 300 sq. mm | Each | 12 |  | 0
b | 3.5 Core 185 sq. mm | Each | 4 |  | 0
c | 3.5 Core 150 sq. mm | Each | RO
d | 3.5 Core 50 sq. mm | Each | 2 |  | 0
e | 3.5 Core 35 sq. mm | Each | 10 |  | 0
f | 4 Core 25 sq. mm | Each | 2 |  | 0
g | 4 Core 16 sq. mm | Each | 16 |  | 0
h | 4 Core 10 sq. mm (Cu cable) | Each | 12 |  | 0
i | 4 Core 6 sq. mm (Cu cable) | Each | 26 |  | 0
j | 4 Core 4 sq. mm (Cu cable) | Each | 10 |  | 0
k | 1 core 70 sq.mm copper cable (With PVC Glands) | Each | 20 |  | 0
l | 4 core 6 sq.mm copper cable (With PVC Glands) | Each | 20 |  | 0
m | 3 core 6 sq.mm copper cable (With PVC Glands) | Each | 14 |  | 0
0
4 | Supply and fixing of Hot dipped perforated type G.I. cable trays of the following sizes including providing suitable angle suspenders at 1800 mm C/C as per specifications. |  |  |  | 0
a | 1000 mm x 50 x 50 x 2 mm thick | meter | 15 |  | 0
b | 750 mm x 50 x 50 x 2 mm thick | meter | 30 |  | 0
c | 600 mm x 50 x 50 x 2 mm thick | meter | RO
d | 450 mm x 40 x 40 x 1.6 mm thick | meter | 5 |  | 0
e | 300 mm x 40 x 40 x 1.6 mm thick | meter | 30 |  | 0
f | 150 mm x 40 x 40 x 1.6 mm thick | meter | 150 |  | 0
g | 150 mm x 40 x 40 x 1.6 mm thick with top cover on boundary wall | meter | 150 |  | 0
0
0
5 | Design, manufacturing, supply and installation of overhead raceways made from 1.6mm thick G.I. sheet in following size complete with suitable knockouts, suspended rods / angle iron, reducer, 1.6 mm thick removable top cover and cable holding arrangement commplete for installationas required: |  |  |  | 0
a | 300mm x 40mm x 1.6 thick with one compartments. | meter | 50 |  | 0
b | 150mm x 40mm x 1.6 thick with one compartments. | meter | 155 |  | 0
c | 100mm x 40mm x 1.6 thick with one compartments. | meter | 20 |  | 0
0
6 | Design, manufacturing, supply and installation of pre-galvalized floor raceways made from 2.0mm thick G.I. sheet in following size for industrial power outlet wiring, tele, data, etc complete with inlcuding junction boxes suitable knockouts, junction box, tap off points, reducer, removable top cover, coupler plate and cable holding arrangement : |  |  |  | 0
a | 150mm x 35mm x 2.0 mm with 3 mm top cover | meter | 230 |  | 0
b | 100mm x 35mm x 2.0 mm with 3 mm top cover | meter | 20 |  | 0
0
0
7 | Supplying and fixing of cable tags made out of aluminum anodized plate of size 90mm × 20 mm , tag to be fixed at both ends of the cable , stating cable size and Source to Termination point in form of From & To | Nos. | RO
Notes-
The Contractor has to draw exact routing of tray and raceway on the layout and got approved the same before going for fabrication. A sample of the same has to be hanged on the site with all necessary support. Cold Rolled process has to be adopted for Galvanization.
| TOTAL CARRIED OVER TO SUMMARY |  |  |  | 0
C | FINAL DISTRIBUTION BOARDS
Supply, installation, testing and commissioning of the following FDB's fabricated out of 1.2 mm thick CRCA sheet steel, double door & IP-43 construction, powder coated with approved shade and partitions to segregate phases. Approved lockable covers with padlocking arrangement for each phase, recessed in wall or surface mounted final distribution boards of the following description: All MCB should be 10KA breaking capacity. Copper bus bars, Neutral & Earth Links and all required accessories for interconnection.
| Note:- The contractor shall add space for DP RCCB provided in each phase as extra other than MCBs and not to be counted in Outgoing ways. For example, the outgoings mentioned as 10way shall give 10 nos. of used MCB outputs only excluding DP RCCB. |  |  |  | 0
| LIGHT & POWER DB |  |  |  | 0
0
1 | Type A |  |  |  | 0
| 12 way TPN DB, 12 Nos. 10/16/20 A SP MCB’s per phase with 3 Nos. 63 A DP RCCB’s of 100 mA leakage current and 1 No. 63 A 4 pole MCB as incomer with separate neutral link for each phase. | Nos. | 7 |  | 0
0
2 | Type B |  |  |  | 0
| 8 way TPN DB, 8 Nos. 10/16/20 A SP MCB’s per phase with 3 Nos. 63 A DP RCCB’s of 100 mA leakage current and 1 No. 63 A 4 pole MCB as incomer with separate neutral link for each phase. | Nos. | RO
0
3 | Type C |  |  |  | 0
| 8 way TPN DB, 8 Nos. 10/16/20 A SP MCB’s per phase with 3 Nos. 32 A DP RCCB’s of 100 mA leakage current and 1 No. 32 A 4 pole MCB as incomer with separate neutral link for each phase. (UDB 1st to 3rd floor) | Nos. | 3 |  | 0
0
5 | Type D |  |  |  | 0
| 6 way TPN DB, 6 Nos. 10/16/20 A SP MCB’s per phase with 3 Nos. 25 A DP RCCB’s of 100 mA leakage current and 1 No. 25 A 4 pole MCB as incomer with separate neutral link for each phase. (UDB Basement, LGF, UGF) | Nos. | 3 |  | 0
| TOTAL CARRIED OVER TO SUMMARY |  |  |  | 0
D | UPS SYSTEM
Supply, Transportation, storing at site, shifting at work place, installation, Testing and commissioning of the following rating UPS as per specifications and complete in all respects. The scope also includes supply, Installation, Testing and Commissioning of Sealed Maintenance Free lead acid Batteries complete with intercell connectors & copper cables, Battery breaker, battery stand made out of Powder Coated MS Angles with adequate supports to carry the load of the batteries & also TVSS at the input of each UPS to protect against transients, surges & Noise as per the tender specifications. UPS shall also have Modbus communication port. UPS shall also have parallel mode of operation in-built and RS485 port for BMS integartion
a | Supply, installation, Testing & commissioning of 70 kVA on line 415 V AC UPS with 15minutes balancing battery back up. | Nos. | 2 |  | 0
| TOTAL CARRIED OVER TO SUMMARY |  |  |  | 0
E | EARTHING SYSTEM
The rates for earthing items shall also include the following
1 | All fixing accessories such as brass, saddles, brass screws, rawl plugs etc.
2 | Jointing by rivetting and brazing after tinning.
3 | Cutting chases, holes and making good the same wherever required.
4 | Effecting adequate and proper interconnections.
5 | Use of copper thimbles.
6 | Excavation of earth, refilling, watering and ramming and making good as approved in all kinds of soil.
7 | All earthing pits shall be interconnected.
8 | Earthing shall be as per IS-3043-1987 |  |  |  | 0
0
| EARTHING INSTALLATION |  |  |  | 0
1 | Supplying and fixing of following bare copper / GI tapes including all necessary fixing accessories and effecting connections. |  |  |  | 0
a | GI Tape |  |  |  | 0
1.1 | 50 mm x 6 mm thick GI tape | RM | 220 |  | 0
1.2 | 40 mm x 10 mm thick GI tape | RM | 80 |  | 0
1.3 | 25 mm x 6 mm thick GI tape | RM | 250 |  | 0
1.4 | 25 mm x 3 mm thick GI tape | RM | RO
1.5 | 8 SWG sqmm GI conductor | RM | 120 |  | 0
0
b | Copper Tape |  |  |  | 0
1.1 | 32 mm x 6 mm thick | RM | 60 |  | 0
1.2 | 25 mm x 3 mm thick | RM | 300 |  | 0
1.3 | 25 mm x 3 mm thick | RM | 300 |  | 0
1.4 | 6sqmm copper conductor, PVC insulated flexible wire | RM | 240 |  | 0
0
2 | Supply, Installation, testing & commissioning of MS powder coated green coloured earthing box with tentative size 300mm x 300mm x 200mm having copper earth bus bar inside it mounted with insulation from box, having holes for connecting copper earth wires with suitable dia hardwares to terminate O type lugs including all necessary accessories to complete the work. (For Server) | Nos. | 3 |  | 0
0
3 | Low impendance chemical Gel earthing system |  |  |  | 0
| Supply, Installation, testing & commissioning of Low Impedence chemical GEL Earth pit sets and installation complete with consisting of 1 no. 3 meters long 17.2 mm dia MS Rod moleculerly bonded with 250 micron copper as per UL 467 and treated with 27 kgs (Minmum ) of Ground Enhancing compound as per IEEE 80 14.5 D per earth pit as per approved make. The Installation procedures should be followed as instructed by the Earth Electrode Supplier. One set of earth pit would consists of 1 No. of rod , 27 Kgs of earth enhancer Carbon / Graphite based earth enhancer compound and 1 no. of suitable Double side GI clamp. | Nos. | 34 |  | 0
| TOTAL CARRIED OVER TO SUMMARY |  |  |  | 0
F | LIGHTNING PROTECTION SYSTEM
Conventional Type system
Note: -The LA system shall be based on risk protection and is a specialized job. The specialized OEM/ vendor shall prepare his desgin & and BOQ and submit for consultant approval prior to procurement.
1 | Supply, installation, testing & commissioning of Vertical Aluminium Lighting Arrester of 16MM dia, 2000 mm long with Gun Metal base plate from approved make list. | Nos. | 2 |  | 0
0
2 | Supply, installation, testing & commissioning 8 mm round aluminium conductor for horizontal lightning protection - run in roof from approved make list. . | Mtr. | 200 |  | 0
0
3 | Supply, installation, testing & commissioning of roof conductor holder for 8 mm round aluminium conductor made of SS 304 for horizontal installation at the roof The distance between each holder should be min of 1 mtr to meet the requirements of IS/IEC 62305 & IEC 62561 2. | Nos. | 200 |  | 0
0
4 | Supply, installation, testing & commissioning of Cross connector for connecting of 8 mm Al round conductor . The connector should be of SS 304 with SS nuts and bolt to meet the requirements of IS/IEC 62305 & IEC 62561 2. | Nos. | 25 |  | 0
0
5 | Supply, installation, testing & commissioning of Expansion piece along with connector to compensate the expansion of round 8 mm Al conductor when temperature variation . Connection should be in every 20 mtr. | Nos. | 10 |  | 0
0
6 | Supply & fixing of GLUE- Glue is used to fix roof conductor holder on roof. | Nos. | 50 |  | 0
0
7 | DOWN CONDUCTOR & RING CONDUCTOR AS PER IEC 62305 |  |  |  | 0
8 | Supply, installation, testing & commissioning of 8 mm round aluminium conductor as a down conductor mounted in the surface of wall which will carry the lightning current to earth pit. | Mtr. | 300 |  | 0
0
9 | Supply, installation, testing & commissioning of Down conductor holder for 8 mm round aluminium conductor made SS 304 for horizontal installation. The distance between each holder should be min of 1 mtr to meet the requirements of IS/IEC 62305 & IEC 62561 2. | Nos. | 300 |  | 0
0
10 | Supply, installation, testing & commissioning of straight connector for connecting of 8 mm Al round conductor . The connector should be of Aluminium with SS nuts and bolt. | Nos. | 50 |  | 0
0
11 | Supply, installation, testing & commissioning of 7 digit lightning strike counter. | Nos. | 2 |  | 0
0
12 | Supply, installation, testing & commissioning of Test Joint Point for 25X3MM CU STRIP in ABS boxes. | Nos. | 6 |  | 0
0
13 | EARTHING AS PER IEC 62561- 2 & 7 |  |  |  | 0
14 | Supply, installation, testing & commissioning of advance chemical gel earthing system for the proper dissipation of fault / leakage current to the ground and ensure the continuous electrical connectivity and proper functioning to the electrical system. The earth rod shall be of UL listed & CPRI tested 3 meter long 17.2 mm dia 250 microns copper bonded steel rod with the connecting clamp (ss - rod to tape). The UL listed copper bonded rod also should be tested & ceritifed from CPRI for a short circuit current of 46 KA or more. The UL listing shall be punched / engraved on the rod for the physical verification at site. The engravings shall contain the following details - UL Control number, Dimension details of the rod, Product model number & UL certificate reference number as per detailed technical specification attached. To ensure the electrical conductivity, 50 Kgs (per pit) or more resistance grounding minerals per earth pit / earth rod shall be used along with the copper bonded rod. As per IEEE 80-2013 (Clause 14.5 d), the grounding minerals shall be tested & certified for the resistivity of less than 0.12 ohm-mtr. The grounding minerals should be ROHS certified to ensure it does not pollute the ground water as per technical specification attached. | Nos. | 8 |  | 0
0
15 | Supply, installation, testing & commissioning of 25X6MM GI STRIP : For earthing connections | Mtr. | 120 |  | 0
| TOTAL CARRIED OVER TO SUMMARY |  |  |  | 0
G | INSTALLATION OF EXTERNAL/ LANDSCAPE LIGHTING
Note: The final quantity & selection of Landscape/ external lighting shall be as per landscape consultant and shall be part of their BOQ. Presently, quantity is available for UGF/ 1st/ 2nd and 3rd floor landscape. No detail was available for ground landscape and the same is considered on assumption basis.
Rate for installation of fixtures shall also include the following :
1 | All component that may be required to make the installation complete in all respects, such as :
a. Suitable length of connecting wires.
b. Connecting wires to the point through connection block.
c. Bonding to earth wires.
2 | Drilling holes in supports wherever required.
3 | Fixing clamps, GI bolts and nuts/brass screws, saddles, rawl bolts and other fixing accessories as required.
4 | Painting with enamel paint of clamps and other fixing accessories.
5 | Suitable size junction boxes with connector block for loop in loop out where ever applicable.
6 | Testing of all fixture after installation.
Cabling and Installation of Lighting Fixtures for External/Landscape Lighting
Installation, testing and commissioning of the following lighting fixtures and poles including excavation and back filling as required.
1 | Installation, testing & commissioning of external lighting fixtures as per landscape selection with UGR 19 or less) suitable to be mounted on boundary wall with 1 meter high structure, heavy duty external GI tubular simple pole & IP65 type driver. | Nos. | 14 |  | 0
0
2 | Installation, testing & commissioning of following external lighting fixtures as per landscape selection with UGR 19 or less) |  |  |  | 0
| Ground light for WB | Nos. | RO
| In Ground mounted Shrub Uplighter | Nos. | 17 |  | 0
| LED Strip light | RM | RO
| Strip ligh @ ground | Nos. | RO
| Under water light | Nos. | 35 |  | 0
| Sculpture uplighter (On Ground at soil level of planter) | Nos. | 1 |  | 0
| Tree uplighter (On Ground at soil level of planter) | Nos. | 4 |  | 0
| Wash light @ ground (wide) | Nos. | 6 |  | 0
0
3 | Supply & installation of suitable size polycarbonate weather proof (IP-65) junction box with tentative size 100mm x 100mm x 50mm including excavation and back filling & connector. These shall be supplied only in case if fixture does not have its provision. | Nos. | 77 |  | 0
| Note :-Boudary wall light Quantity is based on assumption as no lighting layout is avaialable. Box requirement may change as per actual fixture selection. |  |  |  | 0
0
4 | Supply, laying, testing and commissioning of following size PVC insulated copper conductor 1100 V grade armoured cable including excavation of earth, sand/brick protection refilling, watering & ramming complete. |  |  |  | 0
a | 3 C x 4 Sq. mm. (Red, Black & Green) | RM | 500 |  | 0
b | 3 C x 4 Sq. mm. (Yellow, Black & Green) | RM | 500 |  | 0
c | 3 C x 4 Sq. mm. (Blue, Black & Green) | RM | 500 |  | 0
| Note :- Quantity is based on assumption as no landscape lighting layout is avaialable. Box requirement may change as per actual fixture selection. |  |  |  | 0
0
5 | Supply and making end termination & jointing of following size PVC insulated copper conductor 1100 V grade armored cable including cost of crimping lugs, sockets, insulation tapes, double compression glands etc. complete. |  |  |  | 0
a | 3C x 4 Sq. mm. | Nos. | 28 |  | 0
0
5 | Supplying all the material for wiring with 3 x 2.5 sq. mm. PVC insulated copper conductor 1100 V in 16 gauge 20 mm dia G.I. flexible conduit including termination & connecting at terminals of lighting fixtures complete. The cost shall include supply and installation of G.I. flexible conduit. | RM | 14 |  | 0
| TOTAL CARRIED TO SUMMARY |  |  |  | 0
H | ELECTRIC VEHICLE CHARGER
a | Supply, installation, testing and commissioning of AC EV charger of rating 11 kW with 5 meter AC Type 2 cable, as pe specification including all necessary accessories to complete the job. | Nos. | 5 |  | 0
| Charger is considered with average charging time of 8 to 10 hours for an indian SUV. |  |  |  | 0
0
b | Supply, installation, testing and commissioning of EV charger of rating 2.5 kW with 5 meter AC Type 2 cable for 2 Wheelers , as pe specification including all necessary accessories to complete the job. | Nos. | 7 |  | 0
0
c | Supply, installation, testing and commissioning of locally wall mounted 220 volts, single phase, AC energy meter with enclosure near to the EV charger to record energy consumption with RS 485 port and terminals of suitable rating with glands for cable entry/ exit with accessories for completeness of job. | Nos. | 12 |  | 0
Note:-
At present, the contractor shall make the infrastructure ready for EV charger i.e. underground pipe, cables etc., which may be brought in future and plug it to ready to use.
The method of billing shall be decided by client once the charger are purchased by client
| TOTAL CARRIED TO SUMMARY |  |  |  | 0
I. | HV INSTALLATION
I. | Installation of Sub-Station Equipment
The rates under this section shall also include:
1 | Supporting rigid frame work.
2 | All fixing accessories such as foundation bolts, nuts and bolts etc as required.
3 | Touching up all damaged paint with approved paint shade.
4 | Rubber mats shall be provided in front and back of the HT switchgear as per IS-5424-1969.
5 | All control cabling including termination between transformer and HT switchgear as required.
6 | Interlocking shall be provided between transformer door and VCB HT breaker panel. When transformer door open respective VCB breaker shall be tripped.
7 | Degree of protection for transformer enclosure shall be IP-23.
8 | All protection relays shall be microprocessor based.
9 | Provision shall be made for all HT breakers to be hooked up with BAS for status indication.
I. | Sub-Station Equipment
1 | Installation, testing and commissioning of 400 KVA capacity 11/0.433 kV Oil type Compact sub-station (CSS) with ON load tap changer, as per specifications, including RTCC Panel. | Nos. | 1 |  | 0
0
2 | Supply, installation, testing and commissioning of 200 AH capacity 24 volts DC hermetically sealed maintenance free lead acid batteries duly charged for LT Panel & HT Panel. | Nos. | RO
0
3 | Supply, installation, testing and commissioning of battery charger unit with provisions of Boost Charing, and Float charging. Suitable for 240 V single phase + 10% AC, 50 Hz power supply as per specifications. | Nos. | RO
0
4 | Supply and fixing in position the approved “Shock Treatment Charts” written in English and Local Language. These charts shall be framed in teak wood frame and covered with glass. | Nos. | 2 |  | 0
0
5 | Supply and fixing in position the fire extinguishers carbon-di-oxide type 2.5 Kgs capacity. | Nos. | 10 |  | 0
0
6 | Supply and fixing in position the best quality Danger Boards of approved shape and size as specified by Local Electricity Authorities written in English & Local Languages. | Nos. | 5 |  | 0
0
7 | Supply and providing ISI marked electrical 1.1 kV grade anti-skid rubber mat as per IS:15652-2006 with upto date ammendment. | Mtrs. | 10 |  | 0
| TOTAL CARRIED TO SUMMARY |  |  |  | 0
II. | HT Cables & LT Control Cables
The rates under this section shall also include the following:
1 | Providing and fixing approved cable supports and grouting the same as required.
2 | Effecting proper connections at terminations.
3 | Ensuring that provision is left in buildings and trenches as the work proceeds, for incorporating of cable supports at a later date.
4 | Providing all, fixing accessories such as clamping devices, nuts and bolts etc.
5 | ClAing to supports where laid in trenches.
6 | Providing proper supports for cable terminals as called for. |  |  |  | 0
7 | Wherever cables cross walls provide proper sleeves at the time of civil work. |  |  |  | 0
0
II. | HT Cables & LT Control Cables |  |  |  | 0
1 | Supplying and laying following size 11 KV grade un-earthed (UE) XLPE aluminium conductor, flat armoured cables laid within in existing trenches and RCC hume pipes. |  |  |  | 0
a | 3 C x 150 sq.mm 11 KV XLPE cable | RM | 20 |  | 0
0
2 | Supplying and making cable end terminations for the following size of 11 KV grade, XLPE aluminium conductor armoured cable including termination kit complete heat shrinkable sleeve etc. |  |  |  | 0
a | 3 C x 150 sq.mm 11 KV XLPE cable (indoor) | Nos. | 2 |  | 0
0
3 | Supplying and laying of following 1100 volts grade PVC insulated sheathed copper conductor armoured control cables in existing trenches cables trays, cladd on wall with suitable saddles, fixing bolts, including testing and commissioning. |  |  |  | 0
a | 7 core 2.5 sq mm PVC insulated copper conductor armoured control cables | RM | 100 |  | 0
b | 12 core 2.5 sq mm PVC insulated copper conductor armoured control cables | RM | 100 |  | 0
0
4 | Cable end termination of the following PVC insulated sheathed aluminium conductor armoured cables of 1100 volt grade including supplying and fixing of crimping lugs. Double compression glands with earthing provision and cable sockets |  |  |  | 0
a | 7 core 2.5 sq.mm Control cable | Nos. | 4 |  | 0
b | 12 core 2.5 sq.mm Control cable | Nos. | 4 |  | 0
| TOTAL CARRIED TO SUMMARY |  |  |  | 0
| TOTAL (I & II) |  |  |  | 0
J | SUPPLY & INSTALLATION OF LT PANELS
LOW VOLTAGE DISTRIBUTION BOARDS
The followings shall also be included in the Supply, Installation, testing & commisssioning of panels & boards as following :-
1 | Cubicle type, 14 gauge CRCA sheet steel enclosed including supporting M.S frame work and boding to earth.
2 | Complete with internal wiring and distribution bus bars , clamps & supports in cable alley.
3 | Lettering on Panels/ boards, the area they feed, and the circuit diagram.
4 | TPN ACB’s / MCCB’s shall mean 3 pole with adequate size of neutral link.
5 | The breaking capacity of MCCB’s are mentioned panel wise. All MCCB’s shall be with thermal magnetic releases & including 200 amps and microprocessor based above 250 amps (including 250 amps) capacity, unless specified otherwise.
6 | All motor feeders MCCBs shall be of motor duty. |  |  |  | 0
7 | Distribution panels shall be Powder Coated with Siemens gray paint shade no. RAL-7032 of IS-5. |  |  |  | 0
8 | Degree of protection for following type of distribution panel enclosure shall be as per IS:13947-1993. |  |  |  | 0
a. | IP 42 for indoor panels. |  |  |  | 0
b. | IP 54 for kitchen and laundry panels. |  |  |  | 0
c. | IP 55 for outdoor panels. |  |  |  | 0
9 | All MCCB’s shall be provided with operating mechanism for door interlock. |  |  |  | 0
10 | Current density of aluminium shall be 1 sq mm for 1.0 amps for rated current of bus bars and current density of copper shall be 1 sq.mm for 1.25 amps for rated current of bus bars. |  |  |  | 0
11 | Tinned copper / GI earth bus as specified in the BOQ shall be provided through out the length of each panel board. |  |  |  | 0
12 | All measuring instruments (Meters) shall be of digital electronic with LED of approved make and compatible with BAS. |  |  |  | 0
13 | All hinged door shall be earthed through 2.5 sq mm tinned braided copper wire. |  |  |  | 0
14 | All panels shall have provision of the following: |  |  |  | 0
a | Pad locking of Switch board doors. |  |  |  | 0
b | Pad locking of MCCB’s handles in “OFF” Position. |  |  |  | 0
15 | All MCB’s used for protection of resistive and lightly inductive load shall be type “B” characteristic and inductive (motor) load shall be of type “C” characteristic and discharge lamps and UPS etc. shall be of type D characteristic. |  |  |  | 0
16 | All incoming and outgoing air circuit breakers shall be placed on middle portion of the vertical in single tier formation. |  |  |  | 0
17 | All PTs / control transformer shall be provided with centre tap earth secondary. |  |  |  | 0
18 | All panels shall be extendible type from both end. |  |  |  | 0
| LT panels fabricated out of 14 gauge CRCA sheet steel in cubicle compartmentalised free standing floor/ Wall mounted, dust and vermin proof with reinforcement of suitable size angle iron, channel `T’ section and / or flats wherever necessary. 3 mm thick cable gland plates shall be provided on top as well as at the bottom of the panels. Panels shall be treated with all anti corrosive process before powder coating as per specification and final approved shade. 2 Nos. earthing terminals shall be provided for all panels. Panels shall be suitable for 415 V, 3 phase, 4 wire, 50 HZ supply system. Lifting hooks shall also be provided in all panels. Approval shall be taken for each panel in the form of shop drawings before fabrication. Galvanised hardwares with zinc passivation shall be used in fabrication of panels. |  |  |  | 0
0
1 | MAIN LT PANEL |  |  |  | 0
| SECTION I |  |  |  | 0
A | Incoming Air Circuit Breaker `A’ (For Transformer Supply) |  |  |  | 0
i | 800 amps 4 pole electrically operated fully drawout type air circuit breaker with built in microprocessor based release unit for short circuit, over current and earth fault protection with adjustable setting as per specification and with following accessories: |  |  |  | 0
ii | Electronic multi function meter of accuracy class-I, with 3 Nos. 800/5 amps 15VA CTs to measure and display the following electrical quantities : |  |  |  | 0
0
a. | Real Time parameter |  |  |  | 0
b. | Total active energy (KWH/MWH) |  |  |  | 0
c. | Maximum demand (KVA/MVA) (KW/MW) |  |  |  | 0
d. | Maximum demand reset count. |  |  |  | 0
e. | Instantaneous power factor |  |  |  | 0
f. | Logging of active energy eight time of a day |  |  |  | 0
g. | Current |  |  |  | 0
h. | Voltage |  |  |  | 0
i | Frequency / Harmonics |  |  |  | 0
j | Power factor |  |  |  | 0
k | RS -485 Port with THDi+THDv (2 nos. port) |  |  |  | 0
0
iii | Phase indicating light connected through same PT for connecting digital volt meter |  |  |  | 0
| 1 Sets |  |  |  | 0
iv (a) | Breaker ON / OFF / TRIP indicating lights with control MCB’s. |  |  |  | 0
| 1 Set. |  |  |  | 0
(b) | Spring charge / trip circuit healthy indication |  |  |  | 0
0
(c) | DC "ON" indication |  |  |  | 0
0
v | 96 x 96 mm sq. 0-500 Volt digital voltmeter protected by 6 amp TP MPCB’s |  |  |  | 0
| 1 Set |  |  |  | 0
vi | Breaker control switch |  |  |  | 0
| 1 Set |  |  |  | 0
vii | Auto-manual & off selector switch |  |  |  | 0
| 1 Set |  |  |  | 0
vii | Protections: |  |  |  | 0
a) | Master trip relay (86) |  |  |  | 0
b) | Under voltage relay (27) |  |  |  | 0
c) | Over voltage realy (59) |  |  |  | 0
d) | Instantaneous over current and earth fault relay (50+50N) |  |  |  | 0
e) | Voltage Monitoring Relay (VMR) |  |  |  | 0
0
ix | Breaker TRIP/NEUTRAL/CLOSE (TNC) switch |  |  |  | 0
0
xi | Type II surge protection device |  |  |  | 0
0
| Auxiliary contacts required for necessary interlocking of breakers. |  |  |  | 0
0
x | CTs |  |  |  | 0
| Separate set of class 1, 15VA CTs for protection for Solar PV integration |  |  |  | 0
| 1 Set |  |  |  | 0
| Separate set of class 1, 15VA CTs for protection for Hybrid power factor correction panel |  |  |  | 0
| 1 Set |  |  |  | 0
| Separate set of class 5P10, 15VA CTs for protection for protection |  |  |  | 0
| 1 Set |  |  |  | 0
0
B | Incoming Air Circuit Breaker ‘B’ |  |  |  | 0
| (From 500kVA Genset) |  |  |  | 0
i | 800 amps 4 pole electrically operated fully drawout type air circuit breaker with built in microprocessor based release unit for short circuit, over current and earth fault protection with adjustable setting as per specification and with following accessories: |  |  |  | 0
0
ii | Electronic multi function meter of accuracy class-I, with 3 Nos 800/5 amps 15VA CTs to measure and display the following electrical quantities : |  |  |  | 0
a. | Real Time parameter |  |  |  | 0
b. | Total active energy (KWH/MWH) |  |  |  | 0
c. | Maximum demand (KVA/MVA) (KW/MW) |  |  |  | 0
d. | Maximum demand reset count. |  |  |  | 0
e. | Instantaneous power factor |  |  |  | 0
f. | Logging of active energy eight time of a day. |  |  |  | 0
g. | Current |  |  |  | 0
h. | Voltage |  |  |  | 0
i | Frequency / Harmonics |  |  |  | 0
j. | Power factor |  |  |  | 0
k | RS -485 Port with THDi+THDv |  |  |  | 0
0
iii | Phase indicating light connected through |  |  |  | 0
iv (a) | Breaker ON / OFF / TRIP indicating lights with control MCB’s. |  |  |  | 0
| 1 Set. |  |  |  | 0
(b) | Spring charge / trip circuit healthy indication |  |  |  | 0
0
(c) | DC "ON" indication |  |  |  | 0
| 1 Sets |  |  |  | 0
v | Breaker control switch |  |  |  | 0
| 1 Set |  |  |  | 0
vi | Auto-manual & off selector switch |  |  |  | 0
| 1 Set |  |  |  | 0
vii | Timer for auto change over |  |  |  | 0
| 1 Set |  |  |  | 0
viii | 96 x 96 mm sq. 0-500 Volt digital voltmeter protected by 6 amp TP MPCB’s |  |  |  | 0
| 1 Set |  |  |  | 0
ix | Protections: |  |  |  | 0
a) | Master trip relay (86) |  |  |  | 0
b) | Under voltage relay (27) |  |  |  | 0
c) | Over voltage realy (59) |  |  |  | 0
d) | Instantaneous over current and earth fault relay (50+50N) |  |  |  | 0
e) | Voltage Monitoring Relay (VMR) |  |  |  | 0
0
x | Breaker TRIP/NEUTRAL/CLOSE (TNC) switch |  |  |  | 0
0
xi | Type II surge protection device |  |  |  | 0
0
xii | PLC controller for load management and operation control along with grid and solar PV system |  |  |  | 0
0
xiii | AMF relay with all necessary components for DG AMF operation |  |  |  | 0
0
xiv | CTs |  |  |  | 0
| Separate set of class 1, 15VA CTs for protection for Solar PV integration |  |  |  | 0
| 1 Set |  |  |  | 0
| Auxiliary contacts required for necessary interlocking of breakers. |  |  |  | 0
| Separate set of class 5P10, 15VA CTs for protection for protection |  |  |  | 0
| 1 Set |  |  |  | 0
0
C | Incoming Air Circuit Breaker ‘C’ |  |  |  | 0
| (From Solar PV System) |  |  |  | 0
i | 100 amps 4P MCCB with inegral earth fault madule with following accessories: |  |  |  | 0
0
ii | Electronic multi function meter of accuracy class-I, with 3 Nos. 100/5 amps 15VA CTs to measure and display the following electrical quantities : |  |  |  | 0
a. | Real Time parameter |  |  |  | 0
b. | Total active energy (KWH/MWH) |  |  |  | 0
c. | Maximum demand (KVA/MVA) (KW/MW) |  |  |  | 0
d. | Maximum demand reset count. |  |  |  | 0
e. | Instantaneous power factor |  |  |  | 0
f. | Logging of active energy eight time of a day. |  |  |  | 0
g. | Current |  |  |  | 0
h. | Voltage |  |  |  | 0
i | Frequency / Harmonics |  |  |  | 0
j. | Power factor |  |  |  | 0
k | RS -485 Port with THDi+THDv |  |  |  | 0
0
iii | Phase indicating light connected through |  |  |  | 0
| 1 Sets |  |  |  | 0
iv | Breaker ON / OFF / TRIP indicating lights with control MCB’s. |  |  |  | 0
| 1 Set |  |  |  | 0
v | MCCB rotary handle |  |  |  | 0
| 1 Set |  |  |  | 0
vi | Auto-manual & off selector switch |  |  |  | 0
| 1 Set |  |  |  | 0
vii | Timer for auto change over |  |  |  | 0
| 1 Set |  |  |  | 0
viii | 96 x 96 mm sq. 0-500 Volt digital voltmeter protected by 6 amp TP MPCB’s |  |  |  | 0
| 1 Set |  |  |  | 0
ix | Protections: |  |  |  | 0
a) | Master trip relay (86) |  |  |  | 0
b) | Under voltage relay (27) |  |  |  | 0
d) | Over voltage realy (59) |  |  |  | 0
e) | Voltage Monitoring Relay (VMR) |  |  |  | 0
0
x | Breaker TRIP/NEUTRAL/CLOSE (TNC) switch |  |  |  | 0
0
xi | Type II surge protection device |  |  |  | 0
0
xii | 100amp, AC3, Contactor |  |  |  | 0
0
| Auxiliary contacts required for necessary interlocking of breakers. |  |  |  | 0
0
| Bus Bar |  |  |  | 0
| 900 A, TPN Al. Bus Bar with PVC heat shrinkable sleeves of suitable length to withstand fault current of 35 KA for 1 Sec. |  |  |  | 0
| Type II surge protection device |  |  |  | 0
0
0
| Outgoings |  |  |  | 0
0
i | 250 amps 4P MCCB 4 Nos. |  |  |  | 0
ii | 200 amps 4P MCCB 1 Nos. |  |  |  | 0
iii | 160 amps 4P MCCB 3 Nos. |  |  |  | 0
iv | 125 amps 4P MCCB 2 Nos. |  |  |  | 0
v | 100 amps 4P MCCB 2 No. |  |  |  | 0
vi | 63 amps 4P MCCB 4 No. |  |  |  | 0
vii | 63 amps 4P MCB 5 No. |  |  |  | 0
viii | 32 amps 4P MCB 3 No. |  |  |  | 0
ix | 40 amps 4P MCB 2 No. |  |  |  | 0
0
| All incoming and outgoing (MCCB) feeder shall be provided with extra pair of NO+NC contact set for BMS integration except spare feeders. |  |  |  | 0
0
| For detail, refer SLD. |  |  |  | 0
0
| Main LT Panel as described above | Set | 1 |  | 0
0
0
2 | 100 KVAR IGBT MODULE BASED HYBRID ACTIVE PANEL |  |  |  | 0
| Incoming |  |  |  | 0
| Design, supply, installation, testing & commissioning of cubicle type semi compartementalized floor mounted free standing type with configration of Static Var Generator 600 Kvar Modular design ,415V, 50HZ, 3 phase 4 wire supply, moisture, dust and vermin proof IP-42 with cooling intrinsic design of voltage sourced IGBT based technology with multi modular design for parallel operation ,intelligent 3-Level topology with 12 IGBT Hybrid PFC panel with Programmable Microprocessor controller to maintain Power Factor, Harmonics & Unbalancing duly housed in epoxy powder coated 2mm thick CRCA sheet steel compatmentalised enclosure free standing type with all supports, accessories, switch gears, control gears, protections, wiring, interconnections, control MCBs and maintain PF,I-THD,V-THD upto 51 th level of harmonics.Certification Standard having surge test IEC61000-4-5, conducted suseptiablity IEC 61000-6-4 and fast transient test IEC61000-4-4 |  |  |  | 0
| IP Rating: IP 42 |  |  |  | 0
| Short Circuit Fault with stand Capacity: 50 KA |  |  |  | 0
0
| Incomer : |  |  |  | 0
| 1 No.. 250A, TPN, MCCB with integral earth fault protection with following accessories. |  |  |  | 0
| Bus bars: |  |  |  | 0
| 300A, TP, Aluminium Bus Bars of Electrolytic grade with heat shrinkable sleeves. |  |  |  | 0
0
i. | 0-500 volts digital electronic volt meter with in built selector switch protected by 6 amps TP MCB's. |  |  |  | 0
| 1 Set |  |  |  | 0
iii. | Phase indicating light & Breaker ON/OFF/TRIP indication protected by MCB. |  |  |  | 0
| 1 Set |  |  |  | 0
2 | Electronic multi function meter of accuracy class-I, to measure and display the following electrical quantities : |  |  |  | 0
0
a. | Real Time parameter |  |  |  | 0
b. | Total active energy (KWH/MWH) |  |  |  | 0
c. | Maximum demand (KVA/MVA) (KW/MW) |  |  |  | 0
d. | Maximum demand reset count. |  |  |  | 0
e. | Instantaneous power factor |  |  |  | 0
f. | Logging of active energy eight time of a day |  |  |  | 0
g. | Current |  |  |  | 0
h. | Voltage |  |  |  | 0
i | Frequency / Harmonics |  |  |  | 0
j | Power factor |  |  |  | 0
k | RS -485 Port with THDi+THDv |  |  |  | 0
0
| Common HMI Controller 7" inch - Micro processor based, *BMS Compatible: |  |  |  | 0
a. | 3 Phase Display with 7" TFT touch Screen with RS 485 communication port |  |  |  | 0
i. | Multi Protection functions including over and under volatge /frequency/pase failure/over temp/ high harmonic protection |  |  |  | 0
ii. | Total Current |  |  |  | 0
iii. | Voltage |  |  |  | 0
iv. | Power Factor |  |  |  | 0
v. | Instantly displays power information with data before and data after compensation. |  |  |  | 0
0
| Outgoings: |  |  |  | 0
a. | 2 Nos. 50 KVAR ASVG IGBT Modular Sets, each comprising : |  |  |  | 0
| (IGBT based active technology with gate driver,interfacing,voltage sensing & control cards, heat sinks, cooling fan, current tranducers, SMPS, SSR etc.) each have following. |  |  |  | 0
| 50 Kvar ASVG module (3 -Level Topology ,12 IGBT Circuit) with Proper Surge protection meeting,Three-level Neutral point clamped IGBT modules- 3 numbers a)650V/1300V PIV, 300 Amps rated current for 100 Kvar, modular IGBT based design should be a power electronic device to be connected in parallel with the loads that require inductive and/or capacitive reactive powers, for their operation. DC link capacitor Board -900V tolerant,Safe discharging circuit,Relay board Main relays (3 numbers),AC ripple filter Third order LCL filter. Passive damping resistors,Digital signal processing board 32-bit DSP RS485 based isolated communication,Cooling circuit Aluminium heatsink 80 CFM / 24V BLDC fans... 5numbers Auto ON/OFF control, IOT Enbled |  |  |  | 0
| 3 phase ASVG current, current shall be shown with different colors (Red, yellow, blue, black color) Each module shall have separate protection MCCB. For easy repairability the IGBT driver cards shall be separate for different phases, separate common control cards and these should be fitted on main PCB. DC capacitors shall not be mounted on PCB. ASVG shall used powder iron core instead of CRGO and LCL circuit to reduce noises created by switching frequency.. The ASVG shall also be suitable for unbalanced load usage. |  |  |  | 0
0
0
| 100kVAr IGBT MODULE BASED HYBRID ACTIVE PANEL as described above | Set | 1 |  | 0
0
3 | VENTILATION FANS PANEL - BASEMENT |  |  |  | 0
| Incoming |  |  |  | 0
1 | 63 amps 4P MCCB with inegral earth fault madule with following accessories: |  |  |  | 0
0
i. | 0-500 volts digital electronic volt meter with in built selector switch protected by 6 amps TP MCB's. |  |  |  | 0
| 1 Set |  |  |  | 0
iii. | Phase indicating light & Breaker ON/OFF/TRIP indication protected by MCB. |  |  |  | 0
| 1 Set |  |  |  | 0
2 | Electronic multi function meter of accuracy class-I, to measure and display the following electrical quantities : |  |  |  | 0
0
a. | Real Time parameter |  |  |  | 0
b. | Total active energy (KWH/MWH) |  |  |  | 0
c. | Maximum demand (KVA/MVA) (KW/MW) |  |  |  | 0
d. | Maximum demand reset count. |  |  |  | 0
e. | Instantaneous power factor |  |  |  | 0
f. | Logging of active energy eight time of a day |  |  |  | 0
g. | Current |  |  |  | 0
h. | Voltage |  |  |  | 0
i | Frequency / Harmonics |  |  |  | 0
j | Power factor |  |  |  | 0
k | RS -485 Port with THDi+THDv |  |  |  | 0
0
3 | Bus Bars |  |  |  | 0
| 100 amps TPN aluminium bus bars (25kA) with coloured heat shrinkable insulation sleeve. |  |  |  | 0
0
4 | Outgoing |  |  |  | 0
0
i | 40 Amps 4P MCB 2 Nos. |  |  |  | 0
ii | 25 Amps 4P MCB 3 Nos. |  |  |  | 0
iii | 16 Amps 4P MCB 3 Nos. |  |  |  | 0
0
| Note:- |  |  |  | 0
| All incoming feeder shall be provided with extra pair of NO+NC contact set for BMS integration |  |  |  | 0
0
| VENTILATION FANS PANEL - BASEMENT described as above | Set | 1 |  | 0
0
4 | AC ODU PANEL - TERRACE |  |  |  | 0
| Incoming |  |  |  | 0
1 | 250 amps 4P MCCB with inegral earth fault madule with following accessories: |  |  |  | 0
0
i. | 0-500 volts digital electronic volt meter with in built selector switch protected by 6 amps TP MCB's. |  |  |  | 0
| 1 Set |  |  |  | 0
iii. | Phase indicating light & Breaker ON/OFF/TRIP indication protected by MCB. |  |  |  | 0
| 1 Set |  |  |  | 0
2 | Electronic multi function meter of accuracy class-I, to measure and display the following electrical quantities : |  |  |  | 0
0
a. | Real Time parameter |  |  |  | 0
b. | Total active energy (KWH/MWH) |  |  |  | 0
c. | Maximum demand (KVA/MVA) (KW/MW) |  |  |  | 0
d. | Maximum demand reset count. |  |  |  | 0
e. | Instantaneous power factor |  |  |  | 0
f. | Logging of active energy eight time of a day |  |  |  | 0
g. | Current |  |  |  | 0
h. | Voltage |  |  |  | 0
i | Frequency / Harmonics |  |  |  | 0
j | Power factor |  |  |  | 0
k | RS -485 Port with THDi+THDv |  |  |  | 0
0
3 | Bus Bars |  |  |  | 0
| 100 amps TPN aluminium bus bars (25kA) with coloured heat shrinkable insulation sleeve. |  |  |  | 0
0
4 | Outgoing |  |  |  | 0
0
i | 160 Amps 4P MCCB 4 Nos. |  |  |  | 0
0
| Note:- |  |  |  | 0
| All incoming feeder shall be provided with extra pair of NO+NC contact set for BMS integration |  |  |  | 0
0
| AC ODU PANEL - TERRACE described as above | Set | 1 |  | 0
0
5 | STACK PARKING PANEL - BASEMENT |  |  |  | 0
| Incoming |  |  |  | 0
1 | 100 amps 4P MCCB with inegral earth fault madule with following accessories: |  |  |  | 0
0
i. | 0-500 volts digital electronic volt meter with in built selector switch protected by 6 amps TP MCB's. |  |  |  | 0
| 1 Set |  |  |  | 0
iii. | Phase indicating light & Breaker ON/OFF/TRIP indication protected by MCB. |  |  |  | 0
| 1 Set |  |  |  | 0
2 | Electronic multi function meter of accuracy class-I, to measure and display the following electrical quantities : |  |  |  | 0
0
a. | Real Time parameter |  |  |  | 0
b. | Total active energy (KWH/MWH) |  |  |  | 0
c. | Maximum demand (KVA/MVA) (KW/MW) |  |  |  | 0
d. | Maximum demand reset count. |  |  |  | 0
e. | Instantaneous power factor |  |  |  | 0
f. | Logging of active energy eight time of a day |  |  |  | 0
g. | Current |  |  |  | 0
h. | Voltage |  |  |  | 0
i | Frequency / Harmonics |  |  |  | 0
j | Power factor |  |  |  | 0
k | RS -485 Port with THDi+THDv |  |  |  | 0
0
3 | Bus Bars |  |  |  | 0
| 150 amps TPN aluminium bus bars (25kA) with coloured heat shrinkable insulation sleeve. |  |  |  | 0
0
4 | Outgoing |  |  |  | 0
0
i | 32 Amps 4P MCB 4 Nos. |  |  |  | 0
0
| Note:- |  |  |  | 0
| All incoming feeder shall be provided with extra pair of NO+NC contact set for BMS integration |  |  |  | 0
0
| STACK PARKING PANEL - BASEMENT described as above | Set | 1 |  | 0
0
6 | STAIRWELL & LIFT PRESS FAN PANEL - TERRACE |  |  |  | 0
| Incoming |  |  |  | 0
1 | 63 amps 4P MCCB with inegral earth fault madule with following accessories: |  |  |  | 0
0
i. | 0-500 volts digital electronic volt meter with in built selector switch protected by 6 amps TP MCB's. |  |  |  | 0
| 1 Set |  |  |  | 0
iii. | Phase indicating light & Breaker ON/OFF/TRIP indication protected by MCB. |  |  |  | 0
| 1 Set |  |  |  | 0
2 | Electronic multi function meter of accuracy class-I, to measure and display the following electrical quantities : |  |  |  | 0
0
a. | Real Time parameter |  |  |  | 0
b. | Total active energy (KWH/MWH) |  |  |  | 0
c. | Maximum demand (KVA/MVA) (KW/MW) |  |  |  | 0
d. | Maximum demand reset count. |  |  |  | 0
e. | Instantaneous power factor |  |  |  | 0
f. | Logging of active energy eight time of a day |  |  |  | 0
g. | Current |  |  |  | 0
h. | Voltage |  |  |  | 0
i | Frequency / Harmonics |  |  |  | 0
j | Power factor |  |  |  | 0
k | RS -485 Port with THDi+THDv |  |  |  | 0
0
3 | Bus Bars |  |  |  | 0
| 100 amps TPN aluminium bus bars (25kA) with coloured heat shrinkable insulation sleeve. |  |  |  | 0
0
4 | Outgoing |  |  |  | 0
0
i | 32 Amps 4P MCB 5 Nos. |  |  |  | 0
0
| Note:- |  |  |  | 0
| All incoming feeder shall be provided with extra pair of NO+NC contact set for BMS integration |  |  |  | 0
0
| STAIRWELL & LIFT PRESS FAN PANEL - BASEMENT described as above | Set | 1 |  | 0
0
7 | EV CHARGER PANEL - BASEMENT |  |  |  | 0
| Incoming |  |  |  | 0
1 | 160 amps 4P MCCB with inegral earth fault madule with following accessories: |  |  |  | 0
0
i. | 0-500 volts digital electronic volt meter with in built selector switch protected by 6 amps TP MCB's. |  |  |  | 0
| 1 Set |  |  |  | 0
iii. | Phase indicating light & Breaker ON/OFF/TRIP indication protected by MCB. |  |  |  | 0
| 1 Set |  |  |  | 0
2 | Electronic multi function meter of accuracy class-I, to measure and display the following electrical quantities : |  |  |  | 0
0
a. | Real Time parameter |  |  |  | 0
b. | Total active energy (KWH/MWH) |  |  |  | 0
c. | Maximum demand (KVA/MVA) (KW/MW) |  |  |  | 0
d. | Maximum demand reset count. |  |  |  | 0
e. | Instantaneous power factor |  |  |  | 0
f. | Logging of active energy eight time of a day |  |  |  | 0
g. | Current |  |  |  | 0
h. | Voltage |  |  |  | 0
i | Frequency / Harmonics |  |  |  | 0
j | Power factor |  |  |  | 0
k | RS -485 Port with THDi+THDv |  |  |  | 0
0
3 | Bus Bars |  |  |  | 0
| 200 amps TPN aluminium bus bars (25kA) with coloured heat shrinkable insulation sleeve. |  |  |  | 0
0
4 | Outgoing |  |  |  | 0
0
i | 40 Amps 4P MCB 6 Nos. |  |  |  | 0
II | 25 Amps DP MCB 8 Nos. |  |  |  | 0
0
| Note:- |  |  |  | 0
| All incoming feeder shall be provided with extra pair of NO+NC contact set for BMS integration |  |  |  | 0
0
| EV CHARGER PANEL - BASEMENT described as above | Set | 1 |  | 0
0
8 | SDB LIGHT & POWER (LOWER FLOOR) |  |  |  | 0
| Incoming |  |  |  | 0
1 | 160 amps 4P MCCB with inegral earth fault madule with following accessories: |  |  |  | 0
0
i. | 0-500 volts digital electronic volt meter with in built selector switch protected by 6 amps TP MCB's. |  |  |  | 0
| 1 Set |  |  |  | 0
iii. | Phase indicating light & Breaker ON/OFF/TRIP indication protected by MCB. |  |  |  | 0
| 1 Set |  |  |  | 0
2 | Electronic multi function meter of accuracy class-I, to measure and display the following electrical quantities : |  |  |  | 0
0
a. | Real Time parameter |  |  |  | 0
b. | Total active energy (KWH/MWH) |  |  |  | 0
c. | Maximum demand (KVA/MVA) (KW/MW) |  |  |  | 0
d. | Maximum demand reset count. |  |  |  | 0
e. | Instantaneous power factor |  |  |  | 0
f. | Logging of active energy eight time of a day |  |  |  | 0
g. | Current |  |  |  | 0
h. | Voltage |  |  |  | 0
i | Frequency / Harmonics |  |  |  | 0
j | Power factor |  |  |  | 0
k | RS -485 Port with THDi+THDv |  |  |  | 0
0
3 | Bus Bars |  |  |  | 0
| 200 amps TPN aluminium bus bars (25kA) with coloured heat shrinkable insulation sleeve. |  |  |  | 0
0
4 | Outgoing |  |  |  | 0
0
i | 63 Amps 4P MCB 8 Nos. |  |  |  | 0
II | 25 Amps DP MCB 3 Nos. |  |  |  | 0
0
| Note:- |  |  |  | 0
| All incoming feeder shall be provided with extra pair of NO+NC contact set for BMS integration |  |  |  | 0
0
| SDB LIGHT & POWER (LOWER FLOOR) described as above | Set | 1 |  | 0
0
0
9 | UPS PANEL 1 |  |  |  | 0
| Incoming |  |  |  | 0
1 | 200 amps 4P MCCB with inegral earth fault madule with following accessories: |  |  |  | 0
0
i. | 0-500 volts digital electronic volt meter with in built selector switch protected by 6 amps TP MCB's. |  |  |  | 0
| 1 Set |  |  |  | 0
ii | Phase indicating light & Breaker ON/OFF/TRIP indication protected by MCB. |  |  |  | 0
| 1 Set |  |  |  | 0
2 | Electronic multi function meter of accuracy class-I, to measure and display the following electrical quantities : |  |  |  | 0
0
a. | Real Time parameter |  |  |  | 0
b. | Total active energy (KWH/MWH) |  |  |  | 0
c. | Maximum demand (KVA/MVA) (KW/MW) |  |  |  | 0
d. | Maximum demand reset count. |  |  |  | 0
e. | Instantaneous power factor |  |  |  | 0
f. | Logging of active energy eight time of a day |  |  |  | 0
g. | Current |  |  |  | 0
h. | Voltage |  |  |  | 0
i | Frequency / Harmonics |  |  |  | 0
j | Power factor |  |  |  | 0
k | RS -485 Port with THDi+THDv |  |  |  | 0
0
3 | Bus Bars |  |  |  | 0
| 300 amps TPN aluminium bus bars with coloured heat shrinkable insulation sleeve. |  |  |  | 0
0
4 | Outgoing |  |  |  | 0
| 160 Amps 4P MCCB 3 Nos. |  |  |  | 0
0
| Note:- |  |  |  | 0
| Panel shall be extensible type. |  |  |  | 0
| All incoming feeder shall be provided with extra pair of NO+NC contact set for BMS integration |  |  |  | 0
0
| UPS PANEL 1 described as above | Set | 1 |  | 0
0
10 | UPS PANEL 2 |  |  |  | 0
| Incoming |  |  |  | 0
1 | 2 Nos. 160 amps 4P MCB (10kA) with following accessories: |  |  |  | 0
0
i. | 0-500 volts digital electronic volt meter with in built selector switch protected by 6 amps TP MCB's. |  |  |  | 0
| 2 Set |  |  |  | 0
iii. | Phase indicating light & Breaker ON/OFF/TRIP indication protected by MCB. |  |  |  | 0
| 2 Set |  |  |  | 0
0
2 | 300 amps TPN aluminium bus bars (25 kA) with coloured heat shrinkable insulation sleeve. |  |  |  | 0
0
3 | Electronic multi function meter of accuracy class-I, to measure and display the following electrical quantities : |  |  |  | 0
a. | Real Time parameter |  |  |  | 0
b. | Total active energy (KWH/MWH) |  |  |  | 0
c. | Maximum demand (KVA/MVA) (KW/MW) |  |  |  | 0
d. | Maximum demand reset count. |  |  |  | 0
e. | Instantaneous power factor |  |  |  | 0
f. | Logging of active energy eight time of a day |  |  |  | 0
g. | Current |  |  |  | 0
h. | Voltage |  |  |  | 0
i | Frequency / Harmonics |  |  |  | 0
j | Power factor |  |  |  | 0
k | RS -485 Port with THDi+THDv |  |  |  | 0
| 2 Set |  |  |  | 0
0
4 | Outgoing |  |  |  | 0
| 63 Amps 4P MCB 7 Nos. |  |  |  | 0
| 32 Amps 4P MCB 6 Nos. |  |  |  | 0
| 25 Amps 4P MCB 2 Nos. |  |  |  | 0
| 32 Amps DP MCB 4 Nos. |  |  |  | 0
| 25 Amps DP MCB 3 Nos. |  |  |  | 0
0
| Note:- |  |  |  | 0
| Panel shall be extensible type. |  |  |  | 0
| All incoming feeder shall be provided with extra pair of NO+NC contact set for BMS integration |  |  |  | 0
0
| UPS PANEL 2 described as above | Set | 1 |  | 0
0
11 | EXTERNAL FEEDER PILLAR PANEL-1 |  |  |  | 0
1 | Incoming |  |  |  | 0
i | 40 amps 4P MCCB (25kA) . |  |  |  | 0
| 1 set |  |  |  | 0
ii | Programmable Astrounomical timer with three distinct output |  |  |  | 0
| 3 set |  |  |  | 0
iii | 40 DP contactor with necessary NO& NC auxilliary contacts |  |  |  | 0
| 3 set |  |  |  | 0
| 3 Job control flexible cabling from contactor to Timer |  |  |  | 0
0
iv | 40amp DP RCCB (300mA) |  |  |  | 0
| 3 set |  |  |  | 0
0
2 | Bus Bars |  |  |  | 0
| 60 amps SPN aluminium bus bars (25 kA) with coloured heat shrinkable insulation sleeve. |  |  |  | 0
| 3 Set |  |  |  | 0
3 | Outgoing |  |  |  | 0
| 10 Amps DP MCB 30Nos. |  |  |  | 0
0
| External feeder pillar panel-1 described as above | Set | 1 |  | 0
0
12 | ISOLATOR PANEL DG (LOC. Site level) (OUTDOOR TYPE) |  |  |  | 0
| Incoming cum outgoing |  |  |  | 0
1 | 800amps 4P MCCB (25kA) with following accessories: |  |  |  | 0
0
i. | 0-500 volts digital electronic volt meter with in built selector switch protected by 6 amps TP MCB's. |  |  |  | 0
| 1 Set |  |  |  | 0
ii | Phase indicating light & Breaker ON/OFF/TRIP indication protected by Same MCB connected in PT. |  |  |  | 0
| 1 Set |  |  |  | 0
| ISOLATOR PANEL DG (LOC. Site level) (OUTDOOR TYPE) described as above | Set | 1 |  | 0
| TOTAL CARRIED OVER TO SUMMARY |  |  |  | 0
K | EXTERNAL PIPE WORK
1 | Supply and installation of following following size high density polyethylene corrugated two layers DWC pipe (Outer layer corrugated and inner surface plain and smooth) including Accessories like HDPE snap fit coupler with neoprene ‘O’ ring to make the joints water / damp proof. The pipe shall be laid burried and to be protective by brick/ stone bedding all around before directly burrying in soil.
a | 300 mm dia ID / 260mm ID | meter | 70 |  | 0
b | 200 mm dia ID / 175 mm ID | meter | RO
c | 110 mm dia ID / 95 mm ID | meter | 150 |  | 0
0
2 | Supplying and laying of following sizes of 10 KGF/ Cm2 pressure, HDPE coil pipe PE 80 IS:4984 on surface/buried in ground including cutting/filling/ trenching along with accessories etc. complete as required. |  |  |  | 0
a | 90mm inner diameter | RM | RO
| TOTAL CARRIED OVER TO SUMMARY |  |  |  | 0