## ELE BOQ
Project | VCONSTRUCT -1st, 2nd, 3rd FLOOR
Sl.No. | DESCRIPTION | UNIT | 13th | TOTAL | RATE |  | AMOUNT |  |  | MILESTONE | PRODUCT
[5 empty] | Supply | Installation | Supply | Installation | Total
I | LT PANELS :
A | All Panels Should be as per Technical specifications & Power distribution scheme
Supply, installation, testing & commisioning of 3 Phase, 4 wire, 415 V, 50 Hz panels. The fabrication shall be made with cold rolled annealed sheet with Machine pressing. The surface shall be rigorously treated for derusting in 7 tank process with powder coating. The panel shall be totally enclosed metal clad type with double gasketting with rubber / foam gasketting. The panel shall be off- white painted inside and shall be having control directory pasted on the inside surface of the panel door. The panel shall be suitable for mounting on existing trench and shall have cable entry provision from the top and bottom with suitable alley as the case may be. The panel shall be tested for the same KA rating of the relevant highest rating of breaker. All components shall be of approved make and shall have relevant IS/IEC approvals (Fabrication, drawing, list of components and panel detail shall be got approved before fabrication). The panel shall include base frame channel support.All complete as per relevant standard, technical specification, SLD, data sheets and direction of Engineer-in-charge.
Indoor type LT Switchboards, Floor mounting type, Bottom/Top entry. Refer enclosed SLD for component details.
Doors:2mm Body:2mm Gland Plate :3mm covers and partitions:1.6mm
IP class:IP52 for Indoor/IP55 with weather proof enclosure with top cover for outdoor
Bus bars: Electrolytic grade conductivity as per standard IS 5082
Bus bar Material: As per SLD
Bus bar supports: DMC/FRP/SMC
Bus bar joints: Shrouded/Tinned
Protection releases: As per SLD (Adjustable over current & short circuit unless otherwise specified)
Shade: Epoxy powder coated RAL 7032 for RP Panel & another colour for UPS Panel
Design: Modular type & Form 3B Construction
Cable entry: As per site condition
Bus bar insulation: Aluminum bus bars shall be bare with color coding at the ends/Copper shall be bare with color coding at the ends/For Humidified areas the copper bus bars shall be coated with tin.
Note:
1. The Panel shall be fully as per the requirement of CEIG/Electrical Inspectorate/ EB authorities.
2. Auxiliary contactor to be provided along with auto-manual switch where ever required.
3. All Breakers both Incoming & Outgoing shall have LED 'ON / OFF / TRIP' indications without fail.
4. CTs shall be of cast resin /polycarbonate split core type only.
5. All doors to have double rubber/foam gasket with shutter assembly & door seating frame.
6. All AC feeders will have time delays of 0-60 Seconds.
7. All MCCBs of 250A and above for non-ups loads will be microprocessor based only and all UPS Related panels shall be with thermal Magnetic releases only
8. All DLMs to be of dual source meters unless otherwise specified.Make:Elmeasure Model No EN 8410 with maximum demand parameter & RS 485 port or Equivalent
9. The current density for Aluminium busbars shall be 0.8 only.
10. The current density for Copper busbars shall be 1.6 only.
11. All UPS outgoing panels shall have neutral busbars double the size of phase & gland plates should be of alluminium.
12. All MCCB's shall have plug setting from (70 -100%) for < 250A & (40 - 100%) for > 250A
13. All Incomer ACB, MCCB's shall have 2nos. NO + 2nos of NC Auxiliary contacts for BMS integration. Seperate compartment to be provided for BMS cabling with dedicated connectors
14. All Lighting / RP and Lift panels shall have ELR with Rectangular CBCT for incomer.
15. All test certificates must be provided immediately after commissioning.
16. SAFETY CERTIFICATE FOR THE PANELS SHALL BE PRODUCED FROM CEIG.
17. All meters shall be Digital type only.
18. FRLS PVC copper wires shall be used for control wiring
19. Louvers shall be provided for all the bus bars chambers (Horizontal & Vertical) with mesh to meet IP Requirement.
20. All ACBs shall confirm IS 13947-1/IEC 947-1 for general rules & IS 13947 rules & IS 13947-2/IEC 947-2 for Circuit breakers.
21.All breakers shall have spreaders of same make as make of breaker.
22. Panel builder and Switchgear Manufacturer must ensure total selectivity between Upstream and Downstream Breakers for entire electrical distribution network . Switchgear manufacturer shall submit Total Discrimination report along with techno-commercial offer.
23. All vertical bus bars in bus bar alley shall have bottom supports.
24. Panel earthing strip should come out vertically on top/bottom of the panel to suit the site condition.
25. Earthing bus shall be with green colour coding.
27. Door earthings shall be provided for all doors.
28. Base frame shall be with each panel. The size shall be equal to each section.
29. Bi-metallic tape / washers to be used where ever copper & Aluminium are joined.
30. All MCCB's shall have flag indication for tripping.
31. The material of construction shall be CRCA sheet.
32. Live parts shall not be accessible after opening the door, Transparent acrylic sheet to be provided to cover the same & busbar joints section shall be covered with PVC shrouds.
33. In any case Aluminium bus bars should not be connected directly to the breaker without spreaders.
34. Panel should be as per IEC-60439
35. All UPS panels should be with copper bus bar.
36. Panels should be provided with Lifting lugs/ Eye bolts for lifting the panel.
37. All the busbar bolts of 8.8 Grade should be tightened for Torque of 23N-m for 8mm, 45N-m for 10mm, 80N-m for 12mm bolt/nuts using Torque wrench.
38. 3 Point Locks (Front Single Door) and Cam Locks are Provided (Compartments) for Front Doors.
39. Special Retaining washers are provided for busbar chambers to avoid the falling of the bolts from door.
40. Panel Costing shall include base frame also wherever false floor is proposed.600 mm Base frame to be considered for false floor
41. 45 Deg bending construction to achieve the IP.
42. For viewing MCB Chambers Polycarbonate (Unbreakable & High Temperature withstanding) sheets with glass frames to be used. Incoming Panel Meter should be same as Builder Tap -off Box meter
43. All PVC heat shrinkable sleeves should have temperature withstanding capacity of 105 degree celcius.
44. All ACB & MCCB Power feeders should be connected with Busbars.
Only resin cast C.T of suitable burden, class of accuracy, ratio and voltage shall be used as per the SLD
| 45. All breakers and energy should have BMS compatibility as per BMS schematic drawing provided. | [5 empty] | 0 | 0 | 0
|  |  |  | 0 |  |  | 0 | 0 | 0
1.1 | MAIN LT PANEL 13F | No. | 1 | 1 | 790240 | 35000 | 790240 | 35000 | 825240 | LT Panel Installation & Commissioning | 1 - Main LT Panel - Indoor Type
[7 empty] | 0 | 0 | 0
| Busbar: 315Amp FP Aluminium, 36kA | [5 empty] | 0 | 0 | 0
| Incomer 1 : 1Nos 250A Amp FP MCCB 3Ph 4 Wire,ELR - 1No. - EB Supply | [5 empty] | 0 | 0 | 0
| Incomer 2 : 1Nos 250A Amp FP MCCB 3Ph 4 Wire,ELR - 1No. - STAND BY EB Supply | [5 empty] | 0 | 0 | 0
| 1Nos 250 Amp FP ATS B 3Ph 4 Wire | [5 empty] | 0 | 0 | 0
| Source Load Manager- 1 Nos with RS 485 for BMS Integration | [5 empty] | 0 | 0 | 0
| 3 Nos. Phase Indicating Lamps, 3 Nos. On/Off/Trip Lamps | [5 empty] | 0 | 0 | 0
| 40kA Class( B+C) Surge Supressor - SPD | [5 empty] | 0 | 0 | 0
| Outgoings – | [5 empty] | 0 | 0 | 0
| 1) Light and Power Section: | [5 empty] | 0 | 0 | 0
| 63A 4P MCB 10kA C curve - 2Nos RPDB | [5 empty] | 0 | 0 | 0
| 40A 4P MCB 10kA C curve - 2Nos LDB | [5 empty] | 0 | 0 | 0
63/40A 4P MCB 10kA C curve - 1Nos ACDB
| 63/40A 4P MCB 10kA C curve - 3Nos SPARE | [5 empty] | 0 | 0 | 0
| 2) UPS Power Section: | [5 empty] | 0 | 0 | 0
| 250A 4P TMD MCCB 25kA- 0Nos 150A UPS | [5 empty] | 0 | 0 | 0
| 63A 4P TMD MCCB 25kA- 1Nos 20kVA UPS | [5 empty] | 0 | 0 | 0
| 63A/40A DP MCB 10kA C curve - 1Nos 6kVA UPS | [5 empty] | 0 | 0 | 0
| 32A DP MCB 10kA C curve - 1Nos 2kVA UPS | [5 empty] | 0 | 0 | 0
| 63/40A 2P MCB 10kA D curve - 2Nos SPARE | [5 empty] | 0 | 0 | 0
1.2 | 40/32A 2P MCB 10kA C curve - 1Nos SPARE | No. |  |  |  |  | 0 | 0 | 0 | LT Panel Installation & Commissioning
| 3) HVAC Section: 160A TMD MCCB 25kA with Load Manager (In case of fire main breaker should be tripped) | [5 empty] | 0 | 0 | 0
| 63/40A 4P MCB 10kA C curve - 4Nos ODU | [5 empty] | 0 | 0 | 0
| 40/25A 4P MCB 10kA C curve - 1Nos TFA | [5 empty] | 0 | 0 | 0
| 63/40A 2P MCB 10kA C curve - 2Nos Critical Room AC | [5 empty] | 0 | 0 | 0
| 63/40A 4P MCB 10kA C curve - 3Nos SPARE | [5 empty] | 0 | 0 | 0
| 40/32A 2P MCB 10kA C curve - 3Nos SPARE | [5 empty] | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
| 4) APFC Section. | [5 empty] | 0 | 0 | 0
| 125 FP TMD MCCB, 25kA, -1 No. | [5 empty] | 0 | 0 | 0
| Automatic power factor correction system of capacity of 45 KVAR capacity Banks with APP. power capacitor duly wired for power and control wiring with detuned reactors. | [5 empty] | 0 | 0 | 0
| APFC panels will have system display indicating voltage, current, capacitor current, power factor, active-reactive power, harmonics etc. | [5 empty] | 0 | 0 | 0
| APFC panels will be totally automatic and can set power factor. 0.85 lag to 0.99 lag in steps of 0.01 with contactor based switching | [5 empty] | 0 | 0 | 0
| Auxiliary contacts in DG supply incomer to be used to provide interlock to switch off APFCR panel when DG is On. | [5 empty] | 0 | 0 | 0
| As per SLD to be provided. | [5 empty] | 0 | 0 | 0
| Providing On/Off/ Trip status contact of incoming breakers for BMS | [5 empty] | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
1.2 | UPS OUTPUT PANEL | No. | 1 | 1 | 137250 | 10000 | 137250 | 10000 | 147250 | LT Panel Installation & Commissioning | 1 - UPS Output Panel - Indoor Type
[7 empty] | 0 | 0 | 0
| Busbar: 63Amp FP Copper, 25kA | [5 empty] | 0 | 0 | 0
| Incomer 1 : 1Nos 63A Amp FP ACB 3Ph 4 Wire,ELR - 1No. - EB Supply | [5 empty] | 0 | 0 | 0
| Source Load Manager- 1 Nos with RS 485 for BMS Integration | [5 empty] | 0 | 0 | 0
3 Nos. Phase Indicating Lamps, 3 Nos. On/Off/Trip Lamps
Outgoings –
40kA Class( B+C) Surge Supressor - SPD
40A 4P MCB 10kA D curve - 2Nos UPSDB
63A 4P TMD MCCB 16kA - 0Nos SPARE
| 63/40A 2P MCB 10kA C curve - 4Nos SPARE | [5 empty] | 0 | 0 | 0
1.3 | HVAC PANEL - (IP65 OUTDOOR) | No |  |  |  |  | 0 | 0 | 0 | LT Panel Installation & Commissioning | 1 - Main LT Panel - Indoor Type
| SITC of MS structure for outdoor HVAC panel installation on terrace, made out of MS channels/angles (minimum 50×50×6 mm or as required), complete with base frame, supports, stiffeners, and mounting arrangement for panel, including anti-corrosive treatment (red oxide primer + two coats of enamel paint / hot dip galvanizing), grouting/anchoring on terrace floor with necessary hardware, rubber pads for vibration isolation, all nuts, bolts, and accessories, complete in all respects as per site requirement | [5 empty] | 0 | 0 | 0
| 3) HVAC Section: 630A TMD MCCB(ST) 25kA with Load Manager (In case of fire main breaker should be tripped) | [5 empty] | 0 | 0 | 0
| 100A TMD MCCB 16kA - 1Nos for 23HP ODU | [5 empty] | 0 | 0 | 0
| 63/40A 4P MCB 10kA C curve - 23Nos ODU | [5 empty] | 0 | 0 | 0
| 63/40A 4P MCB 10kA C curve - 5Nos SPARE | [5 empty] | 0 | 0 | 0
| 40/32A 2P MCB 10kA C curve - 2Nos SPARE | [5 empty] | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
1.4 | 63A , 4P MCOS FOR CRITICAL HVAC UNITS | No. |  |  |  |  | 0 | 0 | 0 | LT Panel Installation & Commissioning
[7 empty] | 0 | 0 | 0
1.5 | 40A , 4P MCOS FOR CRITICAL HVAC UNITS | No. |  |  |  |  | 0 | 0 | 0 | LT Panel Installation & Commissioning
[7 empty] | 0 | 0 | 0
B | Supply, Installation, testing & commisioning of Fully Automatic DOL/ Star Delta starters with features like Local/Remote, Auto/Manual & programmable timer for auto operation. The necessary NO NC shall be provided with BMS compatibility. The space provision for VFD with bypass facility shall be provided wherever it is specified as below. Starters will be used in case of VFD Panel Maintenance/Failure. Starters to be tripped in case of fire, hence necessary contactors for the same to be provided.The cost shall include free standing support for starter Isolator Box | [5 empty] | 0 | 0 | 0
| INDOOR TYPE - IP 52 | [5 empty] | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
1.51 | 0.5 kW DOL Starter | No. |  |  |  |  | 0 | 0 | 0 | LT Panel Installation & Commissioning
[7 empty] | 0 | 0 | 0
1.52 | 1.0 kW DOL Starter | No. |  |  |  |  | 0 | 0 | 0 | LT Panel Installation & Commissioning
[7 empty] | 0 | 0 | 0
1.53 | 1.5kW DOL Starter | No. |  |  |  |  | 0 | 0 | 0 | LT Panel Installation & Commissioning
[7 empty] | 0 | 0 | 0
1.54 | 2.2 kW DOL Starter | No. |  |  |  |  | 0 | 0 | 0 | LT Panel Installation & Commissioning
[7 empty] | 0 | 0 | 0
1.55 | 4.4 kW DOL Starter | No. |  |  |  |  | 0 | 0 | 0 | LT Panel Installation & Commissioning
[7 empty] | 0 | 0 | 0
1.56 | 5.5kW Star/Delta Starter with VFD Space Provision | No. |  |  |  |  | 0 | 0 | 0 | LT Panel Installation & Commissioning
[7 empty] | 0 | 0 | 0
1.57 | 7.5kW Star/Delta Starter with VFD Space Provision | No. |  |  |  |  | 0 | 0 | 0 | LT Panel Installation & Commissioning
[7 empty] | 0 | 0 | 0
1.58 | 9.3kW Star/Delta Starter with VFD Space Provision | No. |  |  |  |  | 0 | 0 | 0 | LT Panel Installation & Commissioning
[7 empty] | 0 | 0 | 0
1.59 | 11kW Star/Delta Starter with VFD Space Provision | No. |  |  |  |  | 0 | 0 | 0 | LT Panel Installation & Commissioning
[7 empty] | 0 | 0 | 0
1.6 | 15kW Star/Delta Starter with VFD Space Provision | No. |  |  |  |  | 0 | 0 | 0 | LT Panel Installation & Commissioning
[7 empty] | 0 | 0 | 0
| OUTDOOR TYPE - IP 55 | [5 empty] | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
1.61 | 0.5 kW DOL Starter | No. |  |  |  |  | 0 | 0 | 0 | LT Panel Installation & Commissioning
[7 empty] | 0 | 0 | 0
1.62 | 1.0 kW DOL Starter | No. |  |  |  |  | 0 | 0 | 0 | LT Panel Installation & Commissioning
[7 empty] | 0 | 0 | 0
1.63 | 1.5kW DOL Starter | No. |  |  |  |  | 0 | 0 | 0 | LT Panel Installation & Commissioning
[7 empty] | 0 | 0 | 0
1.64 | 2.2 kW DOL Starter | No. |  |  |  |  | 0 | 0 | 0 | LT Panel Installation & Commissioning
[7 empty] | 0 | 0 | 0
1.65 | 4.4 kW DOL Starter | No. |  |  |  |  | 0 | 0 | 0 | LT Panel Installation & Commissioning
[7 empty] | 0 | 0 | 0
1.66 | 5.5kW Star/Delta Starter with VFD Space Provision | No. |  |  |  |  | 0 | 0 | 0 | LT Panel Installation & Commissioning
[7 empty] | 0 | 0 | 0
1.67 | 7.5kW Star/Delta Starter with VFD Space Provision | No. |  |  |  |  | 0 | 0 | 0 | LT Panel Installation & Commissioning
[7 empty] | 0 | 0 | 0
1.68 | 9.3kW Star/Delta Starter with VFD Space Provision | No. |  |  |  |  | 0 | 0 | 0 | LT Panel Installation & Commissioning
[7 empty] | 0 | 0 | 0
1.69 | 11kW Star/Delta Starter with VFD Space Provision | No. |  |  |  |  | 0 | 0 | 0 | LT Panel Installation & Commissioning
[7 empty] | 0 | 0 | 0
1.7 | 15kW Star/Delta Starter with VFD Space Provision | No. |  |  |  |  | 0 | 0 | 0 | LT Panel Installation & Commissioning
[7 empty] | 0 | 0 | 0
C | 4P MCCB BOX wall Mounting type polycarbonate enclosures | [5 empty] | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
| INDOOR TYPE - IP 52 (Ka Rating - 36ka ) | [5 empty] | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
1.71 | 25A to 100A | No. |  |  |  |  | 0 | 0 | 0 | LT Panel Installation & Commissioning | 1 - 25A TP MCB C CURVE, 1 - 32A TP MCB C CURVE, 1 - 40A TP MCB C CURVE, 1 - 63A TP MCCB 10kA, 1 - 80A FP MCCB, 1 - 100A FP MCCB
[7 empty] | 0 | 0 | 0
1.72 | 125A to 160A | No. |  |  |  |  | 0 | 0 | 0 | LT Panel Installation & Commissioning | 1 - 125A FP MCCB, 1 - 125A TP MCCB 10kA
[7 empty] | 0 | 0 | 0
1.73 | 200A to 250A | No. |  |  |  |  | 0 | 0 | 0 | LT Panel Installation & Commissioning | 1 - Adaptor Box With 250A MCCB & AL Busbar
[7 empty] | 0 | 0 | 0
1.74 | 400A to 630A | No. |  |  |  |  | 0 | 0 | 0 | LT Panel Installation & Commissioning | 1 - Adaptor Box With 320A MCCB & AL Busbar, 1 - Adapter Box - 320A Al Busbar
[7 empty] | 0 | 0 | 0
1.75 | 800A | No. |  |  |  |  | 0 | 0 | 0 | LT Panel Installation & Commissioning
[7 empty] | 0 | 0 | 0
| OUTDOOR TYPE - IP 55 (Ka Rating - 36ka ) | [5 empty] | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
1.76 | 20A MCB | No. |  |  |  |  | 0 | 0 | 0 | LT Panel Installation & Commissioning | 1 - 20A SP MCB C CURVE, 1 - 20A SP MCB D CURVE
[7 empty] | 0 | 0 | 0
1.77 | 40A MCB | No. |  |  |  |  | 0 | 0 | 0 | LT Panel Installation & Commissioning | 1 - 40A FP MCB C CURVE, 1 - 40A FP MCB D CURVE
[7 empty] | 0 | 0 | 0
1.78 | 63A MCB | No. |  |  |  |  | 0 | 0 | 0 | LT Panel Installation & Commissioning | 1 - 63A FP MCB C CURVE, 1 - 63A FP MCB D CURVE
[7 empty] | 0 | 0 | 0
1.79 | 25A to 100A | No. |  |  |  |  | 0 | 0 | 0 | LT Panel Installation & Commissioning | 1 - 25A TP MCB C CURVE, 1 - 32A TP MCB C CURVE, 1 - 40A TP MCB C CURVE, 1 - 63A TP MCCB 10kA, 1 - 80A FP MCCB, 1 - 100A FP MCCB
[7 empty] | 0 | 0 | 0
1.8 | 125A to 160A | No. |  |  |  |  | 0 | 0 | 0 | LT Panel Installation & Commissioning | 1 - 125A FP MCCB, 1 - 125A TP MCCB 10kA
[7 empty] | 0 | 0 | 0
1.81 | 200A to 250A | No. |  |  |  |  | 0 | 0 | 0 | LT Panel Installation & Commissioning | 1 - Adaptor Box With 250A MCCB & AL Busbar
[7 empty] | 0 | 0 | 0
1.82 | 400A to 630A | No. |  |  |  |  | 0 | 0 | 0 | LT Panel Installation & Commissioning | 1 - Adaptor Box With 320A MCCB & AL Busbar, 1 - Adapter Box - 320A Al Busbar
[7 empty] | 0 | 0 | 0
1.83 | 1600A | No. |  |  |  |  | 0 | 0 | 0 | LT Panel Installation & Commissioning
[7 empty] | 0 | 0 | 0
II | LT CABLES & ENDTERMINATIONS | [5 empty] | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
| Supply, Laying, Testing and Commissioning of stranded FRLS XLPE/PVC insulated, Armoured/Unarmoured/Flexible, Aluminum / Copper conductor, laid in tray / hume pipe / in ready made trenches, with nylon cable ties. The cost of the nylon tie shall be included in the cost of installation. | [5 empty] | 0 | 0 | 0
| Cable identification labels at both ends clearly mentioning the cable specs & also at appropriate intervals along the cable route should be provided. The labels shall be engraved / anodized aluminium with white letters on black background. The cost of the Cable identification labels shall be included in the cost of installation & Only heavy duty cable ties should be used for cable dressing. | [5 empty] | 0 | 0 | 0
| Supply, Installation, Testing and Commissioning of double Compression type cable gland, aluminum lugs for aluminum cables / copper lugs for copper cables, insulation tape, anti corrosive paste, brass clamps for gland earthing with 14 SWG copper wire to connect to nearest earth flat. | [5 empty] | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
| Inner sheath: Extruded PVC only for Multicore | [5 empty] | 0 | 0 | 0
| Outer sheath: Extruded Type ST2 PVC with FLAME RETARDANT LESS SMOKE | [5 empty] | 0 | 0 | 0
| Voltage grade:1100Volts | [5 empty] | 0 | 0 | 0
| Armoure: Galvanized Steel strip/Wire for multicore | [5 empty] | 0 | 0 | 0
| Non Magnetic Aluminum Wire/Strip for Single core | [5 empty] | 0 | 0 | 0
| Gland type : Brass with nickel plated | [5 empty] | 0 | 0 | 0
| All Glands used should be of double compression for 35 Sq.mm & Above | [5 empty] | 0 | 0 | 0
| PG glands should be used for copper flexible cables. | [5 empty] | 0 | 0 | 0
| Sealing Ring : Natural rubber for indoor, Neoprene for Outdoor | [5 empty] | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
A | FRLS XLPE Insulated & Steel Armoured Aluminium/Copper Conductor Cables | [5 empty] | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
2.1 | 3.5 Core X 400 Sqmm | Mts |  |  |  |  | 0 | 0 | 0 | DB To Panel Cabling - LT Cables | 1 - LUGS / THIMBLE 240 SQMM RING TYPE - ALUMINIUM
2.2 | Endterminations | Nos. |  |  |  |  | 0 | 0 | 0 | DB To Panel Cabling - LT Cables | 1 - 70MM Double Compression Gland
[7 empty] | 0 | 0 | 0
2.3 | 3.5 Core X 300 Sqmm | Mts |  |  |  |  | 0 | 0 | 0 | DB To Panel Cabling - LT Cables | 1 - 3.5CX300 SQMM ALUMINIUM ARMOURED CABLE, 1 - LUGS / THIMBLE 240 SQMM RING TYPE - ALUMINIUM
2.4 | Endterminations | Nos. |  |  |  |  | 0 | 0 | 0 | DB To Panel Cabling - LT Cables | 1 - 63MM Double Compression Gland
[7 empty] | 0 | 0 | 0
2.5 | 3.5 Core X 240 Sqmm | Mts | 180 | 180 | 1600 | 130 | 288000 | 23400 | 311400 | DB To Panel Cabling - LT Cables | 180 - 3.5CX240 SQMM ALUMINIUM ARMOURED CABLE, 180 - LUGS / THIMBLE 240 SQMM RING TYPE - ALUMINIUM
2.6 | Endterminations | Nos. | 10 | 10 | 2610 | 660 | 26100 | 6600 | 32700 | DB To Panel Cabling - LT Cables | 10 - 63MM Double Compression Gland
[7 empty] | 0 | 0 | 0
2.7 | 3.5 Core X 185 Sqmm | Mts |  |  |  |  | 0 | 0 | 0 | DB To Panel Cabling - LT Cables | 1 - 3.5CX185 SQMM ALUMINIUM ARMOURED CABLE, 1 - LUGS / THIMBLE 240 SQMM RING TYPE - ALUMINIUM
2.8 | Endterminations | Nos. |  |  |  |  | 0 | 0 | 0 | DB To Panel Cabling - LT Cables | 1 - 57MM Double Compression Gland
[7 empty] | 0 | 0 | 0
2.9 | 3.5 Core X 150 Sqmm | Mts |  |  |  |  | 0 | 0 | 0 | DB To Panel Cabling - LT Cables | 1 - 3.5CX150 SQMM ALUMINIUM ARMOURED CABLE, 1 - LUGS / THIMBLE 150 SQMM RING TYPE - ALUMINIUM
2.1 | Endterminations | Nos. |  |  |  |  | 0 | 0 | 0 | DB To Panel Cabling - LT Cables | 1 - 45MM Double Compression Gland
[7 empty] | 0 | 0 | 0
2.11 | 3.5 Core X 120 Sqmm | Mts |  |  |  |  | 0 | 0 | 0 | DB To Panel Cabling - LT Cables | 1 - LUGS / THIMBLE 150 SQMM RING TYPE - ALUMINIUM
2.12 | Endterminations | Nos. |  |  |  |  | 0 | 0 | 0 | DB To Panel Cabling - LT Cables | 1 - 45MM Double Compression Gland
[7 empty] | 0 | 0 | 0
2.13 | 3.5 Core X 95 Sqmm | Mts |  |  |  |  | 0 | 0 | 0 | DB To Panel Cabling - LT Cables | 1 - 3.5CX95 SQMM ALUMINIUM ARMOURED CABLE, 1 - LUGS / THIMBLE 70 SQMM RING TYPE - ALUMINIUM
2.14 | Endterminations | Nos. |  |  |  |  | 0 | 0 | 0 | DB To Panel Cabling - LT Cables | 1 - 38MM Single Compression Gland
[7 empty] | 0 | 0 | 0
2.15 | 3.5 Core X 70 Sqmm | Mts |  |  |  |  | 0 | 0 | 0 | DB To Panel Cabling - LT Cables | 1 - 3.5CX70 SQMM ALUMINIUM ARMOURED CABLE, 1 - LUGS / THIMBLE 70 SQMM RING TYPE - ALUMINIUM
2.16 | Endterminations | Nos. |  |  |  |  | 0 | 0 | 0 | DB To Panel Cabling - LT Cables | 1 - 35MM Double Compression Gland
[7 empty] | 0 | 0 | 0
2.17 | 3.5 Core X 50 Sqmm | Mts |  |  |  |  | 0 | 0 | 0 | DB To Panel Cabling - LT Cables | 1 - 3.5CX50 SQMM ALUMINIUM ARMOURED CABLE, 1 - LUGS / THIMBLE 50 SQMM PIN TYPE - ALUMINIUM
2.18 | Endterminations | Nos. |  |  |  |  | 0 | 0 | 0 | DB To Panel Cabling - LT Cables | 1 - 32MM Double Compression Gland
[7 empty] | 0 | 0 | 0
2.19 | 3.5 Core X 35 Sqmm | Mts |  |  |  |  | 0 | 0 | 0 | DB To Panel Cabling - LT Cables | 1 - 3.5CX35 SQMM ALUMINIUM ARMOURED CABLE, 1 - LUGS / THIMBLE 35 SQMM PIN TYPE - ALUMINIUM
2.2 | Endterminations | Nos. |  |  |  |  | 0 | 0 | 0 | DB To Panel Cabling - LT Cables | 1 - 32MM Double Compression Gland
[7 empty] | 0 | 0 | 0
2.21 | 4 Core X 35 Sqmm Cu Cable | Mts |  |  |  |  | 0 | 0 | 0 | DB To Panel Cabling - LT Cables | 1 - LUGS / THIMBLE 35 SQMM PIN TYPE - COPPER
2.22 | Endterminations | Nos. |  |  |  |  | 0 | 0 | 0 | DB To Panel Cabling - LT Cables | 1 - 32MM Double Compression Gland
[7 empty] | 0 | 0 | 0
2.22 | 4 Core X 25 Sqmm Cu Cable | Mts |  |  |  |  | 0 | 0 | 0 | DB To Panel Cabling - LT Cables | 1 - 4CX25 SQMM COPPER ARMOURED CABLE, 1 - LUGS / THIMBLE 25 SQMM PIN TYPE - COPPER
2.23 | Endterminations | Nos. |  |  |  |  | 0 | 0 | 0 | DB To Panel Cabling - LT Cables | 1 - 28MM Double Compression Gland
[7 empty] | 0 | 0 | 0
2.24 | 4 Core X 16 Sqmm Cu Cable | Mts | 20 | 20 | 1240 | 40 | 24800 | 800 | 25600 | DB To Panel Cabling - LT Cables | 20 - 4CX16 SQMM COPPER ARMOURED CABLE, 20 - LUGS / THIMBLE 25 SQMM PIN TYPE - COPPER
2.25 | Endterminations | Nos. | 4 | 4 | 140 | 40 | 560 | 160 | 720 | DB To Panel Cabling - LT Cables | 4 - 25MM Double Compression Gland
[7 empty] | 0 | 0 | 0
2.26 | 4 Core X 10 Sqmm Cu Cable | Mts | 20 | 20 | 840 | 30 | 16800 | 600 | 17400 | DB To Panel Cabling - LT Cables | 20 - 4CX10 SQMM COPPER ARMOURED CABLE, 20 - LUGS / THIMBLE 25 SQMM PIN TYPE - COPPER
2.27 | Endterminations | Nos. | 4 | 4 | 100 | 30 | 400 | 120 | 520 | DB To Panel Cabling - LT Cables | 4 - 25MM Double Compression Gland
[7 empty] | 0 | 0 | 0
2.28 | 4 Core X 6 Sqmm Cu Cable | Mts |  |  |  |  | 0 | 0 | 0 | DB To Panel Cabling - LT Cables | 1 - 4CX6 SQMM COPPER ARMOURED CABLE, 1 - LUGS / THIMBLE 4 SQMM RING TYPE - COPPER
2.29 | Endterminations | Nos. |  |  |  |  | 0 | 0 | 0 | DB To Panel Cabling - LT Cables | 1 - 19MM Double Compression Gland
[7 empty] | 0 | 0 | 0
2.3 | 4 Core X 4 Sqmm Cu Cable | Mts |  |  |  |  | 0 | 0 | 0 | DB To Panel Cabling - LT Cables | 1 - 4CX4 SQMM COPPER ARMORED CABLE, 1 - LUGS / THIMBLE 4 SQMM RING TYPE - COPPER
2.31 | Endterminations | Nos. |  |  |  |  | 0 | 0 | 0 | DB To Panel Cabling - LT Cables | 1 - 19MM Double Compression Gland
[7 empty] | 0 | 0 | 0
2.32 | 3 Core X 16 Sqmm Cu Cable | Mts |  |  |  |  | 0 | 0 | 0 | DB To Panel Cabling - LT Cables | 1 - LUGS / THIMBLE 25 SQMM PIN TYPE - COPPER
2.33 | Endterminations | Nos. |  |  |  |  | 0 | 0 | 0 | DB To Panel Cabling - LT Cables | 1 - 25MM Double Compression Gland
[7 empty] | 0 | 0 | 0
2.34 | 3 Core X 10 Sqmm Cu Cable | Mts |  |  |  |  | 0 | 0 | 0 | DB To Panel Cabling - LT Cables | 1 - 3CX10 SQMM COPPER ARMOURED CABLE, 1 - LUGS / THIMBLE 25 SQMM PIN TYPE - COPPER
2.35 | Endterminations | Nos. |  |  |  |  | 0 | 0 | 0 | DB To Panel Cabling - LT Cables | 1 - 25MM Double Compression Gland
[7 empty] | 0 | 0 | 0
2.36 | 3 Core X 6 Sqmm Cu Cable | Mts |  |  |  |  | 0 | 0 | 0 | DB To Panel Cabling - LT Cables | 1 - 3CX6 SQMM FRLS COPPER ARMOURED CABLE, 1 - LUGS / THIMBLE 4 SQMM RING TYPE - COPPER
2.37 | Endterminations | Nos. |  |  |  |  | 0 | 0 | 0 | DB To Panel Cabling - LT Cables | 1 - 19MM Double Compression Gland
[7 empty] | 0 | 0 | 0
2.38 | 3 Core X 4 Sqmm Cu Cable | Mts |  |  |  |  | 0 | 0 | 0 | DB To Panel Cabling - LT Cables | 1 - 3CX4 SQMM FRLS COPPER ARMOURED CABLE, 1 - LUGS / THIMBLE 4 SQMM RING TYPE - COPPER
2.39 | Endterminations | Nos. |  |  |  |  | 0 | 0 | 0 | DB To Panel Cabling - LT Cables | 1 - 19MM Double Compression Gland
[7 empty] | 0 | 0 | 0
2.4 | 3 Core X 2.5 Sqmm Cu Cable | Mts |  |  |  |  | 0 | 0 | 0 | DB To Panel Cabling - LT Cables | 1 - LUGS / THIMBLE 2.5 SQMM RING TYPE - COPPER
2.41 | Endterminations | Nos. |  |  |  |  | 0 | 0 | 0 | DB To Panel Cabling - LT Cables | 1 - 19MM Double Compression Gland
[7 empty] | 0 | 0 | 0
2.42 | 3 Core X 1.5 Sqmm Cu Cable | Mts |  |  |  |  | 0 | 0 | 0 | DB To Panel Cabling - LT Cables | 1 - LUGS / THIMBLE 2.5 SQMM RING TYPE - COPPER
2.43 | Endterminations | Nos. |  |  |  |  | 0 | 0 | 0 | DB To Panel Cabling - LT Cables | 1 - 19MM Double Compression Gland
[7 empty] | 0 | 0 | 0
B | FRLS PVC Insulated & Un Armoured Copper Conductor cables (YY Type) - IS 694 | [5 empty] | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
2.44 | 1 Core x 400 Sq. mm | Mts |  |  |  |  | 0 | 0 | 0 | DB To Panel Cabling - LT Cables | 1 - LUGS / THIMBLE 150 SQMM RING TYPE - COPPER
2.45 | Endterminations | Nos. |  |  |  |  | 0 | 0 | 0 | DB To Panel Cabling - LT Cables | 1 - 32MM PG Gland
[7 empty] | 0 | 0 | 0
2.46 | 1 Core x 300 Sq. mm | Mts |  |  |  |  | 0 | 0 | 0 | DB To Panel Cabling - LT Cables | 1 - LUGS / THIMBLE 150 SQMM RING TYPE - COPPER
2.47 | Endterminations | Nos. |  |  |  |  | 0 | 0 | 0 | DB To Panel Cabling - LT Cables | 1 - 32MM PG Gland
[7 empty] | 0 | 0 | 0
2.48 | 1 Core x 240 Sq. mm | Mts |  |  |  |  | 0 | 0 | 0 | DB To Panel Cabling - LT Cables | 1 - LUGS / THIMBLE 150 SQMM RING TYPE - COPPER
2.49 | Endterminations | Nos. |  |  |  |  | 0 | 0 | 0 | DB To Panel Cabling - LT Cables | 1 - 32MM PG Gland
[7 empty] | 0 | 0 | 0
2.5 | 1 Core x 185 Sq. mm | Mts |  |  |  |  | 0 | 0 | 0 | DB To Panel Cabling - LT Cables | 1 - LUGS / THIMBLE 150 SQMM RING TYPE - COPPER
2.51 | Endterminations | Nos. |  |  |  |  | 0 | 0 | 0 | DB To Panel Cabling - LT Cables | 1 - 32MM PG Gland
[7 empty] | 0 | 0 | 0
2.52 | 1 Core x 150 Sq. mm | Mts |  |  |  |  | 0 | 0 | 0 | DB To Panel Cabling - LT Cables | 1 - 150 SQMM COPPER WIRE BLACK, 1 - LUGS / THIMBLE 150 SQMM RING TYPE - COPPER
2.53 | Endterminations | Nos. |  |  |  |  | 0 | 0 | 0 | DB To Panel Cabling - LT Cables | 1 - 32MM PG Gland
[7 empty] | 0 | 0 | 0
2.54 | 1 Core x 120 Sq. mm | Mts |  |  |  |  | 0 | 0 | 0 | DB To Panel Cabling - LT Cables | 1 - 120 SQMM COPPER WIRE BLACK, 1 - LUGS / THIMBLE 120 SQMM RING TYPE - COPPER
2.55 | Endterminations | Nos. |  |  |  |  | 0 | 0 | 0 | DB To Panel Cabling - LT Cables | 1 - 32MM PG Gland
[7 empty] | 0 | 0 | 0
2.56 | 1 Core x 95 Sq. mm | Mts |  |  |  |  | 0 | 0 | 0 | DB To Panel Cabling - LT Cables | 1 - LUGS / THIMBLE 95 SQMM RING TYPE - COPPER
2.57 | Endterminations | Nos. |  |  |  |  | 0 | 0 | 0 | DB To Panel Cabling - LT Cables | 1 - 32MM PG Gland
[7 empty] | 0 | 0 | 0
2.58 | 1 Core x 70 Sq. mm | Mts |  |  |  |  | 0 | 0 | 0 | DB To Panel Cabling - LT Cables | 1 - LUGS / THIMBLE 70 SQMM RING TYPE - COPPER
2.59 | Endterminations | Nos. |  |  |  |  | 0 | 0 | 0 | DB To Panel Cabling - LT Cables | 1 - 32MM PG Gland
[7 empty] | 0 | 0 | 0
2.6 | 1 Core x 50 Sq. mm | Mts |  |  |  |  | 0 | 0 | 0 | DB To Panel Cabling - LT Cables | 1 - LUGS / THIMBLE 50 SQMM RING TYPE - COPPER
2.61 | Endterminations | Nos. |  |  |  |  | 0 | 0 | 0 | DB To Panel Cabling - LT Cables | 1 - 29MM PG Gland
[7 empty] | 0 | 0 | 0
2.62 | 1 Core x 35 Sq. mm | Mts |  |  |  |  | 0 | 0 | 0 | DB To Panel Cabling - LT Cables | 1 - LUGS / THIMBLE 35 SQMM PIN TYPE - COPPER
2.63 | Endterminations | Nos. |  |  |  |  | 0 | 0 | 0 | DB To Panel Cabling - LT Cables | 1 - 28MM PG Gland
[7 empty] | 0 | 0 | 0
2.64 | 1 Core x 25 Sq. mm | Mts | 80 | 80 | 500 | 30 | 40000 | 2400 | 42400 | DB To Panel Cabling - LT Cables | 80 - 25 SQMM COPPER WIRE BLACK, 80 - LUGS / THIMBLE 25 SQMM PIN TYPE - COPPER
2.65 | Endterminations | Nos. | 18 | 18 | 130 | 40 | 2340 | 720 | 3060 | DB To Panel Cabling - LT Cables | 18 - 25MM PG Gland
[7 empty] | 0 | 0 | 0
2.66 | 1 Core x 16 Sq. mm | Mts |  |  |  |  | 0 | 0 | 0 | DB To Panel Cabling - LT Cables | 1 - 16 SQMM FRLS COPPER WIRE BLACK, 1 - LUGS / THIMBLE 25 SQMM PIN TYPE - COPPER
2.67 | Endterminations | Nos. |  |  |  |  | 0 | 0 | 0 | DB To Panel Cabling - LT Cables | 1 - 25MM PG Gland
[7 empty] | 0 | 0 | 0
2.68 | 1 Core x 10 Sq. mm | Mts |  |  |  |  | 0 | 0 | 0 | DB To Panel Cabling - LT Cables | 1 - 10 SQMM FRLS COPPER WIRE BLACK, 1 - LUGS / THIMBLE 25 SQMM PIN TYPE - COPPER
2.69 | Endterminations | Nos. |  |  |  |  | 0 | 0 | 0 | DB To Panel Cabling - LT Cables | 1 - 25MM PG Gland
[7 empty] | 0 | 0 | 0
2.7 | 1 Core x 6 Sq. mm | Mts | 80 | 80 | 120 | 20 | 9600 | 1600 | 11200 | DB To Panel Cabling - LT Cables | 80 - 6 SQMM FRLS COPPER WIRE BLACK, 80 - LUGS / THIMBLE 4 SQMM RING TYPE - COPPER
2.71 | Endterminations | Nos. | 12 | 12 | 80 | 20 | 960 | 240 | 1200 | DB To Panel Cabling - LT Cables | 12 - 21MM PG Gland
[7 empty] | 0 | 0 | 0
2.72 | 1 Core x 4 Sq. mm | Mts | 80 | 80 | 80 | 20 | 6400 | 1600 | 8000 | DB To Panel Cabling - LT Cables | 80 - 4 SQMM FRLS COPPER WIRE BLACK, 80 - LUGS / THIMBLE 4 SQMM RING TYPE - COPPER
2.73 | Endterminations | Nos. | 12 | 12 | 70 | 20 | 840 | 240 | 1080 | DB To Panel Cabling - LT Cables | 12 - 19MM PG Gland
[7 empty] | 0 | 0 | 0
2.74 | 1 Core x 2.5 Sq. mm | Mts |  |  |  |  | 0 | 0 | 0 | DB To Panel Cabling - LT Cables | 1 - 2.5 SQMM FRLS COPPER WIRE BLACK, 1 - LUGS / THIMBLE 2.5 SQMM RING TYPE - COPPER
2.75 | Endterminations | Nos. |  |  |  |  | 0 | 0 | 0 | DB To Panel Cabling - LT Cables | 1 - 19MM PG Gland
[7 empty] | 0 | 0 | 0
2.76 | 1 Core x 1.5 Sq. mm | Mts |  |  |  |  | 0 | 0 | 0 | DB To Panel Cabling - LT Cables | 1 - 1.5 SQMM FRLS COPPER WIRE BLACK, 1 - LUGS / THIMBLE 2.5 SQMM RING TYPE - COPPER
2.77 | Endterminations | Nos. |  |  |  |  | 0 | 0 | 0 | DB To Panel Cabling - LT Cables | 1 - 19MM PG Gland
[7 empty] | 0 | 0 | 0
2.78 | 3 Core x 10Sq. mm | Mts |  |  |  |  | 0 | 0 | 0 | DB To Panel Cabling - LT Cables | 1 - 3CX10 SQMM COPPER ARMOURED CABLE, 1 - LUGS / THIMBLE 25 SQMM PIN TYPE - COPPER
2.79 | Endterminations | Nos. |  |  |  |  | 0 | 0 | 0 | DB To Panel Cabling - LT Cables | 1 - 25MM PG Gland
[7 empty] | 0 | 0 | 0
2.8 | 3 Core x 6 Sq. mm | Mts |  |  |  |  | 0 | 0 | 0 | DB To Panel Cabling - LT Cables | 1 - 3CX6 SQMM FRLS COPPER FLEXIBLE CABLE, 1 - LUGS / THIMBLE 4 SQMM RING TYPE - COPPER
2.81 | Endterminations | Nos. |  |  |  |  | 0 | 0 | 0 | DB To Panel Cabling - LT Cables | 1 - 21MM PG Gland
[7 empty] | 0 | 0 | 0
2.82 | 3 Core x 4 Sq. mm | Mts |  |  |  |  | 0 | 0 | 0 | DB To Panel Cabling - LT Cables | 1 - 3CX4 SQMM FRLS COPPER FLEXIBLE CABLE, 1 - LUGS / THIMBLE 4 SQMM RING TYPE - COPPER
2.83 | Endterminations | Nos. |  |  |  |  | 0 | 0 | 0 | DB To Panel Cabling - LT Cables | 1 - 19MM PG Gland
[7 empty] | 0 | 0 | 0
2.84 | 3 Core x 2.5 Sq. mm | Mts |  |  |  |  | 0 | 0 | 0 | DB To Panel Cabling - LT Cables | 1 - 3CX2.5 SQMM FRLS COPPER FLEXIBLE CABLE, 1 - LUGS / THIMBLE 2.5 SQMM RING TYPE - COPPER
2.85 | Endterminations | Nos. |  |  |  |  | 0 | 0 | 0 | DB To Panel Cabling - LT Cables | 1 - 19MM PG Gland
[7 empty] | 0 | 0 | 0
2.86 | 3 Core x 1.5 Sq. mm | Mts |  |  |  |  | 0 | 0 | 0 | DB To Panel Cabling - LT Cables | 1 - 3CX1.5 SQMM FRLS COPPER FLEXIBLE CABLE, 1 - LUGS / THIMBLE 2.5 SQMM RING TYPE - COPPER
2.87 | Endterminations | Nos. |  |  |  |  | 0 | 0 | 0 | DB To Panel Cabling - LT Cables | 1 - 19MM PG Gland
[7 empty] | 0 | 0 | 0
2.88 | 4 Core x 16 Sq. mm | Mts |  |  |  |  | 0 | 0 | 0 | DB To Panel Cabling - LT Cables | 1 - 4CX16 SQMM COPPER FLEXIBLE CABLE, 1 - LUGS / THIMBLE 25 SQMM PIN TYPE - COPPER
2.89 | Endterminations | Nos. |  |  |  |  | 0 | 0 | 0 | DB To Panel Cabling - LT Cables | 1 - 25MM PG Gland
[7 empty] | 0 | 0 | 0
2.9 | 4 Core x 6 Sq. mm | Mts |  |  |  |  | 0 | 0 | 0 | DB To Panel Cabling - LT Cables | 1 - 4CX6 SQMM COPPER FLEXIBLE CABLE, 1 - LUGS / THIMBLE 4 SQMM RING TYPE - COPPER
2.91 | Endterminations | Nos. |  |  |  |  | 0 | 0 | 0 | DB To Panel Cabling - LT Cables | 1 - 21MM PG Gland
[7 empty] | 0 | 0 | 0
2.92 | 4 Core x 4 Sq. mm | Mts |  |  |  |  | 0 | 0 | 0 | DB To Panel Cabling - LT Cables | 1 - 4CX4 SQMM FRLS COPPER FLEXIBLE CABLE, 1 - LUGS / THIMBLE 4 SQMM RING TYPE - COPPER
2.93 | Endterminations | Nos. |  |  |  |  | 0 | 0 | 0 | DB To Panel Cabling - LT Cables | 1 - 19MM PG Gland
[7 empty] | 0 | 0 | 0
2.94 | 4 Core x 10 Sq. mm | Mts |  |  |  |  | 0 | 0 | 0 | DB To Panel Cabling - LT Cables | 1 - 4CX10 SQMM COPPER FLEXIBLE CABLE, 1 - LUGS / THIMBLE 25 SQMM PIN TYPE - COPPER
2.95 | Endterminations | Nos. |  |  |  |  | 0 | 0 | 0 | DB To Panel Cabling - LT Cables | 1 - 25MM PG Gland
[7 empty] | 0 | 0 | 0
2.96 | 5 Core x 25 Sq. mm | Mts |  |  |  |  | 0 | 0 | 0 | DB To Panel Cabling - LT Cables | 1 - LUGS / THIMBLE 25 SQMM PIN TYPE - COPPER
2.97 | Endterminations | Nos. |  |  |  |  | 0 | 0 | 0 | DB To Panel Cabling - LT Cables | 1 - 25MM PG Gland
[7 empty] | 0 | 0 | 0
2.98 | 4 Core x 16 Sq. mm | Mts |  |  |  |  | 0 | 0 | 0 | DB To Panel Cabling - LT Cables | 1 - 4CX16 SQMM COPPER FLEXIBLE CABLE, 1 - LUGS / THIMBLE 25 SQMM PIN TYPE - COPPER
2.1 | Endterminations | Nos. |  |  |  |  | 0 | 0 | 0 | DB To Panel Cabling - LT Cables | 1 - 25MM PG Gland
[7 empty] | 0 | 0 | 0
C | FRLS PVC Insulated & Steel Armoured Copper Conductor cables (YFY Type) | [5 empty] | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
2.101 | 3 Core x 10 Sq. mm | Mts | 40 | 40 | 640 | 40 | 25600 | 1600 | 27200 | DB To Panel Cabling - LT Cables | 40 - 3CX10 SQMM COPPER ARMOURED CABLE, 40 - LUGS / THIMBLE 25 SQMM PIN TYPE - COPPER
2.102 | Endterminations | Nos. | 4 | 4 | 80 | 20 | 320 | 80 | 400 | DB To Panel Cabling - LT Cables | 4 - 25MM Double Compression Gland
[7 empty] | 0 | 0 | 0
2.103 | 3 Core x 6 Sq. mm | Mts |  |  |  |  | 0 | 0 | 0 | DB To Panel Cabling - LT Cables | 1 - 3CX6 SQMM FRLS COPPER ARMOURED CABLE, 1 - LUGS / THIMBLE 4 SQMM RING TYPE - COPPER
2.104 | Endterminations | Nos. |  |  |  |  | 0 | 0 | 0 | DB To Panel Cabling - LT Cables | 1 - 19MM Double Compression Gland
[7 empty] | 0 | 0 | 0
2.105 | 3 Core x 4 Sq. mm | Mts | 20 | 20 | 275 | 30 | 5500 | 600 | 6100 | DB To Panel Cabling - LT Cables | 20 - 3CX4 SQMM FRLS COPPER ARMOURED CABLE, 20 - LUGS / THIMBLE 4 SQMM RING TYPE - COPPER
2.106 | Endterminations | Nos. | 2 | 2 | 70 | 20 | 140 | 40 | 180 | DB To Panel Cabling - LT Cables | 2 - 19MM Double Compression Gland
[7 empty] | 0 | 0 | 0
2.107 | 3 Core x 2.5 Sq. mm | Mts |  |  |  |  | 0 | 0 | 0 | DB To Panel Cabling - LT Cables | 1 - LUGS / THIMBLE 2.5 SQMM RING TYPE - COPPER
2.108 | Endterminations | Nos. |  |  |  |  | 0 | 0 | 0 | DB To Panel Cabling - LT Cables | 1 - 19MM Double Compression Gland
[7 empty] | 0 | 0 | 0
2.109 | 3 Core x 1.5 Sq. mm | Mts |  |  |  |  | 0 | 0 | 0 | DB To Panel Cabling - LT Cables | 1 - LUGS / THIMBLE 2.5 SQMM RING TYPE - COPPER
2.11 | Endterminations | Nos. |  |  |  |  | 0 | 0 | 0 | DB To Panel Cabling - LT Cables | 1 - 19MM Double Compression Gland
[7 empty] | 0 | 0 | 0
2.111 | 4 Core x 25 Sq. mm | Mts | 25 | 25 | 1955 | 60 | 48875 | 1500 | 50375 | DB To Panel Cabling - LT Cables | 25 - 4CX25 SQMM COPPER ARMOURED CABLE, 25 - LUGS / THIMBLE 25 SQMM PIN TYPE - COPPER
2.112 | Endterminations | Nos. | 4 | 4 | 190 | 50 | 760 | 200 | 960 | DB To Panel Cabling - LT Cables | 4 - 28MM Double Compression Gland
[7 empty] | 0 | 0 | 0
2.113 | 4 Core x 16 Sq. mm | Mts |  |  |  |  | 0 | 0 | 0 | DB To Panel Cabling - LT Cables | 1 - 4CX16 SQMM COPPER ARMOURED CABLE, 1 - LUGS / THIMBLE 25 SQMM PIN TYPE - COPPER
2.114 | Endterminations | Nos. |  |  |  |  | 0 | 0 | 0 | DB To Panel Cabling - LT Cables | 1 - 25MM Double Compression Gland
[7 empty] | 0 | 0 | 0
2.115 | 4 Core x 10 Sq. mm | Mts |  |  |  |  | 0 | 0 | 0 | DB To Panel Cabling - LT Cables | 1 - 4CX10 SQMM COPPER ARMOURED CABLE, 1 - LUGS / THIMBLE 25 SQMM PIN TYPE - COPPER
2.116 | Endterminations | Nos. |  |  |  |  | 0 | 0 | 0 | DB To Panel Cabling - LT Cables | 1 - 25MM Double Compression Gland
[7 empty] | 0 | 0 | 0
2.117 | 4 Core x 6 Sq. mm | Mts | 100 | 100 | 515 | 30 | 51500 | 3000 | 54500 | DB To Panel Cabling - LT Cables | 100 - 4CX6 SQMM COPPER ARMOURED CABLE, 100 - LUGS / THIMBLE 4 SQMM RING TYPE - COPPER
2.118 | Endterminations | Nos. | 20 | 20 | 100 | 30 | 2000 | 600 | 2600 | DB To Panel Cabling - LT Cables | 20 - 19MM Double Compression Gland
[7 empty] | 0 | 0 | 0
2.119 | 4 Core x 4 Sq. mm | Mts |  |  |  |  | 0 | 0 | 0 | DB To Panel Cabling - LT Cables | 1 - LUGS / THIMBLE 4 SQMM RING TYPE - COPPER
2.12 | Endterminations | Nos. |  |  |  |  | 0 | 0 | 0 | DB To Panel Cabling - LT Cables | 1 - 19MM Double Compression Gland
[7 empty] | 0 | 0 | 0
2.121 | 4 Core x 2.5 Sq. mm | Mts |  |  |  |  | 0 | 0 | 0 | DB To Panel Cabling - LT Cables | 1 - 4CX2.5 SQMM COPPER ARMOURED CABLE, 1 - LUGS / THIMBLE 2.5 SQMM RING TYPE - COPPER
2.122 | Endterminations | Nos. |  |  |  |  | 0 | 0 | 0 | DB To Panel Cabling - LT Cables | 1 - 19MM Double Compression Gland
[7 empty] | 0 | 0 | 0
| TOTAL FOR LT CABLES & ENDTERMINATIONS | [5 empty] | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
III | MCB DISTRIBUTION BOARDS (DB) | [5 empty] | 0 | 0 | 0
| Supply, Installation, Testing and Commissioning of MCB Distribution board as per approved installation drawings. | [5 empty] | 0 | 0 | 0
| Wall mounted MCB DBs with MS wire way box on top / bottom & on sides. MCBs shall be rated for 10kA with current limiting feature. Dummy ways to be covered with blank plates. All out going ways shall be labeled & laminated. | [5 empty] | 0 | 0 | 0
| Enclosure:1.2mm CRCA Sheet Steel, Powder Coated | [5 empty] | 0 | 0 | 0
| Door : Double Door | [5 empty] | 0 | 0 | 0
| Protection : IP 43 | [5 empty] | 0 | 0 | 0
| Cable Entry : Top & Bottom | [5 empty] | 0 | 0 | 0
| For UPS distribution RCCB's shall be harmonic resistant (HI/SI Series) | [5 empty] | 0 | 0 | 0
| Bus bar : Shall be tinned Copper and 200% rating for UPS DB Neutral Link | [5 empty] | 0 | 0 | 0
| MCB's : C Curve for Lighting & Raw power, 'D' Curve for UPS Distribution | [5 empty] | 0 | 0 | 0
| Note: | [5 empty] | 0 | 0 | 0
| 1) Separate Earth bus/Neutral bus for each phase | [5 empty] | 0 | 0 | 0
| 2) Each Circuit shall have yellow ferrules with circuit number on both sides | [5 empty] | 0 | 0 | 0
| 3) Accessories required for installation of DB's on Wall/Column/Gyp Board shall be considered | [5 empty] | 0 | 0 | 0
| 4) DB's shall be covered with powder coated (paint should match with DB Color) wire ways all around and up to ceiling to receive incoming circuits. Refer DB frame details. | [5 empty] | 0 | 0 | 0
| 5) Laminated A3 OR A4 size SLD shall be pasted inside DB door | [5 empty] | 0 | 0 | 0
| 6) Safe shroud for Neutral link shall be provided | [5 empty] | 0 | 0 | 0
| 7. All DBs shall be of 7 segment type ( Single Phase DB discription to be added seperately ) & Consider flexitier DB wherever 7 segment type is not matching | [5 empty] | 0 | 0 | 0
| 8) In All DBs Incomer TVSS /Surge protection of 2.5Kv to be Provided | [5 empty] | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
A | HUB Room UDB's : | [5 empty] | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
3.1 | 12 Way SPN MCB DB | [5 empty] | 0 | 0 | 0 | DB Box Installation | 1 - SPN DB 12 WAY, 1 - 63A DP RCCB 100mA
| 'Incomer : 1No. 63A 2P, RCBO | [5 empty] | 0 | 0 | 0
| Outgoing : 12 Nos. 32A SP MCB of 'D' curve | No. | 2 | 2 | 8790 | 750 | 17580 | 1500 | 19080 | DB - MCB Installation and Dressing | 12 - 32A SP MCB D CURVE
[7 empty] | 0 | 0 | 0
3.2 | 6 Way TPN MCB DB | [5 empty] | 0 | 0 | 0
| 'Incomer : 1No. 63A 4P, MCB | [5 empty] | 0 | 0 | 0
| Subincomer : 3Nos 63 A DP RCCB with 100mA | [5 empty] | 0 | 0 | 0
| Outgoing : 18 Nos. 32A SP MCB of 'D' curve | No. |  |  |  |  | 0 | 0 | 0 | DB - MCB Installation and Dressing | 18 - 32A SP MCB D CURVE
[7 empty] | 0 | 0 | 0
3.3 | 8 Way TPN MCB DB | [5 empty] | 0 | 0 | 0
| 'Incomer : 1No. 63A 4P, MCB | [5 empty] | 0 | 0 | 0
| Subincomer : 3Nos 63 A DP RCCB with 100mA | [5 empty] | 0 | 0 | 0
| Outgoing : 24 Nos. 32A SP MCB of 'D' curve | No. |  |  |  |  | 0 | 0 | 0 | DB - MCB Installation and Dressing | 24 - 32A SP MCB D CURVE
[7 empty] | 0 | 0 | 0
3.4 | 12 Way TPN MCB DB | [5 empty] | 0 | 0 | 0
| 'Incomer : 1No. 63A 4P, MCB | [5 empty] | 0 | 0 | 0
| Subincomer : 3Nos 63 A DP RCCB with 100mA | [5 empty] | 0 | 0 | 0
| Outgoing : 36 Nos. 32A SP MCB of 'D' curve | No. |  |  |  |  | 0 | 0 | 0 | DB - MCB Installation and Dressing | 36 - 32A SP MCB D CURVE
[7 empty] | 0 | 0 | 0
3.5 | 4 TIER 36 MODULE | [5 empty] | 0 | 0 | 0
| Incomer : 1No. 63A, 4P, MCB | [5 empty] | 0 | 0 | 0
| Sub incomer :3Nos 40A DP 300mA RCCB | [5 empty] | 0 | 0 | 0
| Outgoing : 12 Nos. 32A DP MCB of 'D' curve | No. |  |  |  |  | 0 | 0 | 0 | DB - MCB Installation and Dressing | 12 - 32A DP MCB D CURVE
[7 empty] | 0 | 0 | 0
B | LDB | [5 empty] | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
3.5 | 4 Way TPN MCB DB | [5 empty] | 0 | 0 | 0
| Incomer : 1No. 63A, 4P, MCB | [5 empty] | 0 | 0 | 0
| Subincomer :3Nos 40A DP 30mA RCCB | [5 empty] | 0 | 0 | 0
| Outgoing : 12 Nos. 10A SP MCB of 'C' curve | No. |  |  |  |  | 0 | 0 | 0 | DB - MCB Installation and Dressing | 12 - 10A SP MCB C CURVE
[7 empty] | 0 | 0 | 0
3.6 | 6 Way TPN MCB DB | [5 empty] | 0 | 0 | 0
| Incomer : 1No. 63A, 4P, MCB | [5 empty] | 0 | 0 | 0
| Subincomer :3Nos 40A DP 30mA RCCB | [5 empty] | 0 | 0 | 0
| Outgoing : 18 Nos. 10A SP MCB of 'C' curve | No. |  |  |  |  | 0 | 0 | 0 | DB - MCB Installation and Dressing | 18 - 10A SP MCB C CURVE
[7 empty] | 0 | 0 | 0
3.7 | 8 Way TPN MCB DB | [5 empty] | 0 | 0 | 0
| Incomer : 1No. 63A, 4P, MCB | [5 empty] | 0 | 0 | 0
| Sub incomer :3Nos 40A DP 30mA RCCB | [5 empty] | 0 | 0 | 0
| Outgoing : 24 Nos. 10A SP MCB of 'C' curve | No. |  |  |  |  | 0 | 0 | 0 | DB - MCB Installation and Dressing | 24 - 10A SP MCB C CURVE
[7 empty] | 0 | 0 | 0
3.8 | 12 Way TPN MCB DB | [5 empty] | 0 | 0 | 0
| Incomer : 1No. 63A, 4P, MCB | [5 empty] | 0 | 0 | 0
| Sub incomer :3Nos 40A DP 30mA RCCB | [5 empty] | 0 | 0 | 0
| Outgoing : 36 Nos. 10A SP MCB of 'C' curve | No. | 1 | 1 | 22100 | 1500 | 22100 | 1500 | 23600 | DB - MCB Installation and Dressing | 36 - 10A SP MCB C CURVE
[7 empty] | 0 | 0 | 0
3.9 | 4 TIER 36 MODULE | [5 empty] | 0 | 0 | 0 | DB Box Installation | 1 - TPN FLEXI DB 12X3, 1 - 40A FP MCB C CURVE, 3 - 40A DP RCCB 30mA
| Incomer : 1No. 40A, 4P, MCB | [5 empty] | 0 | 0 | 0
| Sub incomer :3Nos 40A DP 30mA RCCB | [5 empty] | 0 | 0 | 0
| Outgoing : 36 Nos. 10A SP MCB of 'C' curve | No. |  |  |  |  | 0 | 0 | 0 | DB - MCB Installation and Dressing | 36 - 10A SP MCB C CURVE
[7 empty] | 0 | 0 | 0
C | ELDB's & VAV DB's: | [5 empty] | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
3.9 | 12 Way SPN MCB DB | [5 empty] | 0 | 0 | 0
| Incomer : 1No. 63A DP 30mA RCCB | [5 empty] | 0 | 0 | 0
| Outgoing : 8 Nos. 32/40A SP MCB of 'C' curve | No. | 1 | 1 | 8000 | 750 | 8000 | 750 | 8750 | DB - MCB Installation and Dressing | 8 - 40A DP MCB C CURVE
[7 empty] | 0 | 0 | 0
3.1 | 12 Way SPN MCB DB | [5 empty] | 0 | 0 | 0
| Sub Incomer : 1No. 32A DP 30mA RCCB | [5 empty] | 0 | 0 | 0
| Outgoing : 10 Nos. 10A SP MCB of 'C' curve | No. |  |  |  |  | 0 | 0 | 0 | DB - MCB Installation and Dressing | 10 - 10A SP MCB C CURVE
[7 empty] | 0 | 0 | 0
3.11 | 16 Way SPN MCB DB | [5 empty] | 0 | 0 | 0
| Sub Incomer : 1No. 32A DP 30mA RCCB | [5 empty] | 0 | 0 | 0
| Outgoing : 14 Nos. 10A DP MCB of 'C' curve | No. | 1 | 1 | 13150 | 750 | 13150 | 750 | 13900 | DB - MCB Installation and Dressing | 14 - 10A SP MCB C CURVE
[7 empty] | 0 | 0 | 0
3.12 | 4Way TPN MCB DB | [5 empty] | 0 | 0 | 0
| Incomer : 1No. 32A, 4P, MCB | [5 empty] | 0 | 0 | 0
| Sub Incomer : 1No. 25A DP 30mA RCCB | [5 empty] | 0 | 0 | 0
| Outgoing : 12 Nos. 10A SP MCB of 'D' curve | No. |  |  |  |  | 0 | 0 | 0 | DB - MCB Installation and Dressing | 12 - 10A SP MCB D CURVE
[7 empty] | 0 | 0 | 0
3.13 | 6Way TPN MCB DB | [5 empty] | 0 | 0 | 0
| Incomer : 1No. 40A, 4P, MCB | [5 empty] | 0 | 0 | 0
| Sub Incomer : 1No. 32A DP 30mA RCCB | [5 empty] | 0 | 0 | 0
| Outgoing : 18 Nos. 10A SP MCB of 'D' curve | No. |  |  |  |  | 0 | 0 | 0 | DB - MCB Installation and Dressing | 18 - 10A SP MCB D CURVE
[7 empty] | 0 | 0 | 0
3.14 | 8Way TPN MCB DB | [5 empty] | 0 | 0 | 0
| Incomer : 1No. 40A, 4P, MCB | [5 empty] | 0 | 0 | 0
| Sub Incomer : 1No. 32A DP 30mA RCCB | [5 empty] | 0 | 0 | 0
| Outgoing : 24 Nos. 10A SP MCB of 'D' curve | No. |  |  |  |  | 0 | 0 | 0 | DB - MCB Installation and Dressing | 24 - 10A SP MCB D CURVE
[7 empty] | 0 | 0 | 0
3.15 | 12Way TPN MCB DB | [5 empty] | 0 | 0 | 0
| Incomer : 1No. 40A, 4P, MCB | [5 empty] | 0 | 0 | 0
| Sub incomer : 3Nos 32A DP 30mA RCCB | [5 empty] | 0 | 0 | 0
| Outgoing : 36 Nos. 10A SP MCB of 'D' curve | No. |  |  |  |  | 0 | 0 | 0 | DB - MCB Installation and Dressing | 36 - 10A SP MCB D CURVE
[7 empty] | 0 | 0 | 0
3.16 | 4 TIER 36 MODULE | [5 empty] | 0 | 0 | 0 | DB Box Installation | 1 - TPN FLEXI DB 12X3, 1 - 40A FP MCB C CURVE, 3 - 40A DP RCCB 30mA
| Incomer : 1No. 40A, 4P, MCB | [5 empty] | 0 | 0 | 0
| Sub incomer :3Nos 40A DP 30mA RCCB | [5 empty] | 0 | 0 | 0
| Outgoing : 36 Nos. 10A SP MCB of 'C' curve | No. |  |  |  |  | 0 | 0 | 0 | DB - MCB Installation and Dressing | 36 - 10A SP MCB C CURVE
[7 empty] | 0 | 0 | 0
D | UDB's : | [5 empty] | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
3.16 | 4Way TPN MCB DB | [5 empty] | 0 | 0 | 0
| Incomer : 1No. 63A 4P, MCB | [5 empty] | 0 | 0 | 0
| Sub incomer 3Nos 40 A DP RCCB with 100mA | [5 empty] | 0 | 0 | 0
| Outgoing :12. Nos. 16A SP MCB of 'D' curve | No. |  |  |  |  | 0 | 0 | 0 | DB - MCB Installation and Dressing | 12 - 16A SP MCB D CURVE
[7 empty] | 0 | 0 | 0
3.17 | 6 Way TPN MCB DB | [5 empty] | 0 | 0 | 0
| Incomer : 1No. 63A 4P, MCB | [5 empty] | 0 | 0 | 0
| Sub incomer 3Nos 40 A DP RCCB with 100mA | [5 empty] | 0 | 0 | 0
| Outgoing : 18. Nos. 16A SP MCB of 'D' curve | No. |  |  |  |  | 0 | 0 | 0 | DB - MCB Installation and Dressing | 18 - 16A SP MCB D CURVE
[7 empty] | 0 | 0 | 0
3.18 | 8 Way TPN MCB DB | [5 empty] | 0 | 0 | 0
| Incomer : 1No. 63A 4P, MCB | [5 empty] | 0 | 0 | 0
| Sub incomer 3Nos 40 A DP RCCB with 100mA | [5 empty] | 0 | 0 | 0
| Outgoing : 24. Nos. 16A SP MCB of 'D' curve | No. |  |  |  |  | 0 | 0 | 0 | DB - MCB Installation and Dressing | 24 - 16A SP MCB D CURVE
[7 empty] | 0 | 0 | 0
3.19 | 12 Way TPN MCB DB | [5 empty] | 0 | 0 | 0
| Incomer : 1No. 63A 4P, MCB | [5 empty] | 0 | 0 | 0
| Sub incomer 3Nos 63 A DP RCCB with 100mA | [5 empty] | 0 | 0 | 0
| Outgoing : 36 Nos. 16A SP MCB of 'D' curve | No. | 1 | 1 | 26640 | 1500 | 26640 | 1500 | 28140 | DB - MCB Installation and Dressing | 36 - 16A SP MCB D CURVE
[7 empty] | 0 | 0 | 0
3.2 | 4 TIER 36 MODULE | [5 empty] | 0 | 0 | 0 | DB Box Installation | 1 - TPN FLEXI DB 12X3, 1 - 63A FP MCB C CURVE, 3 - 40A DP RCCB 300mA
| Incomer : 1No. 63A, 4P, MCB | [5 empty] | 0 | 0 | 0
| Sub incomer :3Nos 40A DP 300mA RCCB | [5 empty] | 0 | 0 | 0
| Outgoing : 36 Nos. 16A SP MCB of 'D' curve | No. |  |  |  |  | 0 | 0 | 0 | DB - MCB Installation and Dressing | 36 - 16A SP MCB D CURVE
[7 empty] | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
E | RDB's : | [5 empty] | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
3.21 | 4Way TPN MCB DB | [5 empty] | 0 | 0 | 0
| Incomer : 1No. 63A 4P, MCB | [5 empty] | 0 | 0 | 0
| Sub incomer 3Nos 40 A DP RCCB with 100mA | [5 empty] | 0 | 0 | 0
| Outgoing : 12 Nos. 16A SP MCB of 'C' curve | No. |  |  |  |  | 0 | 0 | 0 | DB - MCB Installation and Dressing | 12 - 16A SP MCB C CURVE
[7 empty] | 0 | 0 | 0
3.22 | 6 Way TPN MCB DB | [5 empty] | 0 | 0 | 0
| Incomer : 1No. 63A 4P, MCB | [5 empty] | 0 | 0 | 0
| Sub incomer 3Nos 40 A DP RCCB with 100mA | [5 empty] | 0 | 0 | 0
| Outgoing : 18 Nos. 16A SP MCB of 'C' curve | No. |  |  |  |  | 0 | 0 | 0 | DB - MCB Installation and Dressing | 18 - 16A SP MCB C CURVE
[7 empty] | 0 | 0 | 0
3.23 | 8 Way TPN MCB DB | [5 empty] | 0 | 0 | 0
| Incomer : 1No. 63A 4P, MCB | [5 empty] | 0 | 0 | 0
| Sub incomer 3Nos 63 A DP RCCB with 100mA | [5 empty] | 0 | 0 | 0
| Outgoing : 24 Nos. 16A SP MCB of 'C' curve | No. |  |  |  |  | 0 | 0 | 0 | DB - MCB Installation and Dressing | 24 - 16A SP MCB C CURVE
[7 empty] | 0 | 0 | 0
3.24 | 12 Way TPN MCB DB | [5 empty] | 0 | 0 | 0
| Incomer : 1No. 63A 4P, MCB | [5 empty] | 0 | 0 | 0
| Sub incomer 3Nos 63 A DP RCCB with 100mA | [5 empty] | 0 | 0 | 0
| Outgoing : 36 Nos. 16A SP MCB of 'C' curve | No. | 1 | 1 | 24120 | 1500 | 24120 | 1500 | 25620 | DB - MCB Installation and Dressing | 36 - 16A SP MCB C CURVE
[7 empty] | 0 | 0 | 0
3.25 | 4 TIER 36 MODULE | [5 empty] | 0 | 0 | 0
| Incomer : 1No. 63A, 4P, MCB | [5 empty] | 0 | 0 | 0
| Sub incomer :3Nos 40A DP 100mA RCCB | [5 empty] | 0 | 0 | 0
| Outgoing : 36 Nos. 16A SP MCB of 'D' curve | No. |  |  |  |  | 0 | 0 | 0 | DB - MCB Installation and Dressing | 36 - 16A SP MCB D CURVE
[7 empty] | 0 | 0 | 0
F | VAV , FD & HVAC DB's : | [5 empty] | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
3.26 | 12 Way TPN MCB DB (VAV & FIRE DAMPER ) | [5 empty] | 0 | 0 | 0
| Incomer : 1No. 40A 4P, MCB | [5 empty] | 0 | 0 | 0
| Sub incomer 3Nos32 A DP RCCB with 100mA | [5 empty] | 0 | 0 | 0
| Outgoing : 30 Nos. 16A SP MCB of 'D' curve | No. | 1 | 1 | 23050 | 1500 | 23050 | 1500 | 24550 | DB - MCB Installation and Dressing | 30 - 16A SP MCB D CURVE
[7 empty] | 0 | 0 | 0
3.27 | 4 TIER 36 MODULE | [5 empty] | 0 | 0 | 0
| Incomer : 1No. 40A, 4P, MCB | [5 empty] | 0 | 0 | 0
| Sub incomer :3Nos 40A DP 100mA RCCB | [5 empty] | 0 | 0 | 0
| Outgoing : 36 Nos. 10A SP MCB of 'C' curve | No. |  |  |  |  | 0 | 0 | 0 | DB - MCB Installation and Dressing | 36 - 10A SP MCB C CURVE
[7 empty] | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
F1 | VTPN DBS | [5 empty] | 0 | 0 | 0
| 8 Way VTPN MCCB DB - 40kVA UPS | No. |  |  |  |  | 0 | 0 | 0 | DB - MCB Installation and Dressing
| Incomer : 1No. 100A 4P, MCCB , TMD, 16kA | [5 empty] | 0 | 0 | 0
| Outgoing : 6 Nos. 40A 3P 'D' CURVE MCB | [5 empty] | 0 | 0 | 0
| Outgoing : 6 Nos. 32A SP 'D' CURVE MCB | [5 empty] | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
| 8 Way VTPN MCCB UPS-SMDB | No. |  |  |  |  | 0 | 0 | 0 | DB - MCB Installation and Dressing
| Incomer : 1No. 250A 4P, MCCB , TMD, 16kA | [5 empty] | 0 | 0 | 0
| Outgoing : 8 Nos. 63A 3P 'D' CURVE MCB | [5 empty] | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
| 6 Way VTPN MCB DB (For Emeg) -10kVA UPS | No. |  |  |  |  | 0 | 0 | 0 | DB - MCB Installation and Dressing
| Incomer : 1No. 63A 4P, MCB | [5 empty] | 0 | 0 | 0
| Outgoing : 2 Nos. 32A TP 'C' CURVE MCB | [5 empty] | 0 | 0 | 0
| Outgoing : 8 Nos. 32A TP 'C' CURVE MCB | [5 empty] | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
| 8 Way VTPN MCB DB (For Cafeteria) | No. |  |  |  |  | 0 | 0 | 0 | DB - MCB Installation and Dressing
| Incomer : 1No. 100A 4P, MCCB , TMD, 16kA | [5 empty] | 0 | 0 | 0
| Outgoing : 4 Nos. 40/32A 3P 'C' CURVE MCB | [5 empty] | 0 | 0 | 0
| Outgoing : 12 Nos. 16/20/25A SP 'C' CURVE MCB | [5 empty] | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
G | 4P MCB BOX with Polycarbonate enclosures (Indoor - IP 52) | [5 empty] | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
3.28 | 6A to 32A | No. | 4 | 4 | 1800 | 270 | 7200 | 1080 | 8280 | DB Box Installation
[7 empty] | 0 | 0 | 0
3.29 | 40A to 63A | No. | 2 | 2 | 2370 | 360 | 4740 | 720 | 5460 | DB Box Installation
[7 empty] | 0 | 0 | 0
3.3 | 250A, TMD MCCB, 25kA | No. | 1 | 1 | 18200 | 2730 | 18200 | 2730 | 20930 | DB - MCB Installation and Dressing | 1 - Adaptor Box With 250A MCCB & AL Busbar
3.31 | 1000A, TMD MCCB, 36kA | No. |  |  |  |  | 0 | 0 | 0 | DB - MCB Installation and Dressing | 1 - 125A FP MCCB
| 4P MCB BOX with Polycarbonate enclosures (Outdoor - IP 55) | [5 empty] | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
3.3 | 6A to 32A | No. |  |  |  |  | 0 | 0 | 0 | DB Box Installation
[7 empty] | 0 | 0 | 0
3.31 | 40A to 63A | No. |  |  |  |  | 0 | 0 | 0 | DB Box Installation
[7 empty] | 0 | 0 | 0
| 4P RCBO - AC Series 100ma - with Polycarbonate enclosures (Indoor - IP 52) | [5 empty] | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
3.32 | 6A to 32A | No. |  |  |  |  | 0 | 0 | 0 | DB Box Installation
[7 empty] | 0 | 0 | 0
3.33 | 20A to 16A | No. |  |  |  |  | 0 | 0 | 0 | DB Box Installation
[7 empty] | 0 | 0 | 0
| 4P RCBO - AC Series 100ma - with Polycarbonate enclosures (Outdoor - IP 65) | [5 empty] | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
3.34 | 6A to 32A | No. | 4 | 4 | 5640 | 850 | 22560 | 3400 | 25960 | DB Box Installation
[7 empty] | 0 | 0 | 0
3.35 | 40A to 63A | No. | 4 | 4 | 6140 | 930 | 24560 | 3720 | 28280 | DB Box Installation
[7 empty] | 0 | 0 | 0
3.36 | Providing 2 MODULE Metal back box for Data socket outlets in the WALL/floor. | Nos. | 10 | 10 | 50 | 10 | 500 | 100 | 600 | Wall Switch Socket Installation | 10 - GI BOX - 2 Module, 10 - GI BOX - 3 Module, 10 - GI BOX - 4 Module, 10 - GI BOX - 6 Module, 10 - GI BOX - 8 Module, 10 - GI BOX - 9 Module, 10 - PVC BOX - 2 Module, 10 - PVC BOX - 3 Module, 10 - PVC BOX - 6 Module, 10 - PVC BOX - 8 Module
[7 empty] | 0 | 0 | 0
3.37 | Providing 3 MODULE Metal back box for Data socket outlets in the WALL/floor. | Nos. | 15 | 15 | 60 | 20 | 900 | 300 | 1200 | Wall Switch Socket Installation | 15 - GI BOX - 2 Module, 15 - GI BOX - 3 Module, 15 - GI BOX - 4 Module, 15 - GI BOX - 6 Module, 15 - GI BOX - 8 Module, 15 - GI BOX - 9 Module, 15 - PVC BOX - 2 Module, 15 - PVC BOX - 3 Module, 15 - PVC BOX - 6 Module, 15 - PVC BOX - 8 Module
[7 empty] | 0 | 0 | 0
3.38 | Providing 6 MODULE PVC back box for Data socket outlets in the WALL/floor. | Nos. | 10 | 10 | 90 | 20 | 900 | 200 | 1100 | Wall Switch Socket Installation | 10 - GI BOX - 2 Module, 10 - GI BOX - 3 Module, 10 - GI BOX - 4 Module, 10 - GI BOX - 6 Module, 10 - GI BOX - 8 Module, 10 - GI BOX - 9 Module, 10 - PVC BOX - 2 Module, 10 - PVC BOX - 3 Module, 10 - PVC BOX - 6 Module, 10 - PVC BOX - 8 Module
[7 empty] | 0 | 0 | 0
3.39 | Providing 8 MODULE PVC back box for Data socket outlets in the WALL/floor. | Nos. |  |  |  |  | 0 | 0 | 0 | Wall Switch Socket Installation | 1 - GI BOX - 2 Module, 1 - GI BOX - 3 Module, 1 - GI BOX - 4 Module, 1 - GI BOX - 6 Module, 1 - GI BOX - 8 Module, 1 - GI BOX - 9 Module, 1 - PVC BOX - 2 Module, 1 - PVC BOX - 3 Module, 1 - PVC BOX - 6 Module, 1 - PVC BOX - 8 Module
[7 empty] | 0 | 0 | 0
3.4 | Isolator | Nos. |  |  |  |  | 0 | 0 | 0 | DB - MCB Installation and Dressing
[7 empty] | 0 | 0 | 0
a | 20A 4P Isolator | Nos. |  |  |  |  | 0 | 0 | 0 | DB - MCB Installation and Dressing
[7 empty] | 0 | 0 | 0
b | 40A 4P Isolator | Nos. |  |  |  |  | 0 | 0 | 0 | DB - MCB Installation and Dressing
[7 empty] | 0 | 0 | 0
c | 63A 4P Isolator | Nos. |  |  |  |  | 0 | 0 | 0 | DB - MCB Installation and Dressing
[7 empty] | 0 | 0 | 0
d | 160A 4P Isolator | Nos. |  |  |  |  | 0 | 0 | 0 | DB - MCB Installation and Dressing
[7 empty] | 0 | 0 | 0
e | 200A 4P Isolator | Nos. |  |  |  |  | 0 | 0 | 0 | DB - MCB Installation and Dressing
[7 empty] | 0 | 0 | 0
IV | CIRCUIT MAINS FOR POWER CIRCUITS | [5 empty] | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
| Supply, Installation, Testing and Commissioning of Circuit mains using 1.1kV grade FRLS PVC insulated PVC round sheathed single/multicore core flexible cables drawn in existing conduit or raceway. Circuit mains shall be measured from respective DB to the nearest socket board & looping circuit also be measured in running Mtr. All circuit terminations shall be provided with solder less crimping type copper sockets / lugs, ferrules indicating source code on load side & load code on source side. There shall not be any joints in the circuits, only looping is allowed in terminal blocks/connectors costing shall include terminal blocks/connectors if any & in switches / Sensors/ socket outlets. Kindly refer IS 694:1990. | [5 empty] | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
| Colour codes to be followed as below | [5 empty] | 0 | 0 | 0
| Raw power Circuits - BLACK | [5 empty] | 0 | 0 | 0
| UPS power circuits - WHITE | [5 empty] | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
4.1 | UPS / RP/AV Circuit wiring : | [5 empty] | 0 | 0 | 0 | Power Circuit Wiring - Cu Flexible Cables | 1 - 3CX2.5 SQMM FRLS COPPER FLEXIBLE CABLE, 1 - 4CX2.5 SQMM FRLS COPPER FLEXIBLE CABLE, 1 - 3CX6 SQMM FRLS COPPER FLEXIBLE CABLE, 1 - 4CX6 SQMM COPPER FLEXIBLE CABLE
| Supply, Installation, Testing and Commissioning of 3 C x 2.5 Sqmm FRLS 1100V PVC double insulated flexible multicore cable in existing conduits/raceways. | Mts. | 1500 | 1500 | 160 | 30 | 240000 | 45000 | 285000 | Power Circuit Wiring - Cu Flexible Cables | 1500 - 3CX2.5 SQMM FRLS COPPER FLEXIBLE CABLE
[7 empty] | 0 | 0 | 0
4.2 | UPS / RP/AV looping: | [5 empty] | 0 | 0 | 0
| Supply, Installation, Testing and Commissioning of 3 C x 2.5 Sqmm FRLS 1100V PVC double insulated flexible multicore cable in existing conduits/raceways. | Mts. | 1200 | 1200 | 160 | 30 | 192000 | 36000 | 228000 | Power Circuit Wiring - Cu Flexible Cables | 1200 - 3CX2.5 SQMM FRLS COPPER FLEXIBLE CABLE
[7 empty] | 0 | 0 | 0
4.3 | SERVER POWER CIRCUIT | [5 empty] | 0 | 0 | 0
| Supply, Installation, Testing and Commissioning of 3 C x 6 Sqmm FRLS 1100V PVC double insulated flexible multicore cable in existing conduits/raceways. | Mts. | 50 | 50 | 360 | 30 | 18000 | 1500 | 19500 | Power Circuit Wiring - Cu Flexible Cables | 50 - 3CX6 SQMM FRLS COPPER FLEXIBLE CABLE, 50 - 3CX6 SQMM FRLS COPPER ARMOURED CABLE
[7 empty] | 0 | 0 | 0
4.4 | VAV & FIRE EXIT SINAGES Circuit & looping: | [5 empty] | 0 | 0 | 0
| Supply, Installation, Testing and Commissioning of 3Cx1.5sqmm FRLS 1100V PVC double insulated flexible multicore cable in in existing conduits/raceways. | Mts. | 200 | 200 | 100 | 20 | 20000 | 4000 | 24000 | Power Circuit Wiring - Cu Flexible Cables | 200 - 3CX1.5 SQMM FRLS COPPER FLEXIBLE CABLE
[7 empty] | 0 | 0 | 0
4.5 | Supply & Installation , Testing and Commissioning of male connector of weiland make or equivalent make | Nos. |  |  |  |  | 0 | 0 | 0 | Power Circuit Wiring - Cu Flexible Cables
[7 empty] | 0 | 0 | 0
4.6 | Supply & Installation , Testing and Commissioning of female connector of weiland make or equivalent make | Nos. |  |  |  |  | 0 | 0 | 0 | Power Circuit Wiring - Cu Flexible Cables
[7 empty] | 0 | 0 | 0
4.7 | Supply & Installation , Testing and Commissioning of 1 in 2 out connector of weiland make or equivalent make | Nos. |  |  |  |  | 0 | 0 | 0 | Power Circuit Wiring - Cu Flexible Cables
[7 empty] | 0 | 0 | 0
4.8 | Supply & Installation , Testing and Commissioning of 1 in 3 out connector of weiland make or equivalent make | Nos. |  |  |  |  | 0 | 0 | 0 | Power Circuit Wiring - Cu Flexible Cables
[7 empty] | 0 | 0 | 0
4 | Supply & Installation , Testing and Commissioning of 1 in 5 out connector of weiland make or equivalent make | Nos. |  |  |  |  | 0 | 0 | 0 | Power Circuit Wiring - Cu Flexible Cables
[7 empty] | 0 | 0 | 0
V | CIRCUIT MAINS & POINT WIRING FOR LIGHT FIXTURES | [5 empty] | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
A | POINT WIRING - Switch controls | [5 empty] | 0 | 0 | 0
| Supply, Installation, Testing and Commissioning of 3 C x 1.5 Sqmm FRLS 1100V PVC double insulated flexible multicore cable in multicore cable PVC conduits. The wiring shall be complete with ceiling roses, switches ,Modular Boxes and all consumables.All circuit terminations shall be provided with solder less crimping type copper sockets / lugs, ferrules indicating source code on load side & load code on source side. There shall not be any joints in the circuits, only looping is allowed in terminal blocks & in switches / Sensors/ socket outlets. Kindly refer IS 694:1990. | [5 empty] | 0 | 0 | 0
| Colour codes to be followed as below | [5 empty] | 0 | 0 | 0
| Lighting Circuits - Grey | [5 empty] | 0 | 0 | 0
| Emergency Lighting Circuits - Black | [5 empty] | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
5.1 | PRIMARY LIGHT POINT- Vendor to calculate the length based on the lighting layout & quote accordingly | [5 empty] | 0 | 0 | 0 | Point Wiring for Lights - Cu Flexible Wires | 1 - 3CX1.5 SQMM FRLS COPPER FLEXIBLE CABLE, 1 - 2CX1.5 SQMM FRLS COPPER FLEXIBLE CABLE TRANSPARENT, 1 - 1.5 SQMM FRLS COPPER WIRE RED, 1 - 1.5 SQMM FRLS COPPER WIRE BLACK, 1 - 1.5 SQMM FRLS COPPER WIRE BLUE, 1 - 1.5 SQMM FRLS COPPER WIRE GREEN, 1 - PVC CONDUIT - 19 MM, 1 - PVC BOX - 2 Module, 1 - PVC BOX - 3 Module, 1 - GI BOX - 2 Module, 1 - GI BOX - 3 Module, 1 - GI BOX - 4 Module
| Primary light point means wiring from DB to first switch Point/Sensors & first switch point/Sensors to the first light fixture . The switch and all necessary accessories would be part of primary point & The cost shall also include sub-circuit wiring & accessories. if it is drawn from adjacent switch box/sensors | Nos. | 25 | 25 | 3970 | 800 | 99250 | 20000 | 119250 | Point Wiring for Lights - Cu Flexible Wires | 25 - 3CX1.5 SQMM FRLS COPPER FLEXIBLE CABLE, 25 - 2CX1.5 SQMM FRLS COPPER FLEXIBLE CABLE TRANSPARENT, 25 - 1.5 SQMM FRLS COPPER WIRE RED, 25 - 1.5 SQMM FRLS COPPER WIRE BLACK, 25 - 1.5 SQMM FRLS COPPER WIRE BLUE, 25 - 1.5 SQMM FRLS COPPER WIRE GREEN, 25 - PVC CONDUIT - 19 MM, 25 - PVC BOX - 2 Module, 25 - PVC BOX - 3 Module, 25 - GI BOX - 2 Module, 25 - GI BOX - 3 Module, 25 - GI BOX - 4 Module
[7 empty] | 0 | 0 | 0
5.2 | SECONDARY LIGHT POINT - Vendor to calculate the length based on the lighting layout & quote accordingly | [5 empty] | 0 | 0 | 0
| Secondary light point means extention of light outlet wiring & Accessories from existing primary point. Same to be controlled by the existing switch/Sensors of primary point & the cost shall include Ceiling flexible conduit shall be included at the drop of light fixture. | Nos. | 139 | 139 | 640 | 130 | 88960 | 18070 | 107030 | Point Wiring for Lights - Cu Flexible Wires | 1 - 3CX1.5 SQMM FRLS COPPER FLEXIBLE CABLE, 1 - 2CX1.5 SQMM FRLS COPPER FLEXIBLE CABLE TRANSPARENT, 1 - 1.5 SQMM FRLS COPPER WIRE RED, 1 - 1.5 SQMM FRLS COPPER WIRE BLACK, 1 - 1.5 SQMM FRLS COPPER WIRE BLUE, 1 - 1.5 SQMM FRLS COPPER WIRE GREEN, 1 - PVC CONDUIT - 19 MM, 1 - PVC BOX - 2 Module, 1 - PVC BOX - 3 Module, 1 - GI BOX - 2 Module, 1 - GI BOX - 3 Module, 1 - GI BOX - 4 Module
[7 empty] | 0 | 0 | 0
B | POINT WIRING - MCB Control | [5 empty] | 0 | 0 | 0
| Supply, Installation, Testing and Commissioning of 3 C x 1.5 Sqmm FRLS 1100V PVC double insulated flexible multicore cable in PVC conduits.. The wiring shall be complete with ceiling roses, switches ,Modular Boxes and all consumables.All circuit terminations shall be provided with solder less crimping type copper sockets / lugs, ferrules indicating source code on load side & load code on source side. There shall not be any joints in the circuits, only looping is allowed in terminal blocks & in switches / Sensors/ socket outlets. Kindly refer IS 694:1990. | [5 empty] | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
5.3 | PRIMARY LIGHT POINT - Vendor to calculate the length based on the lighting layout & quote accordingly | [5 empty] | 0 | 0 | 0
| Primary light point means wiring from DB to first light point. The cost shall include Ceiling flexible conduit at the drop of light fixture. | Nos. | 15 | 15 | 2530 | 510 | 37950 | 7650 | 45600 | Point Wiring for Lights - Cu Flexible Wires | 15 - 3CX1.5 SQMM FRLS COPPER FLEXIBLE CABLE, 15 - 2CX1.5 SQMM FRLS COPPER FLEXIBLE CABLE TRANSPARENT, 15 - 1.5 SQMM FRLS COPPER WIRE RED, 15 - 1.5 SQMM FRLS COPPER WIRE BLACK, 15 - 1.5 SQMM FRLS COPPER WIRE BLUE, 15 - 1.5 SQMM FRLS COPPER WIRE GREEN, 15 - PVC CONDUIT - 19 MM, 15 - PVC BOX - 2 Module, 15 - PVC BOX - 3 Module, 15 - GI BOX - 2 Module, 15 - GI BOX - 3 Module, 15 - GI BOX - 4 Module
[7 empty] | 0 | 0 | 0
5.4 | SECONDARY LIGHT POINT - Vendor to calculate the length based on the lighting layout & quote accordingly | [5 empty] | 0 | 0 | 0
| Secondary light point means extention of light outlet from existing primary point. The cost shall include Ceiling flexible conduit at the drop of light fixture. | Nos. | 110 | 110 | 640 | 130 | 70400 | 14300 | 84700 | Point Wiring for Lights - Cu Flexible Wires | 1 - 3CX1.5 SQMM FRLS COPPER FLEXIBLE CABLE, 1 - 2CX1.5 SQMM FRLS COPPER FLEXIBLE CABLE TRANSPARENT, 1 - 1.5 SQMM FRLS COPPER WIRE RED, 1 - 1.5 SQMM FRLS COPPER WIRE BLACK, 1 - 1.5 SQMM FRLS COPPER WIRE BLUE, 1 - 1.5 SQMM FRLS COPPER WIRE GREEN, 1 - PVC CONDUIT - 19 MM, 1 - PVC BOX - 2 Module, 1 - PVC BOX - 3 Module, 1 - GI BOX - 2 Module, 1 - GI BOX - 3 Module, 1 - GI BOX - 4 Module
[7 empty] | 0 | 0 | 0
C | POINT WIRING - Sensor Control | [5 empty] | 0 | 0 | 0
| Supply, Installation, Testing and Commissioning of 3 C x 1.5 Sqmm FRLS 1100V PVC double insulated flexible multicore cable in multicore cable PVC conduits. The wiring shall be complete with ceiling roses, switches ,Modular Boxes and all consumables.All circuit terminations shall be provided with solder less crimping type copper sockets / lugs, ferrules indicating source code on load side & load code on source side. There shall not be any joints in the circuits, only looping is allowed in terminal blocks & in switches / Sensors/ socket outlets. Kindly refer IS 694:1990. | [5 empty] | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
5.5 | PRIMARY LIGHT POINT - Vendor to calculate the length based on the lighting layout & quote accordingly | [5 empty] | 0 | 0 | 0
| Primary light point means wiring from DB to first light point. The cost shall include Ceiling flexible conduit at the drop of light fixture. | Nos. | 5 | 5 | 3970 | 800 | 19850 | 4000 | 23850 | Point Wiring for Lights - Cu Flexible Wires | 5 - 3CX1.5 SQMM FRLS COPPER FLEXIBLE CABLE, 5 - 2CX1.5 SQMM FRLS COPPER FLEXIBLE CABLE TRANSPARENT, 5 - 1.5 SQMM FRLS COPPER WIRE RED, 5 - 1.5 SQMM FRLS COPPER WIRE BLACK, 5 - 1.5 SQMM FRLS COPPER WIRE BLUE, 5 - 1.5 SQMM FRLS COPPER WIRE GREEN, 5 - PVC CONDUIT - 19 MM, 5 - PVC BOX - 2 Module, 5 - PVC BOX - 3 Module, 5 - GI BOX - 2 Module, 5 - GI BOX - 3 Module, 5 - GI BOX - 4 Module
[7 empty] | 0 | 0 | 0
5.6 | SECONDARY LIGHT POINT- Vendor to calculate the length based on the lighting layout & quote accordingly | [5 empty] | 0 | 0 | 0
| Secondary light point means extention of light outlet from existing primary point. The cost shall include Ceiling flexible conduit at the drop of light fixture. | Nos. | 25 | 25 | 640 | 130 | 16000 | 3250 | 19250 | Point Wiring for Lights - Cu Flexible Wires | 25 - 3CX1.5 SQMM FRLS COPPER FLEXIBLE CABLE, 25 - 2CX1.5 SQMM FRLS COPPER FLEXIBLE CABLE TRANSPARENT, 25 - 1.5 SQMM FRLS COPPER WIRE RED, 25 - 1.5 SQMM FRLS COPPER WIRE BLACK, 25 - 1.5 SQMM FRLS COPPER WIRE BLUE, 25 - 1.5 SQMM FRLS COPPER WIRE GREEN, 25 - PVC CONDUIT - 19 MM, 25 - PVC BOX - 2 Module, 25 - PVC BOX - 3 Module, 25 - GI BOX - 2 Module, 25 - GI BOX - 3 Module, 25 - GI BOX - 4 Module
[7 empty] | 0 | 0 | 0
D | POINT WIRING - Sensor + Switch Control | [5 empty] | 0 | 0 | 0
| Supply, Installation, Testing and Commissioning of 3 C x 1.5 Sqmm FRLS 1100V PVC double insulated flexible multicore cable in multicore cable in existing conduits/raceways. The wiring shall be complete with ceiling roses, switches ,Modular Boxes and all consumables.All circuit terminations shall be provided with solder less crimping type copper sockets / lugs, ferrules indicating source code on load side & load code on source side. There shall not be any joints in the circuits, only looping is allowed in terminal blocks & in switches / Sensors/ socket outlets. Kindly refer IS 694:1990. | [5 empty] | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
5.7 | PRIMARY LIGHT POINT - Vendor to calculate the length based on the lighting layout & quote accordingly | [5 empty] | 0 | 0 | 0 | Point Wiring for Lights - Cu Flexible Wires | 1 - 3CX1.5 SQMM FRLS COPPER FLEXIBLE CABLE, 1 - 2CX1.5 SQMM FRLS COPPER FLEXIBLE CABLE TRANSPARENT, 1 - 1.5 SQMM FRLS COPPER WIRE RED, 1 - 1.5 SQMM FRLS COPPER WIRE BLACK, 1 - 1.5 SQMM FRLS COPPER WIRE BLUE, 1 - 1.5 SQMM FRLS COPPER WIRE GREEN, 1 - PVC CONDUIT - 19 MM, 1 - PVC BOX - 2 Module, 1 - PVC BOX - 3 Module, 1 - GI BOX - 2 Module, 1 - GI BOX - 3 Module, 1 - GI BOX - 4 Module
| Primary light point means wiring from DB to first light point. The cost shall include Ceiling flexible conduit at the drop of light fixture. | Nos. | 5 | 5 | 3970 | 800 | 19850 | 4000 | 23850 | Point Wiring for Lights - Cu Flexible Wires | 5 - 3CX1.5 SQMM FRLS COPPER FLEXIBLE CABLE, 5 - 2CX1.5 SQMM FRLS COPPER FLEXIBLE CABLE TRANSPARENT, 5 - 1.5 SQMM FRLS COPPER WIRE RED, 5 - 1.5 SQMM FRLS COPPER WIRE BLACK, 5 - 1.5 SQMM FRLS COPPER WIRE BLUE, 5 - 1.5 SQMM FRLS COPPER WIRE GREEN, 5 - PVC CONDUIT - 19 MM, 5 - PVC BOX - 2 Module, 5 - PVC BOX - 3 Module, 5 - GI BOX - 2 Module, 5 - GI BOX - 3 Module, 5 - GI BOX - 4 Module
[7 empty] | 0 | 0 | 0
5.8 | SECONDARY LIGHT POINT- Vendor to calculate the length based on the lighting layout & quote accordingly | [5 empty] | 0 | 0 | 0 | Point Wiring for Lights - Cu Flexible Wires | 1 - 3CX1.5 SQMM FRLS COPPER FLEXIBLE CABLE, 1 - 2CX1.5 SQMM FRLS COPPER FLEXIBLE CABLE TRANSPARENT, 1 - 1.5 SQMM FRLS COPPER WIRE RED, 1 - 1.5 SQMM FRLS COPPER WIRE BLACK, 1 - 1.5 SQMM FRLS COPPER WIRE BLUE, 1 - 1.5 SQMM FRLS COPPER WIRE GREEN, 1 - PVC CONDUIT - 19 MM, 1 - PVC BOX - 2 Module, 1 - PVC BOX - 3 Module, 1 - GI BOX - 2 Module, 1 - GI BOX - 3 Module, 1 - GI BOX - 4 Module
| Secondary light point means extention of light outlet from existing primary point. The cost shall include Ceiling flexible conduit at the drop of light fixture. | Nos. | 25 | 25 | 640 | 130 | 16000 | 3250 | 19250 | Point Wiring for Lights - Cu Flexible Wires | 25 - 3CX1.5 SQMM FRLS COPPER FLEXIBLE CABLE, 25 - 2CX1.5 SQMM FRLS COPPER FLEXIBLE CABLE TRANSPARENT, 25 - 1.5 SQMM FRLS COPPER WIRE RED, 25 - 1.5 SQMM FRLS COPPER WIRE BLACK, 25 - 1.5 SQMM FRLS COPPER WIRE BLUE, 25 - 1.5 SQMM FRLS COPPER WIRE GREEN, 25 - PVC CONDUIT - 19 MM, 25 - PVC BOX - 2 Module, 25 - PVC BOX - 3 Module, 25 - GI BOX - 2 Module, 25 - GI BOX - 3 Module, 25 - GI BOX - 4 Module
[7 empty] | 0 | 0 | 0
D | Supply, Installation, Testing and Commissioning of of following size 2mm thick rigid FRLS PVC conduits & accessories fixing in ceiling/wall/Parition etc | [5 empty] | 0 | 0 | 0
5.7 | 32mm dia | Mts. | 50 | 50 | 100 | 20 | 5000 | 1000 | 6000 | Ceiling Conduit Work | 50 - PVC CONDUIT - 32 MM, 50 - MS CONDUIT - 32 MM, 50 - PVC BEND - 32 MM, 50 - GI SADDLE WITHOUT BASE - 32MM, 50 - MS Collar - 32MM
[7 empty] | 0 | 0 | 0
5.8 | 25mm dia | Mts. | 150 | 150 | 60 | 20 | 9000 | 3000 | 12000 | Ceiling Conduit Work | 150 - PVC CONDUIT - 25MM, 150 - MS CONDUIT - 25 MM, 150 - GI SADDLE WITHOUT BASE - 25MM, 150 - GI Flexible Conduit Adapter - 25MM
[7 empty] | 0 | 0 | 0
5.9 | 20mm dia | Mts. | 200 | 200 | 50 | 20 | 10000 | 4000 | 14000 | Ceiling Conduit Work | 200 - PVC CONDUIT - 19 MM, 200 - PVC BEND - 19 MM
[7 empty] | 0 | 0 | 0
5.1 | Supply , Installation, Testing and Commissioning of recess mounted Occupancy Sensor having coverage area of 400Sq.ft for a mounting height of 2.8Mtr & PIR Technology. | Nos. |  |  |  |  | 0 | 0 | 0 | Testing & Commissioning | 1 - OCCUPANCY SENSORS - HONEYWELL MK, 1 - Occupancy Sensor With Back Box - Legrand
[7 empty] | 0 | 0 | 0
5.11 | Supply , Installation, Testing and Commissioning of recess mounted dimmable/ Day light Occupancy Sensor having coverage area of 400Sq.ft for a mounting height of 2.8Mtr & PIR Technology. | Nos. |  |  |  |  | 0 | 0 | 0 | Testing & Commissioning | 1 - OCCUPANCY SENSORS - HONEYWELL MK, 1 - Occupancy Sensor With Back Box - Legrand
[7 empty] | 0 | 0 | 0
5.12 | Supply & Installation of supports for sensors . Costig shall include all necessary supports to complete the same. Sample approval to be taken before installation & colour of the supports should match architect intent .. Costing shall include painting works & height adjustable for the supports as per the site requirement | Nos. |  |  |  |  | 0 | 0 | 0 | Testing & Commissioning | 1 - OCCUPANCY SENSORS - HONEYWELL MK, 1 - Occupancy Sensor With Back Box - Legrand
[7 empty] | 0 | 0 | 0
5.13 | Supply, Installation, Testing and Commissioning of 2 channel DALI module The module is DIN rail or direct mountable. Each channel should be capable of handling 64 adre4sses and 16 zones. | Nos. |  |  |  |  | 0 | 0 | 0 | Testing & Commissioning
[7 empty] | 0 | 0 | 0
5.14 | Supply, Installation, Testing and Commissioning of QS sensor module to communicate with wireless occupancy sensor and wireless keypads. This module is mounted in the ceiling. This is connected to 0-10V module using 4C X 1.5 sqmm wire. | Nos. |  |  |  |  | 0 | 0 | 0 | Testing & Commissioning | 1 - OCCUPANCY SENSORS - HONEYWELL MK, 1 - Occupancy Sensor With Back Box - Legrand
[7 empty] | 0 | 0 | 0
5.15 | Supply, Installation, Testing and Commissioning of 6 button with raise & lower wall mounted wired / wireless keypad with white finish. No back box should be required for the same and should be mountable on any surface. No sperate power 230V power supply should be required for this keypad. | Nos. |  |  |  |  | 0 | 0 | 0 | Testing & Commissioning
[7 empty] | 0 | 0 | 0
5.16 | Supply, Installation, Testing and Commissioning of Wireless Ceiling mounted Occupancy dimmable Sensor with radio frequency and connect with relay or 0-10v module wirelessly. The sensors should not interfere with any other wireless devices. | Nos. |  |  |  |  | 0 | 0 | 0 | Testing & Commissioning | 1 - OCCUPANCY SENSORS - HONEYWELL MK, 1 - Occupancy Sensor With Back Box - Legrand
[7 empty] | 0 | 0 | 0
5.17 | Supply, Installation, Testing and Commissioning of Network interface versatile integration access point for Lutron’s QS-based systems. Through either RS232 or TCP/IP over Ethernet, third-party devices can control and/or monitor a QS system. Easily integrate with touchscreens, PCs, A/V systems, or other digital systems and devices. | Nos. |  |  |  |  | 0 | 0 | 0 | Testing & Commissioning
[7 empty] | 0 | 0 | 0
5.18 | Supply, Installation, Testing and Commissioning of 4Cx1.5sqmm FRLS 1100V PVC double insulated flexible multicore cable drawn in 20mm dia 2mm thick rigid PVC existing conduit of approved make. | Mtrs |  |  |  |  | 0 | 0 | 0 | Circuit Wiring for Lights - Cu Flexible Cables | 1 - 4CX1.5 SQMM FRLS COPPER FLEXIBLE CABLE
[7 empty] | 0 | 0 | 0
5.19 | Supply, Installation, Testing and Commissioning of 2Cx1.5sqmm FRLS 1100V PVC double insulated flexible multicore cable drawn in 20mm dia 2mm thick rigid PVC existing conduit of approved make. | Mtrs |  |  |  |  | 0 | 0 | 0 | Circuit Wiring for Lights - Cu Flexible Cables | 1 - 2CX1.5 SQMM FRLS COPPER FLEXIBLE CABLE TRANSPARENT
[7 empty] | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
VI | POWER RECEPTACLES. | [5 empty] | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
| Supply, Installation, Testing and Commissioning of the following Modular/Industrial Switch, sockets with modular front plate, and accessories as per the site conditions. | [5 empty] | 0 | 0 | 0
| The quoted rate for power socket outlets shall include a. Socket outlets - As specified b. Switches c. 20SWG metal boxes with knockout on all sides d. Front plate of required colours(As per architect Approval) with accessories | [5 empty] | 0 | 0 | 0
| Industrial type sockets shall be of Polycarbonate body with plug top & locking facility. All switch / sockets shall be provided with printed labels / stickers indicating source code. Colour code for UPS socket plates : White/ as per architect. Colour code for RP socket plates : Black/Grey/ as per architect. All switch / sockets including front plate & frame which will be mounted on the metal boxes shall have removable film coat to protect from scratches & paint during installation.Prior Approval to be taken from Architect/Consultants before Procurement | [5 empty] | 0 | 0 | 0
| Note: Safety shutters to prevent accidental contact with live parts shall be provided & 4 mm Acrylic sheet to be provided for sockets face plate whichever is connected with box | [5 empty] | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
| Colour codes for HUB/server Industrial Sockets to be followed as below | [5 empty] | 0 | 0 | 0
| Source #1 - Blue | [5 empty] | 0 | 0 | 0
| Source #2 - Orange | [5 empty] | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
| Colour codes for kictehen Industrial Sockets to be followed as per architect .Socket type shall be round pin type as per the availibility/Norms . Same will be decided at the time of approval .. Costing shall include selection of any time of sockets | [5 empty] | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
| Colour codes for workstation Sockets to be followed as below as per architect | [5 empty] | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
A | Without box | [5 empty] | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
6.1 | 1x6/16A intel socket controlled by 16A switch | Nos. | 50 | 50 | 320 | 70 | 16000 | 3500 | 19500 | Wall Switch Socket Installation | 50 - 6/16A 3 PIN ROUND SOCKET, 50 - 6A 3 PIN ROUND SOCKET, 50 - 6A 1 WAY SWITCH, 50 - 6A 2 WAY SWITCH, 50 - 16A 3 PIN ROUND SOCKET, 50 - 16A 1 WAY SWITCH WITH INDICATOR, 50 - 16A 1 WAY SWITCH WITHOUT INDICATOR, 50 - 1M FACE PLATE, 50 - 2M FACE PLATE, 50 - 3M FACE PLATE, 50 - 4M FACE PLATE, 50 - 6M FACE PLATE, 50 - 8M FACE PLATE, 50 - 9M FACE PLATE, 50 - 12M FACE PLATE, 50 - 18M FACE PLATE, 50 - GI BOX - 2 Module, 50 - GI BOX - 3 Module, 50 - GI BOX - 4 Module, 50 - GI BOX - 6 Module, 50 - GI BOX - 8 Module, 50 - GI BOX - 9 Module, 50 - PVC BOX - 2 Module, 50 - PVC BOX - 3 Module, 50 - PVC BOX - 6 Module, 50 - PVC BOX - 8 Module
[7 empty] | 0 | 0 | 0
6.2 | 2x6A intel socket controlled by 16A switch | Nos. |  |  |  |  | 0 | 0 | 0 | Wall Switch Socket Installation | 1 - 6/16A 3 PIN ROUND SOCKET, 1 - 6A 3 PIN ROUND SOCKET, 1 - 6A 1 WAY SWITCH, 1 - 6A 2 WAY SWITCH, 1 - 16A 3 PIN ROUND SOCKET, 1 - 16A 1 WAY SWITCH WITH INDICATOR, 1 - 16A 1 WAY SWITCH WITHOUT INDICATOR, 1 - 1M FACE PLATE, 1 - 2M FACE PLATE, 1 - 3M FACE PLATE, 1 - 4M FACE PLATE, 1 - 6M FACE PLATE, 1 - 8M FACE PLATE, 1 - 9M FACE PLATE, 1 - 12M FACE PLATE, 1 - 18M FACE PLATE, 1 - GI BOX - 2 Module, 1 - GI BOX - 3 Module, 1 - GI BOX - 4 Module, 1 - GI BOX - 6 Module, 1 - GI BOX - 8 Module, 1 - GI BOX - 9 Module, 1 - PVC BOX - 2 Module, 1 - PVC BOX - 3 Module, 1 - PVC BOX - 6 Module, 1 - PVC BOX - 8 Module
[7 empty] | 0 | 0 | 0
6.3 | 3x6/16A intel socket controlled by 16A switch | Nos. | 2 | 2 | 700 | 140 | 1400 | 280 | 1680 | Wall Switch Socket Installation | 2 - 6/16A 3 PIN ROUND SOCKET, 2 - 6A 3 PIN ROUND SOCKET, 2 - 6A 1 WAY SWITCH, 2 - 6A 2 WAY SWITCH, 2 - 16A 3 PIN ROUND SOCKET, 2 - 16A 1 WAY SWITCH WITH INDICATOR, 2 - 16A 1 WAY SWITCH WITHOUT INDICATOR, 2 - 1M FACE PLATE, 2 - 2M FACE PLATE, 2 - 3M FACE PLATE, 2 - 4M FACE PLATE, 2 - 6M FACE PLATE, 2 - 8M FACE PLATE, 2 - 9M FACE PLATE, 2 - 12M FACE PLATE, 2 - 18M FACE PLATE, 2 - GI BOX - 2 Module, 2 - GI BOX - 3 Module, 2 - GI BOX - 4 Module, 2 - GI BOX - 6 Module, 2 - GI BOX - 8 Module, 2 - GI BOX - 9 Module, 2 - PVC BOX - 2 Module, 2 - PVC BOX - 3 Module, 2 - PVC BOX - 6 Module, 2 - PVC BOX - 8 Module
[7 empty] | 0 | 0 | 0
6.4 | 2x6/16A intel socket controlled by 16A switch | Nos. | 50 | 50 | 520 | 110 | 26000 | 5500 | 31500 | Wall Switch Socket Installation | 50 - 6/16A 3 PIN ROUND SOCKET, 50 - 6A 3 PIN ROUND SOCKET, 50 - 6A 1 WAY SWITCH, 50 - 6A 2 WAY SWITCH, 50 - 16A 3 PIN ROUND SOCKET, 50 - 16A 1 WAY SWITCH WITH INDICATOR, 50 - 16A 1 WAY SWITCH WITHOUT INDICATOR, 50 - 1M FACE PLATE, 50 - 2M FACE PLATE, 50 - 3M FACE PLATE, 50 - 4M FACE PLATE, 50 - 6M FACE PLATE, 50 - 8M FACE PLATE, 50 - 9M FACE PLATE, 50 - 12M FACE PLATE, 50 - 18M FACE PLATE, 50 - GI BOX - 2 Module, 50 - GI BOX - 3 Module, 50 - GI BOX - 4 Module, 50 - GI BOX - 6 Module, 50 - GI BOX - 8 Module, 50 - GI BOX - 9 Module, 50 - PVC BOX - 2 Module, 50 - PVC BOX - 3 Module, 50 - PVC BOX - 6 Module, 50 - PVC BOX - 8 Module
[7 empty] | 0 | 0 | 0
6.5 | 1x6/16A Round pin socket controlled by 6A switch | Nos. |  |  |  |  | 0 | 0 | 0 | Wall Switch Socket Installation | 1 - 6/16A 3 PIN ROUND SOCKET, 1 - 6A 3 PIN ROUND SOCKET, 1 - 6A 1 WAY SWITCH, 1 - 6A 2 WAY SWITCH, 1 - 16A 3 PIN ROUND SOCKET, 1 - 16A 1 WAY SWITCH WITH INDICATOR, 1 - 16A 1 WAY SWITCH WITHOUT INDICATOR, 1 - 1M FACE PLATE, 1 - 2M FACE PLATE, 1 - 3M FACE PLATE, 1 - 4M FACE PLATE, 1 - 6M FACE PLATE, 1 - 8M FACE PLATE, 1 - 9M FACE PLATE, 1 - 12M FACE PLATE, 1 - 18M FACE PLATE, 1 - GI BOX - 2 Module, 1 - GI BOX - 3 Module, 1 - GI BOX - 4 Module, 1 - GI BOX - 6 Module, 1 - GI BOX - 8 Module, 1 - GI BOX - 9 Module, 1 - PVC BOX - 2 Module, 1 - PVC BOX - 3 Module, 1 - PVC BOX - 6 Module, 1 - PVC BOX - 8 Module
[7 empty] | 0 | 0 | 0
6.6 | 2x6/16A Round pin socket controlled by 16A switch | Nos. |  |  |  |  | 0 | 0 | 0 | Wall Switch Socket Installation | 1 - 6/16A 3 PIN ROUND SOCKET, 1 - 6A 3 PIN ROUND SOCKET, 1 - 6A 1 WAY SWITCH, 1 - 6A 2 WAY SWITCH, 1 - 16A 3 PIN ROUND SOCKET, 1 - 16A 1 WAY SWITCH WITH INDICATOR, 1 - 16A 1 WAY SWITCH WITHOUT INDICATOR, 1 - 1M FACE PLATE, 1 - 2M FACE PLATE, 1 - 3M FACE PLATE, 1 - 4M FACE PLATE, 1 - 6M FACE PLATE, 1 - 8M FACE PLATE, 1 - 9M FACE PLATE, 1 - 12M FACE PLATE, 1 - 18M FACE PLATE, 1 - GI BOX - 2 Module, 1 - GI BOX - 3 Module, 1 - GI BOX - 4 Module, 1 - GI BOX - 6 Module, 1 - GI BOX - 8 Module, 1 - GI BOX - 9 Module, 1 - PVC BOX - 2 Module, 1 - PVC BOX - 3 Module, 1 - PVC BOX - 6 Module, 1 - PVC BOX - 8 Module
[7 empty] | 0 | 0 | 0
6.7 | 3x6/16A Round pin socket controlled by 16A switch | Nos. |  |  |  |  | 0 | 0 | 0 | Wall Switch Socket Installation | 1 - 6/16A 3 PIN ROUND SOCKET, 1 - 6A 3 PIN ROUND SOCKET, 1 - 6A 1 WAY SWITCH, 1 - 6A 2 WAY SWITCH, 1 - 16A 3 PIN ROUND SOCKET, 1 - 16A 1 WAY SWITCH WITH INDICATOR, 1 - 16A 1 WAY SWITCH WITHOUT INDICATOR, 1 - 1M FACE PLATE, 1 - 2M FACE PLATE, 1 - 3M FACE PLATE, 1 - 4M FACE PLATE, 1 - 6M FACE PLATE, 1 - 8M FACE PLATE, 1 - 9M FACE PLATE, 1 - 12M FACE PLATE, 1 - 18M FACE PLATE, 1 - GI BOX - 2 Module, 1 - GI BOX - 3 Module, 1 - GI BOX - 4 Module, 1 - GI BOX - 6 Module, 1 - GI BOX - 8 Module, 1 - GI BOX - 9 Module, 1 - PVC BOX - 2 Module, 1 - PVC BOX - 3 Module, 1 - PVC BOX - 6 Module, 1 - PVC BOX - 8 Module
[7 empty] | 0 | 0 | 0
6.8 | 4x6/16A Round pin socket controlled by 16A switch | Nos. |  |  |  |  | 0 | 0 | 0 | Wall Switch Socket Installation | 1 - 6/16A 3 PIN ROUND SOCKET, 1 - 6A 3 PIN ROUND SOCKET, 1 - 6A 1 WAY SWITCH, 1 - 6A 2 WAY SWITCH, 1 - 16A 3 PIN ROUND SOCKET, 1 - 16A 1 WAY SWITCH WITH INDICATOR, 1 - 16A 1 WAY SWITCH WITHOUT INDICATOR, 1 - 1M FACE PLATE, 1 - 2M FACE PLATE, 1 - 3M FACE PLATE, 1 - 4M FACE PLATE, 1 - 6M FACE PLATE, 1 - 8M FACE PLATE, 1 - 9M FACE PLATE, 1 - 12M FACE PLATE, 1 - 18M FACE PLATE, 1 - GI BOX - 2 Module, 1 - GI BOX - 3 Module, 1 - GI BOX - 4 Module, 1 - GI BOX - 6 Module, 1 - GI BOX - 8 Module, 1 - GI BOX - 9 Module, 1 - PVC BOX - 2 Module, 1 - PVC BOX - 3 Module, 1 - PVC BOX - 6 Module, 1 - PVC BOX - 8 Module
[7 empty] | 0 | 0 | 0
B | With box | [5 empty] | 0 | 0 | 0
6.9 | 1x6/16A intel socket controlled by 16A switch | Nos. | 20 | 20 | 370 | 80 | 7400 | 1600 | 9000 | Wall Switch Socket Installation | 20 - 6/16A 3 PIN ROUND SOCKET, 20 - 6A 3 PIN ROUND SOCKET, 20 - 6A 1 WAY SWITCH, 20 - 6A 2 WAY SWITCH, 20 - 16A 3 PIN ROUND SOCKET, 20 - 16A 1 WAY SWITCH WITH INDICATOR, 20 - 16A 1 WAY SWITCH WITHOUT INDICATOR, 20 - 1M FACE PLATE, 20 - 2M FACE PLATE, 20 - 3M FACE PLATE, 20 - 4M FACE PLATE, 20 - 6M FACE PLATE, 20 - 8M FACE PLATE, 20 - 9M FACE PLATE, 20 - 12M FACE PLATE, 20 - 18M FACE PLATE, 20 - GI BOX - 2 Module, 20 - GI BOX - 3 Module, 20 - GI BOX - 4 Module, 20 - GI BOX - 6 Module, 20 - GI BOX - 8 Module, 20 - GI BOX - 9 Module, 20 - PVC BOX - 2 Module, 20 - PVC BOX - 3 Module, 20 - PVC BOX - 6 Module, 20 - PVC BOX - 8 Module
[7 empty] | 0 | 0 | 0
6.1 | 2x6/16A intel socket controlled by 16A switch | Nos. | 10 | 10 | 610 | 130 | 6100 | 1300 | 7400 | Wall Switch Socket Installation | 10 - 6/16A 3 PIN ROUND SOCKET, 10 - 6A 3 PIN ROUND SOCKET, 10 - 6A 1 WAY SWITCH, 10 - 6A 2 WAY SWITCH, 10 - 16A 3 PIN ROUND SOCKET, 10 - 16A 1 WAY SWITCH WITH INDICATOR, 10 - 16A 1 WAY SWITCH WITHOUT INDICATOR, 10 - 1M FACE PLATE, 10 - 2M FACE PLATE, 10 - 3M FACE PLATE, 10 - 4M FACE PLATE, 10 - 6M FACE PLATE, 10 - 8M FACE PLATE, 10 - 9M FACE PLATE, 10 - 12M FACE PLATE, 10 - 18M FACE PLATE, 10 - GI BOX - 2 Module, 10 - GI BOX - 3 Module, 10 - GI BOX - 4 Module, 10 - GI BOX - 6 Module, 10 - GI BOX - 8 Module, 10 - GI BOX - 9 Module, 10 - PVC BOX - 2 Module, 10 - PVC BOX - 3 Module, 10 - PVC BOX - 6 Module, 10 - PVC BOX - 8 Module
[7 empty] | 0 | 0 | 0
6.11 | 3x6/16A intel socket controlled by 16A switch | Nos. | 6 | 6 | 810 | 170 | 4860 | 1020 | 5880 | Wall Switch Socket Installation | 6 - 6/16A 3 PIN ROUND SOCKET, 6 - 6A 3 PIN ROUND SOCKET, 6 - 6A 1 WAY SWITCH, 6 - 6A 2 WAY SWITCH, 6 - 16A 3 PIN ROUND SOCKET, 6 - 16A 1 WAY SWITCH WITH INDICATOR, 6 - 16A 1 WAY SWITCH WITHOUT INDICATOR, 6 - 1M FACE PLATE, 6 - 2M FACE PLATE, 6 - 3M FACE PLATE, 6 - 4M FACE PLATE, 6 - 6M FACE PLATE, 6 - 8M FACE PLATE, 6 - 9M FACE PLATE, 6 - 12M FACE PLATE, 6 - 18M FACE PLATE, 6 - GI BOX - 2 Module, 6 - GI BOX - 3 Module, 6 - GI BOX - 4 Module, 6 - GI BOX - 6 Module, 6 - GI BOX - 8 Module, 6 - GI BOX - 9 Module, 6 - PVC BOX - 2 Module, 6 - PVC BOX - 3 Module, 6 - PVC BOX - 6 Module, 6 - PVC BOX - 8 Module
[7 empty] | 0 | 0 | 0
6.12 | 4x6/16A intel socket controlled by 16A switch | Nos. |  |  |  |  | 0 | 0 | 0 | Wall Switch Socket Installation | 1 - 6/16A 3 PIN ROUND SOCKET, 1 - 6A 3 PIN ROUND SOCKET, 1 - 6A 1 WAY SWITCH, 1 - 6A 2 WAY SWITCH, 1 - 16A 3 PIN ROUND SOCKET, 1 - 16A 1 WAY SWITCH WITH INDICATOR, 1 - 16A 1 WAY SWITCH WITHOUT INDICATOR, 1 - 1M FACE PLATE, 1 - 2M FACE PLATE, 1 - 3M FACE PLATE, 1 - 4M FACE PLATE, 1 - 6M FACE PLATE, 1 - 8M FACE PLATE, 1 - 9M FACE PLATE, 1 - 12M FACE PLATE, 1 - 18M FACE PLATE, 1 - GI BOX - 2 Module, 1 - GI BOX - 3 Module, 1 - GI BOX - 4 Module, 1 - GI BOX - 6 Module, 1 - GI BOX - 8 Module, 1 - GI BOX - 9 Module, 1 - PVC BOX - 2 Module, 1 - PVC BOX - 3 Module, 1 - PVC BOX - 6 Module, 1 - PVC BOX - 8 Module
[7 empty] | 0 | 0 | 0
6.13 | 1x6/16A intel socket controlled by 16A switch | Nos. |  |  |  |  | 0 | 0 | 0 | Wall Switch Socket Installation | 1 - 6/16A 3 PIN ROUND SOCKET, 1 - 6A 3 PIN ROUND SOCKET, 1 - 6A 1 WAY SWITCH, 1 - 6A 2 WAY SWITCH, 1 - 16A 3 PIN ROUND SOCKET, 1 - 16A 1 WAY SWITCH WITH INDICATOR, 1 - 16A 1 WAY SWITCH WITHOUT INDICATOR, 1 - 1M FACE PLATE, 1 - 2M FACE PLATE, 1 - 3M FACE PLATE, 1 - 4M FACE PLATE, 1 - 6M FACE PLATE, 1 - 8M FACE PLATE, 1 - 9M FACE PLATE, 1 - 12M FACE PLATE, 1 - 18M FACE PLATE, 1 - GI BOX - 2 Module, 1 - GI BOX - 3 Module, 1 - GI BOX - 4 Module, 1 - GI BOX - 6 Module, 1 - GI BOX - 8 Module, 1 - GI BOX - 9 Module, 1 - PVC BOX - 2 Module, 1 - PVC BOX - 3 Module, 1 - PVC BOX - 6 Module, 1 - PVC BOX - 8 Module
[7 empty] | 0 | 0 | 0
6.14 | 1x6A Round pin socket controlled by 6A switch | Nos. |  |  |  |  | 0 | 0 | 0 | Wall Switch Socket Installation | 1 - 6/16A 3 PIN ROUND SOCKET, 1 - 6A 3 PIN ROUND SOCKET, 1 - 6A 1 WAY SWITCH, 1 - 6A 2 WAY SWITCH, 1 - 1M FACE PLATE, 1 - 2M FACE PLATE, 1 - 3M FACE PLATE, 1 - 4M FACE PLATE, 1 - 6M FACE PLATE, 1 - 8M FACE PLATE, 1 - 9M FACE PLATE, 1 - 12M FACE PLATE, 1 - 18M FACE PLATE, 1 - GI BOX - 2 Module, 1 - GI BOX - 3 Module, 1 - GI BOX - 4 Module, 1 - GI BOX - 6 Module, 1 - GI BOX - 8 Module, 1 - GI BOX - 9 Module, 1 - PVC BOX - 2 Module, 1 - PVC BOX - 3 Module, 1 - PVC BOX - 6 Module, 1 - PVC BOX - 8 Module
[7 empty] | 0 | 0 | 0
6.15 | 1x6/16A Round pin socket controlled by 16A switch | Nos. |  |  |  |  | 0 | 0 | 0 | Wall Switch Socket Installation | 1 - 6/16A 3 PIN ROUND SOCKET, 1 - 6A 3 PIN ROUND SOCKET, 1 - 6A 1 WAY SWITCH, 1 - 6A 2 WAY SWITCH, 1 - 16A 3 PIN ROUND SOCKET, 1 - 16A 1 WAY SWITCH WITH INDICATOR, 1 - 16A 1 WAY SWITCH WITHOUT INDICATOR, 1 - 1M FACE PLATE, 1 - 2M FACE PLATE, 1 - 3M FACE PLATE, 1 - 4M FACE PLATE, 1 - 6M FACE PLATE, 1 - 8M FACE PLATE, 1 - 9M FACE PLATE, 1 - 12M FACE PLATE, 1 - 18M FACE PLATE, 1 - GI BOX - 2 Module, 1 - GI BOX - 3 Module, 1 - GI BOX - 4 Module, 1 - GI BOX - 6 Module, 1 - GI BOX - 8 Module, 1 - GI BOX - 9 Module, 1 - PVC BOX - 2 Module, 1 - PVC BOX - 3 Module, 1 - PVC BOX - 6 Module, 1 - PVC BOX - 8 Module
[7 empty] | 0 | 0 | 0
6.16 | 2x6/16A Round pin socket controlled by 16A switch | Nos. |  |  |  |  | 0 | 0 | 0 | Wall Switch Socket Installation | 1 - 6/16A 3 PIN ROUND SOCKET, 1 - 6A 3 PIN ROUND SOCKET, 1 - 6A 1 WAY SWITCH, 1 - 6A 2 WAY SWITCH, 1 - 16A 3 PIN ROUND SOCKET, 1 - 16A 1 WAY SWITCH WITH INDICATOR, 1 - 16A 1 WAY SWITCH WITHOUT INDICATOR, 1 - 1M FACE PLATE, 1 - 2M FACE PLATE, 1 - 3M FACE PLATE, 1 - 4M FACE PLATE, 1 - 6M FACE PLATE, 1 - 8M FACE PLATE, 1 - 9M FACE PLATE, 1 - 12M FACE PLATE, 1 - 18M FACE PLATE, 1 - GI BOX - 2 Module, 1 - GI BOX - 3 Module, 1 - GI BOX - 4 Module, 1 - GI BOX - 6 Module, 1 - GI BOX - 8 Module, 1 - GI BOX - 9 Module, 1 - PVC BOX - 2 Module, 1 - PVC BOX - 3 Module, 1 - PVC BOX - 6 Module, 1 - PVC BOX - 8 Module
[7 empty] | 0 | 0 | 0
6.17 | 3x6/16A Round pin socket controlled by 16A switch | Nos. |  |  |  |  | 0 | 0 | 0 | Wall Switch Socket Installation | 1 - 6/16A 3 PIN ROUND SOCKET, 1 - 6A 3 PIN ROUND SOCKET, 1 - 6A 1 WAY SWITCH, 1 - 6A 2 WAY SWITCH, 1 - 16A 3 PIN ROUND SOCKET, 1 - 16A 1 WAY SWITCH WITH INDICATOR, 1 - 16A 1 WAY SWITCH WITHOUT INDICATOR, 1 - 1M FACE PLATE, 1 - 2M FACE PLATE, 1 - 3M FACE PLATE, 1 - 4M FACE PLATE, 1 - 6M FACE PLATE, 1 - 8M FACE PLATE, 1 - 9M FACE PLATE, 1 - 12M FACE PLATE, 1 - 18M FACE PLATE, 1 - GI BOX - 2 Module, 1 - GI BOX - 3 Module, 1 - GI BOX - 4 Module, 1 - GI BOX - 6 Module, 1 - GI BOX - 8 Module, 1 - GI BOX - 9 Module, 1 - PVC BOX - 2 Module, 1 - PVC BOX - 3 Module, 1 - PVC BOX - 6 Module, 1 - PVC BOX - 8 Module
[7 empty] | 0 | 0 | 0
6.18 | 4x6/16A Round pin socket controlled by 16A switch | Nos. |  |  |  |  | 0 | 0 | 0 | Wall Switch Socket Installation | 1 - 6/16A 3 PIN ROUND SOCKET, 1 - 6A 3 PIN ROUND SOCKET, 1 - 6A 1 WAY SWITCH, 1 - 6A 2 WAY SWITCH, 1 - 16A 3 PIN ROUND SOCKET, 1 - 16A 1 WAY SWITCH WITH INDICATOR, 1 - 16A 1 WAY SWITCH WITHOUT INDICATOR, 1 - 1M FACE PLATE, 1 - 2M FACE PLATE, 1 - 3M FACE PLATE, 1 - 4M FACE PLATE, 1 - 6M FACE PLATE, 1 - 8M FACE PLATE, 1 - 9M FACE PLATE, 1 - 12M FACE PLATE, 1 - 18M FACE PLATE, 1 - GI BOX - 2 Module, 1 - GI BOX - 3 Module, 1 - GI BOX - 4 Module, 1 - GI BOX - 6 Module, 1 - GI BOX - 8 Module, 1 - GI BOX - 9 Module, 1 - PVC BOX - 2 Module, 1 - PVC BOX - 3 Module, 1 - PVC BOX - 6 Module, 1 - PVC BOX - 8 Module
[7 empty] | 0 | 0 | 0
6.19 | 1 x 16A Round pin socket controlled by 16A switch | Nos. |  |  |  |  | 0 | 0 | 0 | Wall Switch Socket Installation | 1 - 6/16A 3 PIN ROUND SOCKET, 1 - 6A 3 PIN ROUND SOCKET, 1 - 6A 1 WAY SWITCH, 1 - 6A 2 WAY SWITCH, 1 - 16A 3 PIN ROUND SOCKET, 1 - 16A 1 WAY SWITCH WITH INDICATOR, 1 - 16A 1 WAY SWITCH WITHOUT INDICATOR, 1 - 1M FACE PLATE, 1 - 2M FACE PLATE, 1 - 3M FACE PLATE, 1 - 4M FACE PLATE, 1 - 6M FACE PLATE, 1 - 8M FACE PLATE, 1 - 9M FACE PLATE, 1 - 12M FACE PLATE, 1 - 18M FACE PLATE, 1 - GI BOX - 2 Module, 1 - GI BOX - 3 Module, 1 - GI BOX - 4 Module, 1 - GI BOX - 6 Module, 1 - GI BOX - 8 Module, 1 - GI BOX - 9 Module, 1 - PVC BOX - 2 Module, 1 - PVC BOX - 3 Module, 1 - PVC BOX - 6 Module, 1 - PVC BOX - 8 Module
[7 empty] | 0 | 0 | 0
6.2 | Supply, Installation, Testing and Commissioning of USB port (Output Current 0 to 2Amp) - Type C | Nos. |  |  |  |  | 0 | 0 | 0 | Wall Switch Socket Installation | 1 - USB Charger - Type A (1 Module), 1 - USB Charger - Type C (1 Module)
[7 empty] | 0 | 0 | 0
6.21 | Supply, Installation, Testing and Commissioning of USB port (Output Current 0 to 2Amp) - Type A | Nos. |  |  |  |  | 0 | 0 | 0 | Wall Switch Socket Installation | 1 - USB Charger - Type A (1 Module), 1 - USB Charger - Type C (1 Module)
[7 empty] | 0 | 0 | 0
a | Shifting, and refixing of existing workstation power provision sockets, including dismantling, refixing at revised location, reconnection with wiring, testing, and commissioning complete as per site requirements. (460 WS tables) | Nos |  |  |  |  | 0 | 0 | 0 | Wall Switch Socket Installation | 1 - 1M FACE PLATE, 1 - 2M FACE PLATE, 1 - 3M FACE PLATE, 1 - 4M FACE PLATE, 1 - 6M FACE PLATE, 1 - 8M FACE PLATE, 1 - 9M FACE PLATE, 1 - 12M FACE PLATE, 1 - 18M FACE PLATE, 1 - GI BOX - 2 Module, 1 - GI BOX - 3 Module, 1 - GI BOX - 4 Module, 1 - GI BOX - 6 Module, 1 - GI BOX - 8 Module, 1 - GI BOX - 9 Module, 1 - PVC BOX - 2 Module, 1 - PVC BOX - 3 Module, 1 - PVC BOX - 6 Module, 1 - PVC BOX - 8 Module
[7 empty] | 0 | 0 | 0
b | Removing of existing workstaion power sockets set of 2X6/16A 1 nos and 1X6/16 2 nos | Nos |  |  |  |  | 0 | 0 | 0 | Wall Switch Socket Installation | 1 - 6/16A 3 PIN ROUND SOCKET, 1 - 6A 3 PIN ROUND SOCKET, 1 - 6A 1 WAY SWITCH, 1 - 6A 2 WAY SWITCH, 1 - 16A 3 PIN ROUND SOCKET, 1 - 16A 1 WAY SWITCH WITH INDICATOR, 1 - 16A 1 WAY SWITCH WITHOUT INDICATOR, 1 - 1M FACE PLATE, 1 - 2M FACE PLATE, 1 - 3M FACE PLATE, 1 - 4M FACE PLATE, 1 - 6M FACE PLATE, 1 - 8M FACE PLATE, 1 - 9M FACE PLATE, 1 - 12M FACE PLATE, 1 - 18M FACE PLATE, 1 - GI BOX - 2 Module, 1 - GI BOX - 3 Module, 1 - GI BOX - 4 Module, 1 - GI BOX - 6 Module, 1 - GI BOX - 8 Module, 1 - GI BOX - 9 Module, 1 - PVC BOX - 2 Module, 1 - PVC BOX - 3 Module, 1 - PVC BOX - 6 Module, 1 - PVC BOX - 8 Module
C | Industrial Sockets | [5 empty] | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
6.22 | 1No. 63A 3 pin 1phase Industrial type socket with plug top controlled by 32A DP MCB (D CURVE) & Same shall be mounted on Existing powder coated ceiling raceways as per approved sample. ( IP 44) | Nos. | 4 | 4 | 6500 | 1500 | 26000 | 6000 | 32000 | Wall Switch Socket Installation | 4 - 32A Industrial Socket Outlet With MCB Provision Single Phase IP67 - Neptune
[7 empty] | 0 | 0 | 0
6.23 | SCAME/Equivalent Make OPTIMA Series Socket IP44/IP54 Mounted on DOMO Series Surface Mounting Enclosure IP67, with 16 A, P+N+E, 346-415 Volts, IP44 , 6h Type socket with straight Plug 16A, P+N+E, 346-415 Volts. Costing shall include mounting plate to fix the industrial socket in basket tray with all accessories complete .. Make OBO better man & Mounting plate no - MPG 65FT | Nos. |  |  |  |  | 0 | 0 | 0 | Wall Switch Socket Installation | 1 - 32A 4P+E Industrial Socket/Plug IP44 Surface Mount - Legrand Tempra Pro, 1 - 32A Industrial Plug/Socket Three Phase With MCB IP44/54 - Neptune
[7 empty] | 0 | 0 | 0
6.24 | 1No. 16 A 3 pin round pin Socket with 16A Switch (IP65) | Nos. |  |  |  |  | 0 | 0 | 0 | Wall Switch Socket Installation | 1 - 16/20A Industrial Plug/Socket Single Phase With MCB IP44/54 - Neptune
[7 empty] | 0 | 0 | 0
6.25 | 1No. 16A 3 pin 1phase Industrial type socket with plug top controlled by 16A DP MCB with back acrylic sheet 4mm thickness having an overlap around socket face plate 1inch . | Nos. |  |  |  |  | 0 | 0 | 0 | Wall Switch Socket Installation | 1 - 16A 2P+E Industrial Socket/Plug IP44 Panel Mount - Legrand Tempra Pro, 1 - 16/20A Industrial Plug/Socket Single Phase With MCB IP44/54 - Neptune
[7 empty] | 0 | 0 | 0
6.26 | 1No. 16A 5 pin 3phase Industrial type socket with plug top controlled by 16A DP S/W. | Nos. |  |  |  |  | 0 | 0 | 0 | Wall Switch Socket Installation | 1 - 32A 4P+E Industrial Socket/Plug IP44 Surface Mount - Legrand Tempra Pro, 1 - 32A Industrial Socket Outlet Interlocked Three Phase IP67 - Neptune, 1 - 32A Industrial Plug/Socket Three Phase With MCB IP44/54 - Neptune
[7 empty] | 0 | 0 | 0
6.27 | 1No. 32A 3 pin 1phase Industrial type socket with plug top controlled by 32A DP MCB. | Nos. |  |  |  |  | 0 | 0 | 0 | Wall Switch Socket Installation | 1 - 32A 2P+E Industrial Socket/Plug IP44 Surface Mount - Legrand Tempra Pro, 1 - 32A Industrial Socket Outlet Interlocked Single Phase IP67 - Neptune
[7 empty] | 0 | 0 | 0
6.28 | 1No. 40A 3 pin 1phase Industrial type socket with plug top controlled by 40A DP MCB | Nos. |  |  |  |  | 0 | 0 | 0 | Wall Switch Socket Installation | 1 - 32A Industrial Socket Outlet With MCB Provision Single Phase IP67 - Neptune
[7 empty] | 0 | 0 | 0
6.29 | 1No. 63A 3 pin 1phase Industrial type socket with plug top controlled by 63A DP MCB. | Nos. |  |  |  |  | 0 | 0 | 0 | Wall Switch Socket Installation | 1 - 32A Industrial Socket Outlet With MCB Provision Single Phase IP67 - Neptune
[7 empty] | 0 | 0 | 0
6.3 | 1No. 16A 5 pin 3 phase Industrial type socket with plug top controlled by 16A 4P MCB | Nos. |  |  |  |  | 0 | 0 | 0 | Wall Switch Socket Installation | 1 - 6/16A 3 PIN ROUND SOCKET, 1 - 6A 3 PIN ROUND SOCKET, 1 - 6A 1 WAY SWITCH, 1 - 6A 2 WAY SWITCH, 1 - 16A 3 PIN ROUND SOCKET, 1 - 16A 1 WAY SWITCH WITH INDICATOR, 1 - 16A 1 WAY SWITCH WITHOUT INDICATOR, 1 - 1M FACE PLATE, 1 - 2M FACE PLATE, 1 - 3M FACE PLATE, 1 - 4M FACE PLATE, 1 - 6M FACE PLATE, 1 - 8M FACE PLATE, 1 - 9M FACE PLATE, 1 - 12M FACE PLATE, 1 - 18M FACE PLATE, 1 - GI BOX - 2 Module, 1 - GI BOX - 3 Module, 1 - GI BOX - 4 Module, 1 - GI BOX - 6 Module, 1 - GI BOX - 8 Module, 1 - GI BOX - 9 Module, 1 - PVC BOX - 2 Module, 1 - PVC BOX - 3 Module, 1 - PVC BOX - 6 Module, 1 - PVC BOX - 8 Module
[7 empty] | 0 | 0 | 0
6.31 | 1No. 20A 5 pin 3 phase Industrial type socket with plug top controlled by 20A 4P MCB | Nos. |  |  |  |  | 0 | 0 | 0 | Wall Switch Socket Installation | 1 - 32A 4P+E Industrial Socket/Plug IP44 Surface Mount - Legrand Tempra Pro, 1 - 32A Industrial Socket Outlet Interlocked Three Phase IP67 - Neptune, 1 - 32A Industrial Plug/Socket Three Phase With MCB IP44/54 - Neptune
[7 empty] | 0 | 0 | 0
6.32 | 1No. 32A 5 pin 3 phase Industrial type socket with plug top controlled by 32A 4P MCB | Nos. |  |  |  |  | 0 | 0 | 0 | Wall Switch Socket Installation | 1 - 32A 4P+E Industrial Socket/Plug IP44 Surface Mount - Legrand Tempra Pro, 1 - 32A Industrial Socket Outlet Interlocked Three Phase IP67 - Neptune, 1 - 32A Industrial Plug/Socket Three Phase With MCB IP44/54 - Neptune
[7 empty] | 0 | 0 | 0
6.33 | 1No. 40A 5 pin 3 phase Industrial type socket with plug top controlled by 40A 4P MCB | Nos. |  |  |  |  | 0 | 0 | 0 | Wall Switch Socket Installation | 1 - 32A 4P+E Industrial Socket/Plug IP44 Surface Mount - Legrand Tempra Pro, 1 - 32A Industrial Socket Outlet Interlocked Three Phase IP67 - Neptune, 1 - 32A Industrial Plug/Socket Three Phase With MCB IP44/54 - Neptune
[7 empty] | 0 | 0 | 0
6.34 | 1No. 63A 5 pin 3 phase Industrial type socket with plug top controlled by 63A 4P MCB | Nos. |  |  |  |  | 0 | 0 | 0 | Wall Switch Socket Installation | 1 - 32A 4P+E Industrial Socket/Plug IP44 Surface Mount - Legrand Tempra Pro, 1 - 32A Industrial Socket Outlet Interlocked Three Phase IP67 - Neptune, 1 - 32A Industrial Plug/Socket Three Phase With MCB IP44/54 - Neptune
[7 empty] | 0 | 0 | 0
D | FLOOR SERVICE BOXES | [5 empty] | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
6.35 | Supply & Installation of Floor service box suitable for fixing 1 Set of 2x6/16A round socket controlled by 16A switch in one compartment & in other compartment place provision for mounting 2 Data / 1 HDMI (The rate to include cost of sockets) Finish:SS Type | Nos. | 2 | 2 | 8500 | 1000 | 17000 | 2000 | 19000 | User Switch Socket Installation | 2 - Legrand Floor Power Box 275×275×60, 2 - Floor EGA Box (300X300) - Steelways, 2 - 6/16A 3 PIN ROUND SOCKET, 2 - 16A 3 PIN ROUND SOCKET, 2 - 1M FACE PLATE, 2 - 2M FACE PLATE, 2 - 3M FACE PLATE, 2 - 4M FACE PLATE
[7 empty] | 0 | 0 | 0
6.36 | Supply & Installation of Floor service box suitable for fixing 1 Set of 2x6/16A round socket controlled by 16A switch in one compartment & in other compartment place provision for mounting 1 Data (The rate to include cost of sockets) Finish:SS Type | Nos. |  |  |  |  | 0 | 0 | 0 | User Switch Socket Installation | 1 - Legrand Floor Power Box 275×275×60, 1 - Floor EGA Box (300X300) - Steelways, 1 - 6/16A 3 PIN ROUND SOCKET, 1 - 16A 3 PIN ROUND SOCKET, 1 - 1M FACE PLATE, 1 - 2M FACE PLATE, 1 - 3M FACE PLATE, 1 - 4M FACE PLATE
[7 empty] | 0 | 0 | 0
6.37 | Supply & Installation of Floor service box suitable for fixing 2 Set of 3x6/16A round socket controlled by 16A switch in one compartment & in other compartment place provision for mounting 1 Data (The rate to include cost of sockets) Finish:SS Type | Nos. |  |  |  |  | 0 | 0 | 0 | User Switch Socket Installation | 1 - Legrand Floor Power Box 275×275×60, 1 - Floor EGA Box (300X300) - Steelways, 1 - 6/16A 3 PIN ROUND SOCKET, 1 - 16A 3 PIN ROUND SOCKET, 1 - 1M FACE PLATE, 1 - 2M FACE PLATE, 1 - 3M FACE PLATE, 1 - 4M FACE PLATE
[7 empty] | 0 | 0 | 0
6.38 | Supply & Installation of Floor service box suitable for fixing 2 Set of 3 x6/16A round socket controlled by 16A switch in one compartment & in other compartment place provision for mounting 1 Data / 1 Voice points/1 HDMI (The rate to include cost of sockets) Finish:SS Type | Nos. |  |  |  |  | 0 | 0 | 0 | User Switch Socket Installation | 1 - Legrand Floor Power Box 275×275×60, 1 - Floor EGA Box (300X300) - Steelways, 1 - 6/16A 3 PIN ROUND SOCKET, 1 - 16A 3 PIN ROUND SOCKET, 1 - 1M FACE PLATE, 1 - 2M FACE PLATE, 1 - 3M FACE PLATE, 1 - 4M FACE PLATE
[7 empty] | 0 | 0 | 0
6.39 | Supply & Installation of Floor service box suitable for fixing1 Set of 4x6/16A round socket controlled by 16A switch in one compartment & in other compartment place provision for mounting 1 Data / 1 Voice points/1 HDMI (The rate to include cost of sockets) Finish:SS Type | Nos. |  |  |  |  | 0 | 0 | 0 | User Switch Socket Installation | 1 - Legrand Floor Power Box 275×275×60, 1 - Floor EGA Box (300X300) - Steelways, 1 - 6/16A 3 PIN ROUND SOCKET, 1 - 16A 3 PIN ROUND SOCKET, 1 - 1M FACE PLATE, 1 - 2M FACE PLATE, 1 - 3M FACE PLATE, 1 - 4M FACE PLATE
[7 empty] | 0 | 0 | 0
6.4 | Supply & Installation of Floor service box suitable for fixing 2 Set of 4 x6/16A round socket controlled by 16A switch in one compartment & in other compartment place provision for mounting 1 Data / 1 Voice points/1 HDMI (The rate to include cost of sockets) Finish:SS Type | Nos. |  |  |  |  | 0 | 0 | 0 | User Switch Socket Installation | 1 - Legrand Floor Power Box 275×275×60, 1 - Floor EGA Box (300X300) - Steelways, 1 - 6/16A 3 PIN ROUND SOCKET, 1 - 16A 3 PIN ROUND SOCKET, 1 - 1M FACE PLATE, 1 - 2M FACE PLATE, 1 - 3M FACE PLATE, 1 - 4M FACE PLATE
[7 empty] | 0 | 0 | 0
6.41 | Supply & Installation of Flip flop box with 2x6/16A round pin socket controlled by 16A switch +2 data Ports + 1 HDMI ( 10 Module Box) for Board rooms . (The rate to include cost of sockets) Finish:SS Type | Nos. |  |  |  |  | 0 | 0 | 0 | User Switch Socket Installation | 1 - Legrand Floor Power Box 275×275×60, 1 - Floor EGA Box (300X300) - Steelways, 1 - 6/16A 3 PIN ROUND SOCKET, 1 - 16A 3 PIN ROUND SOCKET, 1 - 1M FACE PLATE, 1 - 2M FACE PLATE, 1 - 3M FACE PLATE, 1 - 4M FACE PLATE
[7 empty] | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
VII | CABLE TRAYS & RACEWAYS FOR POWER | [5 empty] | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
| Factory made Standard accessories only to be used for bends, curve, tees etc., | [5 empty] | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
A | Ladder Type Cable Tray : | [5 empty] | 0 | 0 | 0
| Supply and Erection of Heavy duty GI ladder type 2mm thick hot dipped galvanized by 610gms/sqm (87 microns) in line with IS: 4759. The tray and accessories includes cleat angle, rungs, side runner, coupler plate, Elbows, Bends, Tees and Reducers and Hardware .The fixing of cable trays include necessary ceiling suspended / wall mounted supports fixed in ceiling with Fabricated Ms Angle supports,Ms C channel,Base plate etc, The rate shall include bends, angles, Ts, HITECH ROD and all accessories complete Supports Shall be provided at every 1200mm. The cost of supports to be included. Supports must be welded to a square true ceiling base plate with arc welding, the base plate must be fixed to the true ceiling with 04 nos. of HILTI anchor fasteners. The cost of 2runs of 25x3mm GI Strip to be included in the cost of the cable tray. Supports must be made out of MS L angle type for cable tray width of 450mm and above. For Less than 450mm width tray support with hi-tech threaded rods & anchor fasteners. | [5 empty] | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
7.1 | 1200 x 100 mm Size | Mts. |  |  |  |  | 0 | 0 | 0 | Ceiling Raceway & Cable Tray Work | 1 - GI LADDER TYPE CABLE TRAY 450 X 50MM
[7 empty] | 0 | 0 | 0
7.2 | 1000 x 100 mm Size | Mts. |  |  |  |  | 0 | 0 | 0 | Ceiling Raceway & Cable Tray Work | 1 - GI LADDER TYPE CABLE TRAY 450 X 50MM
[7 empty] | 0 | 0 | 0
7.3 | 750 x 75mm Size | Mts. |  |  |  |  | 0 | 0 | 0 | Ceiling Raceway & Cable Tray Work | 1 - GI LADDER TYPE CABLE TRAY 450 X 50MM
[7 empty] | 0 | 0 | 0
7.4 | 600 x 75mm Size | Mts. |  |  |  |  | 0 | 0 | 0 | Ceiling Raceway & Cable Tray Work | 1 - GI LADDER TYPE CABLE TRAY 450 X 50MM
[7 empty] | 0 | 0 | 0
7.5 | 450 x 50mm Size | Mts. | 80 | 80 | 740 | 255 | 59200 | 20400 | 79600 | Ceiling Raceway & Cable Tray Work | 80 - GI LADDER TYPE CABLE TRAY 450 X 50MM
[7 empty] | 0 | 0 | 0
7.6 | 300 x 50mm Size | Mts. |  |  |  |  | 0 | 0 | 0 | Ceiling Raceway & Cable Tray Work | 1 - GI LADDER TYPE CABLE TRAY 300 X 50MM
[7 empty] | 0 | 0 | 0
7.7 | 250 x 50mm Size | Mts. |  |  |  |  | 0 | 0 | 0 | Ceiling Raceway & Cable Tray Work | 1 - GI LADDER TYPE CABLE TRAY 300 X 50MM
[7 empty] | 0 | 0 | 0
7.8 | 200 x 50mm Size | Mts. |  |  |  |  | 0 | 0 | 0 | Ceiling Raceway & Cable Tray Work | 1 - GI LADDER TYPE CABLE TRAY 150 X 50MM
[7 empty] | 0 | 0 | 0
7.9 | 150 x 50mm Size | Mts. |  |  |  |  | 0 | 0 | 0 | Ceiling Raceway & Cable Tray Work | 1 - GI LADDER TYPE CABLE TRAY 150 X 50MM
[7 empty] | 0 | 0 | 0
7.1 | 100 x 50mm Size | Mts. |  |  |  |  | 0 | 0 | 0 | Ceiling Raceway & Cable Tray Work | 1 - GI LADDER TYPE CABLE TRAY 100 X 50MM
[7 empty] | 0 | 0 | 0
B | GI Perforated type cable tray with top cover ( POWER ) | [5 empty] | 0 | 0 | 0
| Supply and installation of following sizes of perforated GI cable trays of 2mm thickness and height as per below description for supporting cables including bends, tees & reducers and including all labour and materials, as per approved drawings, specifications of this tender and directions of Engineer-in-charge. Supports Shall be provided at every 1200mm. The cost of supports to be included. Supports must be welded to a square true ceiling base plate with arc welding, the base plate must be fixed to the true ceiling with 04 nos. of HILTI anchor fasteners. Supports must be made out of MS L angle type for cable tray width of 450mm and above. For Less than 450mm width tray support with hi-tech threaded rods & anchor fasteners. Note: * Factory fabricated bends to be used for all ceiling raceways & trays | [5 empty] | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
7.11 | 1200 x 100 mm Size | Mts. |  |  |  |  | 0 | 0 | 0 | Ceiling Raceway & Cable Tray Work | 1 - GI PERFORATED CABLE TRAY - 600 X 50MM
[7 empty] | 0 | 0 | 0
7.12 | 1000 x 100 mm Size | Mts. |  |  |  |  | 0 | 0 | 0 | Ceiling Raceway & Cable Tray Work | 1 - GI PERFORATED CABLE TRAY - 600 X 50MM
[7 empty] | 0 | 0 | 0
7.13 | 750x 75 mm Size | Mts. |  |  |  |  | 0 | 0 | 0 | Ceiling Raceway & Cable Tray Work | 1 - GI PERFORATED CABLE TRAY - 600 X 50MM
[7 empty] | 0 | 0 | 0
7.14 | 600 x 75mm Size | Mts. |  |  |  |  | 0 | 0 | 0 | Ceiling Raceway & Cable Tray Work | 1 - GI PERFORATED CABLE TRAY - 600 X 50MM
[7 empty] | 0 | 0 | 0
7.15 | 450 x 60mm Size | Mts. |  |  |  |  | 0 | 0 | 0 | Ceiling Raceway & Cable Tray Work | 1 - GI PERFORATED CABLE TRAY - 450 X 50MM
[7 empty] | 0 | 0 | 0
7.16 | 300 x 60mm Size | Mts. | 80 | 80 | 1280 | 165 | 102400 | 13200 | 115600 | Ceiling Raceway & Cable Tray Work | 80 - GI PERFORATED CABLE TRAY - 300 X 50MM
[7 empty] | 0 | 0 | 0
7.17 | 250 x 60mm Size | Mts. | 100 | 100 | 1120 | 135 | 112000 | 13500 | 125500 | Ceiling Raceway & Cable Tray Work | 100 - GI PERFORATED CABLE TRAY - 250 X 50MM
[7 empty] | 0 | 0 | 0
7.18 | 200 x 60mm Size | Mts. | 80 | 80 | 970 | 120 | 77600 | 9600 | 87200 | Ceiling Raceway & Cable Tray Work | 80 - GI PERFORATED CABLE TRAY - 200 X 50MM
[7 empty] | 0 | 0 | 0
7.19 | 150 x 60mm Size | Mts. |  |  |  |  | 0 | 0 | 0 | Ceiling Raceway & Cable Tray Work | 1 - GI PERFORATED CABLE TRAY - 150 X 50MM
[7 empty] | 0 | 0 | 0
7.2 | 100 x 60mm Size | Mts. |  |  |  |  | 0 | 0 | 0 | Ceiling Raceway & Cable Tray Work | 1 - GI PERFORATED CABLE TRAY - 100 X 50MM
[7 empty] | 0 | 0 | 0
7.21 | 80 x 60mm Size | Mts. |  |  |  |  | 0 | 0 | 0 | Ceiling Raceway & Cable Tray Work | 1 - GI PERFORATED CABLE TRAY - 100 X 50MM
[7 empty] | 0 | 0 | 0
C | GI Perforated type cable tray with top cover for (LIGHTING) | [5 empty] | 0 | 0 | 0
| Supply and installation of following sizes of perforated GI cable trays of 2mm thickness and height as per below description for supporting cables including bends, tees & reducers and including all labour and materials, as per approved drawings, specifications of this tender and directions of Engineer-in-charge. Supports Shall be provided at every 1200mm. The cost of supports to be included. Supports must be welded to a square true ceiling base plate with arc welding, the base plate must be fixed to the true ceiling with 04 nos. of HILTI anchor fasteners. Supports must be made out of MS L angle type for cable tray width of 450mm and above. For Less than 450mm width tray support with hi-tech threaded rods & anchor fasteners. Note: * Factory fabricated bends to be used for all ceiling raceways & trays | [5 empty] | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
7.22 | 450 x 60mm Size | Mts. |  |  |  |  | 0 | 0 | 0 | Ceiling Raceway & Cable Tray Work | 1 - GI PERFORATED CABLE TRAY - 450 X 50MM
[7 empty] | 0 | 0 | 0
7.23 | 300 x 60mm Size | Mts. |  |  |  |  | 0 | 0 | 0 | Ceiling Raceway & Cable Tray Work | 1 - GI PERFORATED CABLE TRAY - 300 X 50MM
[7 empty] | 0 | 0 | 0
7.24 | 250 x 60mm Size | Mts. |  |  |  |  | 0 | 0 | 0 | Ceiling Raceway & Cable Tray Work | 1 - GI PERFORATED CABLE TRAY - 250 X 50MM
[7 empty] | 0 | 0 | 0
7.25 | 200 x 60mm Size | Mts. |  |  |  |  | 0 | 0 | 0 | Ceiling Raceway & Cable Tray Work | 1 - GI PERFORATED CABLE TRAY - 200 X 50MM
[7 empty] | 0 | 0 | 0
7.26 | 150 x 60mm Size | Mts. |  |  |  |  | 0 | 0 | 0 | Ceiling Raceway & Cable Tray Work | 1 - GI PERFORATED CABLE TRAY - 150 X 50MM
[7 empty] | 0 | 0 | 0
7.27 | 100 x 60mm Size | Mts. | 85 | 85 | 660 | 90 | 56100 | 7650 | 63750 | Ceiling Raceway & Cable Tray Work | 85 - GI PERFORATED CABLE TRAY - 100 X 50MM
[7 empty] | 0 | 0 | 0
7.28 | 80 x 60mm Size | Mts. |  |  |  |  | 0 | 0 | 0 | Ceiling Raceway & Cable Tray Work | 1 - GI PERFORATED CABLE TRAY - 100 X 50MM
[7 empty] | 0 | 0 | 0
7.29 | 60 x 60mm Size | Mts. | 50 | 50 | 510 | 75 | 25500 | 3750 | 29250 | Ceiling Raceway & Cable Tray Work | 50 - GI PERFORATED CABLE TRAY - 100 X 50MM
[7 empty] | 0 | 0 | 0
D | GI Perforated type cable tray with top cover for (HVAC) | [5 empty] | 0 | 0 | 0
| Supply and installation of following sizes of perforated GI cable trays of 2mm thickness and height as per below description for supporting cables including bends, tees & reducers and including all labour and materials, as per approved drawings, specifications of this tender and directions of Engineer-in-charge. Supports Shall be provided at every 1200mm. The cost of supports to be included. Supports must be welded to a square true ceiling base plate with arc welding, the base plate must be fixed to the true ceiling with 04 nos. of HILTI anchor fasteners. Supports must be made out of MS L angle type for cable tray width of 450mm and above. For Less than 450mm width tray support with hi-tech threaded rods & anchor fasteners. Note: * Factory fabricated bends and accessories to be used for all ceiling raceways & trays | [5 empty] | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
7.3 | 450 x 60mm Size | Mts. |  |  |  |  | 0 | 0 | 0 | Ceiling Raceway & Cable Tray Work | 1 - GI PERFORATED CABLE TRAY - 450 X 50MM
[7 empty] | 0 | 0 | 0
7.31 | 300 x 60mm Size | Mts. |  |  |  |  | 0 | 0 | 0 | Ceiling Raceway & Cable Tray Work | 1 - GI PERFORATED CABLE TRAY - 300 X 50MM
[7 empty] | 0 | 0 | 0
7.32 | 250 x 60mm Size | Mts. |  |  |  |  | 0 | 0 | 0 | Ceiling Raceway & Cable Tray Work | 1 - GI PERFORATED CABLE TRAY - 250 X 50MM
[7 empty] | 0 | 0 | 0
7.33 | 200 x 60mm Size | Mts. | 60 | 60 | 970 | 120 | 58200 | 7200 | 65400 | Ceiling Raceway & Cable Tray Work | 60 - GI PERFORATED CABLE TRAY - 200 X 50MM
[7 empty] | 0 | 0 | 0
7.34 | 150 x 150mm Size | Mts. |  |  |  |  | 0 | 0 | 0 | Ceiling Raceway & Cable Tray Work | 1 - GI PERFORATED CABLE TRAY - 150 X 50MM
[7 empty] | 0 | 0 | 0
7.35 | 100 x 150mm Size | Mts. |  |  |  |  | 0 | 0 | 0 | Ceiling Raceway & Cable Tray Work | 1 - GI PERFORATED CABLE TRAY - 100 X 50MM
[7 empty] | 0 | 0 | 0
7.36 | 80 x 60mm Size | Mts. |  |  |  |  | 0 | 0 | 0 | Ceiling Raceway & Cable Tray Work | 1 - GI PERFORATED CABLE TRAY - 100 X 50MM
[7 empty] | 0 | 0 | 0
7.37 | 50 x 50mm Size | Mts. |  |  |  |  | 0 | 0 | 0 | Ceiling Raceway & Cable Tray Work | 1 - GI PERFORATED CABLE TRAY - 100 X 50MM
[7 empty] | 0 | 0 | 0
D | Raceways | [5 empty] | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
| Supply & Installation of following size GI raceway / wire way with cover, made out of 16 SWG GI for body and 14 SWG GI for cover. Junction boxes to be provided with enough supports inside the box. Raceway installed above false ceiling/floor shall include necessary mounting supports, junction boxes and accessories to fix it firmly to the ground/ ceiling. The rate quote shall include providing earthing for the Wireway trunking. All edges, cut faces shall be free of burrs & shall be smooth. The channels shall be earthed at the boxes and at the joints with 4sq.mm copper Wire with end terminations screws so that earth is continuous. Jointing of the race ways to be done with welding. Colour code should be followed for cover as per project incharge. The costing shall include chipping works, disposal of debris, Proper cleaning & Packing of junction boxes/Raceways & filling the Cement concrete with chicken mesh, making it for floor finishing level as per site Incharge. Note: * Factory fabricated bends and accessories to be used for all ceiling raceways & trays | [5 empty] | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
1 | Floor raceways with respective Junction Box (For Power & Network) | [5 empty] | 0 | 0 | 0 | Floor Raceway & Cable Tray Work | 1 - GI RACEWAY - 300 X 40 X 1.2 MM with Cover 2MM, 1 - GI RACEWAY - 250 X 40 X 1.2 MM with Cover 2MM, 1 - GI RACEWAY - 200 X 40 X 1.2 MM with Cover 2MM, 1 - GI HOT DIP GALVANIZED RACEWAY - 300 X 40 X 2MM, 1 - GI HOT DIP GALVANIZED RACEWAY - 250 X 40 X 2MM, 1 - Electro Galvanized Hardware M8X20MM (1 Nut, 1 - 1 Hex Bolt, 1 - 2 Washer)
[7 empty] | 0 | 0 | 0
7.38 | 450 x 40mm Size | Mts. |  |  |  |  | 0 | 0 | 0 | Floor Raceway & Cable Tray Work | 1 - GI RACEWAY - 300 X 40 X 1.2 MM with Cover 2MM
7.39 | 460 x 460 x 50mm Size | Nos. |  |  |  |  | 0 | 0 | 0 | Floor Raceway & Cable Tray Work | 1 - GI JUNCTION BOX - 475 X 50MM
[7 empty] | 0 | 0 | 0
7.4 | 300 x 40mm Size | Mts. | 25 | 25 | 1160 | 165 | 29000 | 4125 | 33125 | Floor Raceway & Cable Tray Work | 25 - GI RACEWAY - 300 X 40 X 1.2 MM with Cover 2MM
7.41 | 310 x 310 x 50mm Size | Nos. | 8 | 8 | 890 | 190 | 7120 | 1520 | 8640 | Floor Raceway & Cable Tray Work | 8 - GI JUNCTION BOX - 325 X 50MM
[7 empty] | 0 | 0 | 0
7.42 | 250 x 40mm Size | Mts. | 75 | 75 | 1010 | 135 | 75750 | 10125 | 85875 | Floor Raceway & Cable Tray Work | 75 - GI RACEWAY - 250 X 40 X 1.2 MM with Cover 2MM
7.43 | 260 x 260 x 50mm Size | Nos. | 10 | 10 | 580 | 120 | 5800 | 1200 | 7000 | Floor Raceway & Cable Tray Work | 10 - GI JUNCTION BOX - 275 X 50MM
[7 empty] | 0 | 0 | 0
7.44 | 200 x 40mm Size | Mts. | 80 | 80 | 850 | 120 | 68000 | 9600 | 77600 | Floor Raceway & Cable Tray Work | 80 - GI RACEWAY - 200 X 40 X 1.2 MM with Cover 2MM
7.45 | 210 x 210 x 50mm Size | Nos. | 16 | 16 | 520 | 110 | 8320 | 1760 | 10080 | Floor Raceway & Cable Tray Work | 16 - GI JUNCTION BOX - 225 X 50MM
[7 empty] | 0 | 0 | 0
7.46 | 150 x 40mm Size | Mts. |  |  |  |  | 0 | 0 | 0 | Floor Raceway & Cable Tray Work | 1 - GI RACEWAY - 150 X 40 X 1.2 MM with Cover 1.6MM
7.47 | 160 x 160 x 50mm Size | Nos. |  |  |  |  | 0 | 0 | 0 | Floor Raceway & Cable Tray Work | 1 - GI JUNCTION BOX - 175 X 50MM
[7 empty] | 0 | 0 | 0
7.48 | 100 x 40mm Size | Mts. | 55 | 55 | 530 | 90 | 29150 | 4950 | 34100 | Floor Raceway & Cable Tray Work | 55 - GI RACEWAY - 100 X 40 X 1.2 MM with Cover 1.6MM
7.49 | 110 x 110 x 50mm Size | Nos. | 16 | 16 | 350 | 70 | 5600 | 1120 | 6720 | Floor Raceway & Cable Tray Work | 16 - GI JUNCTION BOX - 125 X 50MM
[7 empty] | 0 | 0 | 0
7.5 | 80 x 40mm Size | Mts. |  |  |  |  | 0 | 0 | 0 | Floor Raceway & Cable Tray Work | 1 - GI RACEWAY - 100 X 40 X 1.2 MM with Cover 1.6MM
7.51 | 90 x 90 x 50mm Size | Nos. |  |  |  |  | 0 | 0 | 0 | Floor Raceway & Cable Tray Work | 1 - GI JUNCTION BOX - 125 X 50MM
[7 empty] | 0 | 0 | 0
1 | Floor raceways with respective Junction Box(In False floor area) | [5 empty] | 0 | 0 | 0 | Floor Raceway & Cable Tray Work | 1 - GI RACEWAY - 300 X 40 X 1.2 MM with Cover 2MM, 1 - GI RACEWAY - 250 X 40 X 1.2 MM with Cover 2MM, 1 - GI RACEWAY - 200 X 40 X 1.2 MM with Cover 2MM, 1 - GI HOT DIP GALVANIZED RACEWAY - 300 X 40 X 2MM, 1 - GI HOT DIP GALVANIZED RACEWAY - 250 X 40 X 2MM, 1 - Electro Galvanized Hardware M8X20MM (1 Nut, 1 - 1 Hex Bolt, 1 - 2 Washer)
[7 empty] | 0 | 0 | 0
7.49 | 450 x 40mm Size | Mts. |  |  |  |  | 0 | 0 | 0 | Floor Raceway & Cable Tray Work | 1 - GI RACEWAY - 300 X 40 X 1.2 MM with Cover 2MM
7.5 | 460 x 460 x 50mm Size | Nos. |  |  |  |  | 0 | 0 | 0 | Floor Raceway & Cable Tray Work | 1 - GI JUNCTION BOX - 475 X 50MM
[7 empty] | 0 | 0 | 0
7.51 | 300 x 40mm Size | Mts. |  |  |  |  | 0 | 0 | 0 | Floor Raceway & Cable Tray Work | 1 - GI RACEWAY - 300 X 40 X 1.2 MM with Cover 2MM
7.52 | 310 x 310 x 50mm Size | Nos. |  |  |  |  | 0 | 0 | 0 | Floor Raceway & Cable Tray Work | 1 - GI JUNCTION BOX - 325 X 50MM
[7 empty] | 0 | 0 | 0
7.53 | 250 x 40mm Size | Mts. |  |  |  |  | 0 | 0 | 0 | Floor Raceway & Cable Tray Work | 1 - GI RACEWAY - 250 X 40 X 1.2 MM with Cover 2MM
7.54 | 260 x 260 x 50mm Size | Nos. |  |  |  |  | 0 | 0 | 0 | Floor Raceway & Cable Tray Work | 1 - GI JUNCTION BOX - 275 X 50MM
[7 empty] | 0 | 0 | 0
7.55 | 200 x 40mm Size | Mts. |  |  |  |  | 0 | 0 | 0 | Floor Raceway & Cable Tray Work | 1 - GI RACEWAY - 200 X 40 X 1.2 MM with Cover 2MM
7.56 | 210 x 210 x 50mm Size | Nos. |  |  |  |  | 0 | 0 | 0 | Floor Raceway & Cable Tray Work | 1 - GI JUNCTION BOX - 225 X 50MM
[7 empty] | 0 | 0 | 0
7.57 | 150 x 40mm Size | Mts. |  |  |  |  | 0 | 0 | 0 | Floor Raceway & Cable Tray Work | 1 - GI RACEWAY - 150 X 40 X 1.2 MM with Cover 1.6MM
7.58 | 160 x 160 x 50mm Size | Nos. |  |  |  |  | 0 | 0 | 0 | Floor Raceway & Cable Tray Work | 1 - GI JUNCTION BOX - 175 X 50MM
[7 empty] | 0 | 0 | 0
7.59 | 100 x 40mm Size | Mts. | 60 | 60 | 530 | 90 | 31800 | 5400 | 37200 | Floor Raceway & Cable Tray Work | 60 - GI RACEWAY - 100 X 40 X 1.2 MM with Cover 1.6MM
7.6 | 110 x 110 x 50mm Size | Nos. | 8 | 8 | 350 | 70 | 2800 | 560 | 3360 | Floor Raceway & Cable Tray Work | 8 - GI JUNCTION BOX - 125 X 50MM
[7 empty] | 0 | 0 | 0
7.61 | 80 x 40mm Size | Mts. |  |  |  |  | 0 | 0 | 0 | Floor Raceway & Cable Tray Work | 1 - GI RACEWAY - 100 X 40 X 1.2 MM with Cover 1.6MM
7.62 | 90 x 90 x 50mm Size | Nos. |  |  |  |  | 0 | 0 | 0 | Floor Raceway & Cable Tray Work | 1 - GI JUNCTION BOX - 125 X 50MM
[7 empty] | 0 | 0 | 0
F | Ceiling Raceways | [5 empty] | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
7.63 | 600 x 60mm Size | Mts. |  |  |  |  | 0 | 0 | 0 | Ceiling Raceway & Cable Tray Work | 1 - GI CEILING RACEWAY - 300 X 75 X 1MM
7.64 | 610 x 610 x 60mm Size | Nos. |  |  |  |  | 0 | 0 | 0 | Ceiling Raceway & Cable Tray Work | 1 - GI JUNCTION BOX - 475 X 50MM
[7 empty] | 0 | 0 | 0
7.65 | 450 x 60mm Size | Mts. |  |  |  |  | 0 | 0 | 0 | Ceiling Raceway & Cable Tray Work | 1 - GI CEILING RACEWAY - 300 X 75 X 1MM
7.66 | 460 x 460 x 60mm Size | Nos. |  |  |  |  | 0 | 0 | 0 | Ceiling Raceway & Cable Tray Work | 1 - GI JUNCTION BOX - 475 X 50MM
[7 empty] | 0 | 0 | 0
7.67 | 300 x 60mm Size | Mts. |  |  |  |  | 0 | 0 | 0 | Ceiling Raceway & Cable Tray Work | 1 - GI CEILING RACEWAY - 300 X 75 X 1MM
7.68 | 310 x 310 x 60mm Size | Nos. |  |  |  |  | 0 | 0 | 0 | Ceiling Raceway & Cable Tray Work | 1 - GI JUNCTION BOX - 325 X 50MM
[7 empty] | 0 | 0 | 0
7.69 | 250 x 60mm Size | Mts. |  |  |  |  | 0 | 0 | 0 | Ceiling Raceway & Cable Tray Work | 1 - GI CEILING RACEWAY - 250 X 75 X 1MM
7.7 | 260 x 260 x 60mm Size | Nos. |  |  |  |  | 0 | 0 | 0 | Ceiling Raceway & Cable Tray Work | 1 - GI JUNCTION BOX - 275 X 50MM
[7 empty] | 0 | 0 | 0
7.71 | 200 x 60mm Size | Mts. |  |  |  |  | 0 | 0 | 0 | Ceiling Raceway & Cable Tray Work | 1 - GI CEILING RACEWAY - 200 X 75 X 1MM
7.72 | 210 x 210 x 60mm Size | Nos. |  |  |  |  | 0 | 0 | 0 | Ceiling Raceway & Cable Tray Work | 1 - GI JUNCTION BOX - 225 X 50MM
[7 empty] | 0 | 0 | 0
7.73 | 150 x 60mm Size | Mts. |  |  |  |  | 0 | 0 | 0 | Ceiling Raceway & Cable Tray Work | 1 - GI CEILING RACEWAY - 150 X 75 X 1MM
7.74 | 160 x 160 x 60mm Size | Nos. |  |  |  |  | 0 | 0 | 0 | Ceiling Raceway & Cable Tray Work | 1 - GI JUNCTION BOX - 175 X 50MM
[7 empty] | 0 | 0 | 0
7.75 | 100 x 60mm Size | Mts. |  |  |  |  | 0 | 0 | 0 | Ceiling Raceway & Cable Tray Work | 1 - GI CEILING RACEWAY - 100 X 75 X 1MM
7.76 | 110 x 110 x 60mm Size | Nos. |  |  |  |  | 0 | 0 | 0 | Ceiling Raceway & Cable Tray Work | 1 - GI JUNCTION BOX - 125 X 50MM
[7 empty] | 0 | 0 | 0
7.77 | 80 x 60mm Size | Mts. |  |  |  |  | 0 | 0 | 0 | Ceiling Raceway & Cable Tray Work | 1 - GI CEILING RACEWAY - 100 X 75 X 1MM
7.78 | 90 x 90 x 60mm Size | Nos. |  |  |  |  | 0 | 0 | 0 | Ceiling Raceway & Cable Tray Work | 1 - GI JUNCTION BOX - 75 X 75MM
[7 empty] | 0 | 0 | 0
F | Supply & Laying of following size 2mm thick rigid FRLS PVC conduits & accessories fixing in ceiling | [5 empty] | 0 | 0 | 0
7.79 | 32mm dia | Mts. |  |  |  |  | 0 | 0 | 0 | Ceiling Conduit Work | 1 - MS CONDUIT - 32 MM, 1 - PVC CONDUIT - 32 MM, 1 - PVC FLEXIBLE CONDUIT - 32 MM, 1 - GI SADDLE WITHOUT BASE - 32MM, 1 - MS Collar - 32MM, 1 - Check Nut 32MM for Conduit
[7 empty] | 0 | 0 | 0
7.8 | 25mm dia | Mts. | 120 | 120 | 60 | 20 | 7200 | 2400 | 9600 | Ceiling Conduit Work | 120 - MS CONDUIT - 25 MM, 120 - PVC CONDUIT - 25MM, 120 - GI FLEXIBLE CONDUIT - 25MM, 120 - GI Flexible Conduit Adapter - 25MM, 120 - GI SADDLE WITHOUT BASE - 25MM
[7 empty] | 0 | 0 | 0
7.81 | 20mm dia | Mts. |  |  |  |  | 0 | 0 | 0 | Ceiling Conduit Work | 1 - PVC CONDUIT - 19 MM, 1 - PVC BEND - 19 MM, 1 - PVC LONG BEND - 19 MM, 1 - PVC FLEXIBLE CONDUIT ADAPTOR - 19MM
[7 empty] | 0 | 0 | 0
G | Supply & Laying of following size 2mm thick rigid FRLS PVC conduits & accessories fixing in wall/ floor/false floor | [5 empty] | 0 | 0 | 0
7.82 | 32mm dia | Mts. |  |  |  |  | 0 | 0 | 0 | Wall Conduit Work | 1 - MS CONDUIT - 32 MM, 1 - PVC CONDUIT - 32 MM, 1 - PVC BEND - 32 MM, 1 - MS INSPECTION BEND - 32 MM, 1 - GI BOX - 3 Module, 1 - GI BOX - 4 Module, 1 - MS JUNCTION BOX 4 WAY - 25 MM
[7 empty] | 0 | 0 | 0
7.83 | 25mm dia | Mts. | 50 | 50 | 60 | 20 | 3000 | 1000 | 4000 | Wall Conduit Work | 50 - MS CONDUIT - 25 MM, 50 - PVC CONDUIT - 25MM, 50 - PVC COLLAR - 25MM, 50 - GI BOX - 2 Module, 50 - GI BOX - 3 Module, 50 - MS JUNCTION BOX 4 WAY - 25 MM
[7 empty] | 0 | 0 | 0
7.84 | 20mm dia | Mts. |  |  |  |  | 0 | 0 | 0 | Wall Conduit Work | 1 - PVC CONDUIT - 19 MM, 1 - PVC BEND - 19 MM, 1 - GI BOX - 2 Module, 1 - PVC JUNCTION BOX 4 WAY - 19 MM, 1 - PVC JUNCTION BOX 2 WAY - 19 MM
[7 empty] | 0 | 0 | 0
F | Supply & Laying of following size 1.6mm thick rigid MS conduits & accessories fixing in ceiling | [5 empty] | 0 | 0 | 0
7.85 | 32mm dia | Mts. |  |  |  |  | 0 | 0 | 0 | Ceiling Conduit Work | 1 - MS CONDUIT - 32 MM, 1 - PVC CONDUIT - 32 MM, 1 - PVC FLEXIBLE CONDUIT - 32 MM, 1 - GI SADDLE WITHOUT BASE - 32MM, 1 - MS Collar - 32MM, 1 - Check Nut 32MM for Conduit
[7 empty] | 0 | 0 | 0
7.86 | 25mm dia | Mts. |  |  |  |  | 0 | 0 | 0 | Ceiling Conduit Work | 1 - MS CONDUIT - 25 MM, 1 - PVC CONDUIT - 25MM, 1 - GI FLEXIBLE CONDUIT - 25MM, 1 - GI Flexible Conduit Adapter - 25MM, 1 - GI SADDLE WITHOUT BASE - 25MM
[7 empty] | 0 | 0 | 0
7.87 | 20mm dia | Mts. |  |  |  |  | 0 | 0 | 0 | Ceiling Conduit Work | 1 - PVC CONDUIT - 19 MM, 1 - PVC BEND - 19 MM, 1 - PVC LONG BEND - 19 MM, 1 - PVC FLEXIBLE CONDUIT ADAPTOR - 19MM
[7 empty] | 0 | 0 | 0
G | Supply & Laying of following size 1.6mm thick rigid MS conduits & accessories fixing in wall/ floor/false floor | [5 empty] | 0 | 0 | 0
7.88 | 32mm dia | Mts. |  |  |  |  | 0 | 0 | 0 | Wall Conduit Work | 1 - MS CONDUIT - 32 MM, 1 - PVC CONDUIT - 32 MM, 1 - PVC BEND - 32 MM, 1 - MS INSPECTION BEND - 32 MM, 1 - GI BOX - 3 Module, 1 - GI BOX - 4 Module, 1 - MS JUNCTION BOX 4 WAY - 25 MM
[7 empty] | 0 | 0 | 0
7.89 | 25mm dia | Mts. |  |  |  |  | 0 | 0 | 0 | Wall Conduit Work | 1 - MS CONDUIT - 25 MM, 1 - PVC CONDUIT - 25MM, 1 - PVC COLLAR - 25MM, 1 - GI BOX - 2 Module, 1 - GI BOX - 3 Module, 1 - MS JUNCTION BOX 4 WAY - 25 MM
[7 empty] | 0 | 0 | 0
7.9 | 20mm dia | Mts. |  |  |  |  | 0 | 0 | 0 | Wall Conduit Work | 1 - PVC CONDUIT - 19 MM, 1 - PVC BEND - 19 MM, 1 - GI BOX - 2 Module, 1 - PVC JUNCTION BOX 4 WAY - 19 MM, 1 - PVC JUNCTION BOX 2 WAY - 19 MM
[7 empty] | 0 | 0 | 0
F | Supply & Laying of following size 1.6mm thick rigid GI conduits & accessories fixing in ceiling | [5 empty] | 0 | 0 | 0
7.91 | 32mm dia | Mts. |  |  |  |  | 0 | 0 | 0 | Ceiling Conduit Work | 1 - MS CONDUIT - 32 MM, 1 - PVC CONDUIT - 32 MM, 1 - PVC FLEXIBLE CONDUIT - 32 MM, 1 - GI SADDLE WITHOUT BASE - 32MM, 1 - MS Collar - 32MM, 1 - Check Nut 32MM for Conduit
[7 empty] | 0 | 0 | 0
7.92 | 25mm dia | Mts. |  |  |  |  | 0 | 0 | 0 | Ceiling Conduit Work | 1 - MS CONDUIT - 25 MM, 1 - PVC CONDUIT - 25MM, 1 - GI FLEXIBLE CONDUIT - 25MM, 1 - GI Flexible Conduit Adapter - 25MM, 1 - GI SADDLE WITHOUT BASE - 25MM
[7 empty] | 0 | 0 | 0
7.93 | 20mm dia | Mts. |  |  |  |  | 0 | 0 | 0 | Ceiling Conduit Work | 1 - PVC CONDUIT - 19 MM, 1 - PVC BEND - 19 MM, 1 - PVC LONG BEND - 19 MM, 1 - PVC FLEXIBLE CONDUIT ADAPTOR - 19MM
[7 empty] | 0 | 0 | 0
G | Supply & Laying of following size 1.6mm thick rigid FRLS GI conduits & accessories fixing in wall/ floor/false floor | [5 empty] | 0 | 0 | 0
7.94 | 32mm dia | Mts. |  |  |  |  | 0 | 0 | 0 | Wall Conduit Work | 1 - MS CONDUIT - 32 MM, 1 - PVC CONDUIT - 32 MM, 1 - PVC BEND - 32 MM, 1 - MS INSPECTION BEND - 32 MM, 1 - GI BOX - 3 Module, 1 - GI BOX - 4 Module, 1 - MS JUNCTION BOX 4 WAY - 25 MM
[7 empty] | 0 | 0 | 0
7.95 | 25mm dia | Mts. |  |  |  |  | 0 | 0 | 0 | Wall Conduit Work | 1 - MS CONDUIT - 25 MM, 1 - PVC CONDUIT - 25MM, 1 - PVC COLLAR - 25MM, 1 - GI BOX - 2 Module, 1 - GI BOX - 3 Module, 1 - MS JUNCTION BOX 4 WAY - 25 MM
[7 empty] | 0 | 0 | 0
7.96 | 20mm dia | Mts. |  |  |  |  | 0 | 0 | 0 | Wall Conduit Work | 1 - PVC CONDUIT - 19 MM, 1 - PVC BEND - 19 MM, 1 - GI BOX - 2 Module, 1 - PVC JUNCTION BOX 4 WAY - 19 MM, 1 - PVC JUNCTION BOX 2 WAY - 19 MM
[7 empty] | 0 | 0 | 0
H | Supply & Installation of following size Powder coated raceway / wire way with cover, made out of 2mm thick steel sheet factory fabricated post galvanized raceways to be laid in the ceiling / Floor for Server/ HUB room area with cutouts for installation of MCB and Industrial socket outlets. The rate to include providing 2 mm thick GI cover fixing accessories, Earthing with 8SWG copper wire, complete with necessary supports, bends, access boxes, Tap off boxes & Cross over as per specification and site requirement. The shade shall be as per site approval.Colour code should be followed for as per project incharge. | [5 empty] | 0 | 0 | 0
| Supply & Installation of following size Powder coated junction boxes , made out of 16 SWG GI/MS for body and 14 SWG GI/MS for cover. - The shade shall be as per site approval.Colour code should be followed for cover as per project incharge. | [5 empty] | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
7.97 | 200 x 200mm Size | Mts. |  |  |  |  | 0 | 0 | 0 | Wall Conduit Work | 1 - GI RACEWAY - 200 X 40 X 1.2 MM with Cover 2MM
7.98 | 210 x 210 x 200mm Size | Nos. |  |  |  |  | 0 | 0 | 0 | Wall Conduit Work | 1 - GI JUNCTION BOX - 225 X 50MM
[7 empty] | 0 | 0 | 0
7.99 | 150 x 100mm Size | Mts. |  |  |  |  | 0 | 0 | 0 | Wall Conduit Work | 1 - GI RACEWAY - 150 X 40 X 1.2 MM with Cover 1.6MM
7.1 | 160 x 160 x 100mm Size | Nos. |  |  |  |  | 0 | 0 | 0 | Wall Conduit Work | 1 - GI JUNCTION BOX - 175 X 50MM
[7 empty] | 0 | 0 | 0
7.101 | 100 x100mm Size | Mts. |  |  |  |  | 0 | 0 | 0 | Wall Conduit Work | 1 - GI RACEWAY - 100 X 40 X 1.2 MM with Cover 1.6MM
7.102 | 110 x 110 x 100mm Size | Nos. |  |  |  |  | 0 | 0 | 0 | Wall Conduit Work | 1 - GI JUNCTION BOX - 125 X 50MM
[7 empty] | 0 | 0 | 0
7.103 | Supply and installation of 450mm X 100mm Electroinc type SS Basket type cable tray/Cablofil type and include all necessary supporting rods, C channel complete as required at distance of 1200mm. | Mts. | 20 | 20 | 2900 | 280 | 58000 | 5600 | 63600 | Wall Conduit Work | 20 - SS Junction Box Cover Plate 250 X 250 X 2MM
[7 empty] | 0 | 0 | 0
7.104 | Supply and installation of 300mm X 100mm Electroinc type Basket type cable tray/Cablofil type and include all necessary supporting rods, C channel complete as required at distance of 1200mm. | Mts. |  |  |  |  | 0 | 0 | 0 | Wall Conduit Work | 1 - SS Junction Box Cover Plate 250 X 250 X 2MM
[7 empty] | 0 | 0 | 0
VIII | EARTHING | [5 empty] | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
A | Supplier shall provide installation methodology for the installation of earth electrodes | [5 empty] | 0 | 0 | 0
| Supplier shall be present during the installation of earth electrode | [5 empty] | 0 | 0 | 0
| All the testing at site shall be conducted in presence of consultants | [5 empty] | 0 | 0 | 0
| Rate shall include all civil works including construction of chamber with PCC cover alongwith Name plate details as per the requirement. Costing shall include soil test report & additional equipments if any to achieve the desired value as mentioned in technical specification | [5 empty] | 0 | 0 | 0
8.1 | Body Earthing: 'Supply, installation, testing & commissioning of MAINTENANCEFREE earthing system with Earthing Electrode dual pipe consist of 3mtr long 47 mm dia outer pipe, 25 mm dia inner pipe, Terminal flat of 30 x 10/ 12 x 12mm, the entire construction processed with Hot Dip Galvanization, outer surface upto 100 microns, and all inner surface 300 microns, all inner annular space filled with highly conductive and non-corrosive nature crystalline material, along with electrode Moisture Booster compound of 2 x 25 Kg bags to fill surround the pipe at the time of installation. (Moisture Booster having its property of moisture retention, conduction and non-corrosive nature). Also include 300mm x 300mm heavy duty GI frame and heavy duty RCC Pre cast cover, 150mm brick masonry chamber etc., complete | Nos. | 4 | 4 | 18500 | 4000 | 74000 | 16000 | 90000 | Earthing Works | 4 - EARTHING ELECTRODE GI - 3 Mtr, 4 - EARTHING ELECTRODE CU - 3 Mtr, 4 - EARTHING ELECTRODE CU - 1 Mtr, 4 - EARTHING CHEMICAL BAG, 4 - Earth Electrode Connector, 4 - Earth Chamber Cover 160 x 160 MM
[7 empty] | 0 | 0 | 0
8.2 | Neutral Earthing: 'Supply, installation, testing & commissioning of MAINTENANCEFREE earthing system with Earthing Electrode dual pipe consist of 3mtr long 77 mm dia outer pipe, 47 mm dia inner pipe, Terminal flat of 38 x 10 mm, the entire construction processed with Hot Dip Galvanization, outer surface upto 100 microns and all inner surface Upto 300 microns, all inner annular space filled with highly conductive and non-corrosive nature crystalline material, along with electrode Moisture Booster compound of 2 x 25 kg bags to fill surround the pipe at the time of installation. (Moisture Booster having its property of moisture retention, conduction and non – corrosive nature) .Also include 300mm x 300mm heavy duty GI frame and heavy duty RCC Pre cast cover, 150mm brick masonry chamber etc., complete. | Nos. | 2 | 2 | 20000 | 4000 | 40000 | 8000 | 48000 | Earthing Works | 2 - EARTHING ELECTRODE GI - 3 Mtr, 2 - EARTHING ELECTRODE CU - 3 Mtr, 2 - EARTHING ELECTRODE CU - 1 Mtr, 2 - EARTHING CHEMICAL BAG, 2 - Earth Electrode Connector, 2 - Earth Chamber Cover 160 x 160 MM
[7 empty] | 0 | 0 | 0
B | EARTH STRIPS | [5 empty] | 0 | 0 | 0
| GI/Cu earth strips on cable tray or below ground as per site condition. All Cu. Strips shall be run in pvc heat shrinkable sleeve & mounted on insulation mounts. Cost of civil works shall be included for strips laid below ground. Including connection/ terminating with nut, bolt, spring, washer etc. as required. Jointing shall be done by overlapping and with 2 sets of brass nut bolt & spring washer spaced at 50mm. Joints to be welded for GI and brazing for copper strips. | [5 empty] | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
8.3 | 8 SWG GI Wire | Mts. | 300 | 300 | 60 | 20 | 18000 | 6000 | 24000 | Earthing Works | 300 - GI WIRE - 8 SWG
[7 empty] | 0 | 0 | 0
8.4 | 25 x 3mm GI Earth flat | Mts. | 100 | 100 | 125 | 35 | 12500 | 3500 | 16000 | Earthing Works | 100 - GI STRIP - 25MM X 3MM
[7 empty] | 0 | 0 | 0
8.5 | 25 x 6mm GI Earth flat | Mts. |  |  |  |  | 0 | 0 | 0 | Earthing Works | 1 - GI STRIP - 25MM X 6MM
[7 empty] | 0 | 0 | 0
8.6 | 50 x 6mm GI Earth flat | Mts. | 150 | 150 | 330 | 55 | 49500 | 8250 | 57750 | Earthing Works | 150 - GI STRIP - 40MM X 6MM
[7 empty] | 0 | 0 | 0
8.7 | 75 x 10mm GI Earth flat | Mts. |  |  |  |  | 0 | 0 | 0 | Earthing Works | 1 - GI STRIP - 40MM X 6MM
[7 empty] | 0 | 0 | 0
8.8 | Busbar of 0.5 Mtr length made out of 50 x 6 mm GI strip with drill holes of M8 at 25mm interval mounted on insulators with glass covered box & Naming to be done as per the Requirement. Detailed drawings attached in earthing schematic & construction of earth box to be made as per schematic | Nos. | 3 | 3 | 3400 | 500 | 10200 | 1500 | 11700 | Earthing Works | 3 - Earth Bus Bar - GI (0.5 MTR), 3 - Earth Distribution Box - GI (25MM X 6MM)
[7 empty] | 0 | 0 | 0
8.9 | Busbar of 0.5 Mtr length made out of 75 x10 mm GI strip with drill holes of M8 at 25mm interval mounted on insulators with glass covered box & Naming to be done as per the Requirement.Detailed drawings attached in earthing schematic & construction of earth box to be made as per schematic. | Nos. |  |  |  |  | 0 | 0 | 0 | Earthing Works | 1 - Earth Bus Bar - GI (0.5 MTR), 1 - Earth Distribution Box - GI (25MM X 6MM)
[7 empty] | 0 | 0 | 0
8.1 | Busbar of 0.5 Mtr length made out of 100 x10 mm GI strip with drill holes of M8 at 25mm interval mounted on insulators with glass covered box & Naming to be done as per the Requirement.Detailed drawings attached in earthing schematic & construction of earth box to be made as per schematic | Nos. |  |  |  |  | 0 | 0 | 0 | Earthing Works | 1 - Earth Bus Bar - GI (0.5 MTR), 1 - Earth Distribution Box - GI (25MM X 6MM)
[7 empty] | 0 | 0 | 0
8.11 | 8 SWG Cu Wire | Mts. |  |  |  |  | 0 | 0 | 0 | Earthing Works | 1 - COPPER WIRE - 8 SWG
[7 empty] | 0 | 0 | 0
8.12 | 25 x 3mm Cu. Earth flat | Mts. |  |  |  |  | 0 | 0 | 0 | Earthing Works | 1 - Earth Distribution Box - Copper (25MM X 6MM)
[7 empty] | 0 | 0 | 0
8.13 | 25 x 6mm Cu. Earth flat | Mts. |  |  |  |  | 0 | 0 | 0 | Earthing Works | 1 - Earth Distribution Box - Copper (25MM X 6MM)
[7 empty] | 0 | 0 | 0
8.14 | 50 x 6mm Cu. Earth flat | Mts. |  |  |  |  | 0 | 0 | 0 | Earthing Works | 1 - Earth Distribution Box - Copper (75MM X 6MM)
[7 empty] | 0 | 0 | 0
8.15 | 75 x 10mm Cu. Earth flat | Mts. |  |  |  |  | 0 | 0 | 0 | Earthing Works
[7 empty] | 0 | 0 | 0
C | PVC Insulated Copper Conductor Unarmoured Cables (YY Type) - IS 694 | [5 empty] | 0 | 0 | 0
| Supply, Laying, Testing and Commissioning of 1.1kV grade, copper conductor, PVC insulated, unarmoured, power cables as per IS - 694. The cables shall be laid on tray / hume pipe /in ready made trenches, with nylon cable ties / MS Clamps @ 600mm interval etc., as required. The cost of the nylon tie shall be included in the cost of installation. Rate quoted shall exclude cost of tray / hume pipe | [5 empty] | 0 | 0 | 0
| Cable identification labels at both ends clearly mentioning the cable specs & also at appropriate intervals along the cable route should be provided. The labels shall be engraved / anodized aluminium with white letters on black background. The cost of the Cable identification labels shall be included in the cost of installation. | [5 empty] | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
8.16 | 1 Core x 300 Sq. mm | Mts. |  |  |  |  | 0 | 0 | 0 | Earthing Works | 1 - LUGS / THIMBLE 25 SQMM PIN TYPE - COPPER, 1 - LUGS / THIMBLE 50 SQMM RING TYPE - COPPER, 1 - Heat Shrink Sleeve - 25 SQMM, 1 - Heat Shrink Sleeve - 50 SQMM
8.17 | Endterminations | Nos. |  |  |  |  | 0 | 0 | 0 | Earthing Works
[7 empty] | 0 | 0 | 0
8.18 | 1 Core x 240 Sq. mm | Mts. |  |  |  |  | 0 | 0 | 0 | Earthing Works | 1 - LUGS / THIMBLE 25 SQMM PIN TYPE - COPPER, 1 - LUGS / THIMBLE 50 SQMM RING TYPE - COPPER, 1 - Heat Shrink Sleeve - 25 SQMM, 1 - Heat Shrink Sleeve - 50 SQMM
8.19 | Endterminations | Nos. |  |  |  |  | 0 | 0 | 0 | Earthing Works
[7 empty] | 0 | 0 | 0
8.2 | 1 Core x 185 Sq. mm | Mts. |  |  |  |  | 0 | 0 | 0 | Earthing Works | 1 - LUGS / THIMBLE 25 SQMM PIN TYPE - COPPER, 1 - LUGS / THIMBLE 50 SQMM RING TYPE - COPPER, 1 - Heat Shrink Sleeve - 25 SQMM, 1 - Heat Shrink Sleeve - 50 SQMM
8.21 | Endterminations | Nos. |  |  |  |  | 0 | 0 | 0 | Earthing Works
[7 empty] | 0 | 0 | 0
8.22 | 1 Core x 150 Sq. mm | Mts. |  |  |  |  | 0 | 0 | 0 | Earthing Works | 1 - 150 SQMM COPPER WIRE BLACK, 1 - LUGS / THIMBLE 25 SQMM PIN TYPE - COPPER, 1 - LUGS / THIMBLE 50 SQMM RING TYPE - COPPER, 1 - Heat Shrink Sleeve - 25 SQMM, 1 - Heat Shrink Sleeve - 50 SQMM
8.23 | Endterminations | Nos. |  |  |  |  | 0 | 0 | 0 | Earthing Works
[7 empty] | 0 | 0 | 0
8.24 | 1 Core x 120 Sq. mm | Mts. |  |  |  |  | 0 | 0 | 0 | Earthing Works | 1 - 120 SQMM COPPER WIRE BLACK, 1 - LUGS / THIMBLE 25 SQMM PIN TYPE - COPPER, 1 - LUGS / THIMBLE 50 SQMM RING TYPE - COPPER, 1 - Heat Shrink Sleeve - 25 SQMM, 1 - Heat Shrink Sleeve - 50 SQMM
8.25 | Endterminations | Nos. |  |  |  |  | 0 | 0 | 0 | Earthing Works
[7 empty] | 0 | 0 | 0
8.26 | 1 Core x 95 Sq. mm | Mts |  |  |  |  | 0 | 0 | 0 | Earthing Works | 1 - LUGS / THIMBLE 25 SQMM PIN TYPE - COPPER, 1 - LUGS / THIMBLE 50 SQMM RING TYPE - COPPER, 1 - Heat Shrink Sleeve - 25 SQMM, 1 - Heat Shrink Sleeve - 50 SQMM
8.27 | Endterminations | Nos. |  |  |  |  | 0 | 0 | 0 | Earthing Works
[7 empty] | 0 | 0 | 0
8.28 | 1 Core x 70 Sq. mm | Mts. |  |  |  |  | 0 | 0 | 0 | Earthing Works | 1 - LUGS / THIMBLE 25 SQMM PIN TYPE - COPPER, 1 - LUGS / THIMBLE 50 SQMM RING TYPE - COPPER, 1 - Heat Shrink Sleeve - 25 SQMM, 1 - Heat Shrink Sleeve - 50 SQMM
8.29 | Endterminations | Nos. |  |  |  |  | 0 | 0 | 0 | Earthing Works
[7 empty] | 0 | 0 | 0
8.3 | 1 Core x 50 Sq. mm | Mts. |  |  |  |  | 0 | 0 | 0 | Earthing Works | 1 - 150 SQMM COPPER WIRE BLACK, 1 - LUGS / THIMBLE 25 SQMM PIN TYPE - COPPER, 1 - LUGS / THIMBLE 50 SQMM RING TYPE - COPPER, 1 - Heat Shrink Sleeve - 25 SQMM, 1 - Heat Shrink Sleeve - 50 SQMM
8.31 | Endterminations | Nos. |  |  |  |  | 0 | 0 | 0 | Earthing Works
[7 empty] | 0 | 0 | 0
8.32 | 1 Core x 35 Sq. mm | Mts. |  |  |  |  | 0 | 0 | 0 | Earthing Works | 1 - LUGS / THIMBLE 25 SQMM PIN TYPE - COPPER, 1 - LUGS / THIMBLE 50 SQMM RING TYPE - COPPER, 1 - Heat Shrink Sleeve - 25 SQMM, 1 - Heat Shrink Sleeve - 50 SQMM
8.33 | Endterminations | Nos. |  |  |  |  | 0 | 0 | 0 | Earthing Works
[7 empty] | 0 | 0 | 0
8.34 | 1 Core x 25Sq. mm | Mts. | 200 | 200 | 500 | 30 | 100000 | 6000 | 106000 | Earthing Works | 200 - 25 SQMM COPPER WIRE YELLOW, 200 - 25 SQMM COPPER WIRE RED, 200 - 25 SQMM COPPER WIRE BLUE, 200 - 25 SQMM COPPER WIRE GREEN, 200 - 25 SQMM COPPER WIRE BLACK, 200 - LUGS / THIMBLE 25 SQMM PIN TYPE - COPPER, 200 - LUGS / THIMBLE 50 SQMM RING TYPE - COPPER, 200 - Heat Shrink Sleeve - 25 SQMM, 200 - Heat Shrink Sleeve - 50 SQMM
8.35 | Endterminations | Nos. | 4 | 4 | 130 | 40 | 520 | 160 | 680 | Earthing Works
[7 empty] | 0 | 0 | 0
8.36 | 1 Core x 16Sq. mm | Mts. | 200 | 200 | 320 | 30 | 64000 | 6000 | 70000 | Earthing Works | 200 - LUGS / THIMBLE 25 SQMM PIN TYPE - COPPER, 200 - LUGS / THIMBLE 50 SQMM RING TYPE - COPPER, 200 - Heat Shrink Sleeve - 25 SQMM, 200 - Heat Shrink Sleeve - 50 SQMM
8.37 | End terminations | Nos. | 6 | 6 | 80 | 20 | 480 | 120 | 600 | Earthing Works
[7 empty] | 0 | 0 | 0
8.38 | 1 Core x 10Sq. mm | Mts. |  |  |  |  | 0 | 0 | 0 | Earthing Works | 1 - LUGS / THIMBLE 25 SQMM PIN TYPE - COPPER, 1 - LUGS / THIMBLE 50 SQMM RING TYPE - COPPER, 1 - Heat Shrink Sleeve - 25 SQMM, 1 - Heat Shrink Sleeve - 50 SQMM
8.39 | Endterminations | Nos. |  |  |  |  | 0 | 0 | 0 | Earthing Works
[7 empty] | 0 | 0 | 0
8.4 | 1 Core x 6Sq. mm | Mts. | 150 | 150 | 120 | 20 | 18000 | 3000 | 21000 | Earthing Works | 150 - LUGS / THIMBLE 25 SQMM PIN TYPE - COPPER, 150 - LUGS / THIMBLE 50 SQMM RING TYPE - COPPER, 150 - Heat Shrink Sleeve - 25 SQMM, 150 - Heat Shrink Sleeve - 50 SQMM
8.41 | Endterminations | Nos. | 2 | 2 | 80 | 20 | 160 | 40 | 200 | Earthing Works
[7 empty] | 0 | 0 | 0
8.42 | 1 Core x 4Sq. mm | Mts. | 150 | 150 | 80 | 20 | 12000 | 3000 | 15000 | Earthing Works | 150 - LUGS / THIMBLE 25 SQMM PIN TYPE - COPPER, 150 - LUGS / THIMBLE 50 SQMM RING TYPE - COPPER, 150 - Heat Shrink Sleeve - 25 SQMM, 150 - Heat Shrink Sleeve - 50 SQMM
8.43 | Endterminations | Nos. | 4 | 4 | 70 | 20 | 280 | 80 | 360 | Earthing Works
[7 empty] | 0 | 0 | 0
8.44 | 1 Core x 2.5Sq. mm | Mts. |  |  |  |  | 0 | 0 | 0 | Earthing Works | 1 - LUGS / THIMBLE 25 SQMM PIN TYPE - COPPER, 1 - LUGS / THIMBLE 50 SQMM RING TYPE - COPPER, 1 - Heat Shrink Sleeve - 25 SQMM, 1 - Heat Shrink Sleeve - 50 SQMM
8.45 | Endterminations | Nos. |  |  |  |  | 0 | 0 | 0 | Earthing Works
[7 empty] | 0 | 0 | 0
8.46 | 1 Core x 1.5Sq. mm | Mts. |  |  |  |  | 0 | 0 | 0 | Earthing Works | 1 - LUGS / THIMBLE 25 SQMM PIN TYPE - COPPER, 1 - LUGS / THIMBLE 50 SQMM RING TYPE - COPPER, 1 - Heat Shrink Sleeve - 25 SQMM, 1 - Heat Shrink Sleeve - 50 SQMM
8.47 | Endterminations | Nos. |  |  |  |  | 0 | 0 | 0 | Earthing Works
[7 empty] | 0 | 0 | 0
8.48 | Antistatic floor earthing with 25 x 0.05mm thick copper film | Mts. |  |  |  |  | 0 | 0 | 0 | Earthing Works
[7 empty] | 0 | 0 | 0
8.49 | PVC insulating tapes of 19mm width in rolls of 10 meters for Neutral taping earth strips | Mtrs |  |  |  |  | 0 | 0 | 0 | Earthing Works
[7 empty] | 0 | 0 | 0
8.5 | 600mm long, 25 x 6 Copper, Earth bus suitable for terminating for cables with holes at regular intervals connected to main bus. The same need to be mounted in MS box with transparent cover.Naming to be done as per the requirement.Detailed drawings attached in earthing schematic & construction of earth box to be made as per schematic[For UPS Cables termination] | Nos. | 1 | 1 | 5400 | 500 | 5400 | 500 | 5900 | Earthing Works | 1 - Earth Bus Bar - Copper (0.5 MTR), 1 - Earth Distribution Box - Copper (25MM X 6MM)
[7 empty] | 0 | 0 | 0
8.51 | 600mm long, 50 x 6 Copper, Earth bus suitable for terminating for cables with holes at regular intervals connected to main bus. The same need to be mounted in MS box with transparent cover.Naming to be done as per the Requirement.Detailed drawings attached in earthing schematic & construction of earth box to be made as per schematic [For UPS Cables termination] | Nos. |  |  |  |  | 0 | 0 | 0 | Earthing Works | 1 - Earth Bus Bar - Copper (0.5 MTR), 1 - Earth Distribution Box - Copper (75MM X 6MM)
[7 empty] | 0 | 0 | 0
8.52 | Bimettalic Strip | Nos. |  |  |  |  | 0 | 0 | 0 | Earthing Works | 1 - Earth Strip Sleeve 25MM X 6MM - Green
[7 empty] | 0 | 0 | 0
X | MISCELLANEOUS ITEMS | [5 empty] | 0 | 0 | 0
| All the items shall be of IS certified | [5 empty] | 0 | 0 | 0
| All the items shall be in line with CEIG requirement | [5 empty] | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
| Providing, Laying and fixing of following dia RCC Pipe NP2 class in ground complete with RCC collars, jointing with cement mortar 1:2 (1 cement : 2 fine sand) including trenching (75 cm deep) & refilling etc. as required for cable laying at the road crossing or wherever necessary as per site condition. Cost to include RCC collar and necessary civil works as required. | [5 empty] | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
10.1 | 200mm dia | Mts. |  |  |  |  | 0 | 0 | 0 | Testing & Commissioning
[7 empty] | 0 | 0 | 0
10.2 | 300mm dia | Mts. |  |  |  |  | 0 | 0 | 0 | Testing & Commissioning
[7 empty] | 0 | 0 | 0
10.3 | 100 mm dia HDPE pipe | Mts. |  |  |  |  | 0 | 0 | 0 | Floor Raceway & Cable Tray Work
[7 empty] | 0 | 0 | 0
10.4 | Supply and fixing of 1.1 KV grade nominal 2.0 mm +/- 10% thick insulated Synthetic Mat conforming to IS 15652: 2006 and meeting the requirements of IS 5216 (Part1,2&3), IS 8437, IEC-479 Pub-1, along-with suitable adhesive/ chemibound, Pu resin, waterproofing compound and sealing material as per in service recommendation - 2 m x 1m | Nos. | 1 | 1 | 3200 | 500 | 3200 | 500 | 3700 | DB - MCB Installation and Dressing
[7 empty] | 0 | 0 | 0
10.5 | Supply & fixing of shock treatment chart duly framed with 5mm thick glass required both in Hindi, English & Kannada for treating person suffering due to electric shock suitable to mount on wall. | Nos. | 1 | 1 | 1500 | 500 | 1500 | 500 | 2000 | Testing & Commissioning
[7 empty] | 0 | 0 | 0
10.6 | Supply & fixing of First Aid box conforming to IS 2217 -1963. | Nos. | 1 | 1 | 2000 | 500 | 2000 | 500 | 2500 | Testing & Commissioning
[7 empty] | 0 | 0 | 0
10.7 | Providing and fixing L.V. danger notice plate of 200 mm X 150 mm, made of mild steel, 2 mm thick, and vitreous enameled white on both sides, and with inscription in single red Colour on front side as required. | Nos. | 1 | 1 | 1500 | 500 | 1500 | 500 | 2000 | Testing & Commissioning
[7 empty] | 0 | 0 | 0
10.8 | Fire Bucket with stand suitable for 2 buckets of round shape bottom, painted red marked 'FIRE' and duly filled with river sand. | Nos. | 1 | 1 | 850 | 500 | 850 | 500 | 1350 | Testing & Commissioning
[7 empty] | 0 | 0 | 0
10.9 | Supply and fixing of self illuminated LAMINATED Single line diagram chart duly framed with 5mm thick glass suitable to mount on wall with studs. (AO size) | Nos. | 1 | 1 | 2500 | 500 | 2500 | 500 | 3000 | Testing & Commissioning
[7 empty] | 0 | 0 | 0
10.1 | MS support with 2 coats of anti rusting primer & epoxy enamel paint - Approval should be taken before operating the item. | Kgs | 25 | 25 | 165 | 35 | 4125 | 875 | 5000 | Ceiling Cable Tray & Raceway Supporting Work | 25 - Electro Galvanized Hardware M8X20MM (1 Nut, 25 - 1 Hex Bolt, 25 - 2 Washer)
[7 empty] | 0 | 0 | 0
10.11 | Supply & installation of 150mm wide x 100mm depth 16G DB cabinet MS Powder coated of DB colour. | Mtr | 55 | 55 | 770 | 105 | 42350 | 5775 | 48125 | Testing & Commissioning
[7 empty] | 0 | 0 | 0
10.12 | Fire Barrier Sealants (acrylic Latex Caulk) for Metal pipes,cables through Gypsum walls of 50 mm thick with smaller gaps of less than 20 mm. | Sq.Mtr |  |  |  |  | 0 | 0 | 0 | Critical Room Works
[7 empty] | 0 | 0 | 0
10.13 | Supply of Rubber hand gloves suitable for 1.1KV. | Pairs | 2 | 2 | 600 | 100 | 1200 | 200 | 1400 | Testing & Commissioning
10.13 | SITC of fire sealent-Qnt added as per asumption-Quantity may be increse or decrease subject to site requirements | Sqmtr | 1 | 1 | 5000 | 2500 | 5000 | 2500 | 7500 | Critical Room Works
10.14 | 2 hour fire rated fire retardant material sealing all electrical cutouts/ducts and openings made in the slab / wall / partition to take conduits / cable trays / raceways etc as required complete / as directed by the site incharge. Vertical openings will be closed wit 4.5 mm chequered plate and sealent(3m/Hilti) | Sq.Mtr |  |  |  |  | 0 | 0 | 0 | Critical Room Works
[7 empty] | 0 | 0 | 0
10.15 | Neccesary wall opening , wall chasing for Electrical /Data /ACS/CCtV/AV services entry and closure with chicken mesh and cement mortar with experience professional for all the civil walls in the project . | Ls |  |  |  |  | 0 | 0 | 0 | Critical Room Works
[7 empty] | 0 | 0 | 0
10.16 | Emergency power off | [5 empty] | 0 | 0 | 0
| The EPO station button has one double pole, double throw momentary contact push-button switch. One normally opened (NO) contact is connected from the power source (240 V AC) to the shunt trip contactor coil. When actuated, the contact connects the 240V AC power. One normally closed (NC) contact is connected to the BMS or monitoring/alarm system for the raised floor operation such that an alarm point is displayed or recorded to identify the specific EPO station which has been activated. | Nos. |  |  |  |  | 0 | 0 | 0 | Testing & Commissioning
[7 empty] | 0 | 0 | 0
10.17 | As built drawings: | [5 empty] | 0 | 0 | 0
| Preparation and Submission of self illuminated A1 size as built drawings of total work executed (5 Sets hard and 1 Sets soft copy in Pen drive/CD's(5 No). | LS | 1 | 1 | 30000 | 10000 | 30000 | 10000 | 40000 | Testing & Commissioning
[7 empty] | 0 | 0 | 0
XI | Temporary Lighting & Power arrangement | [5 empty] | 0 | 0 | 0
A | Providing Temporary Lighting & Power arrangement with sufficient temporary Lighting ( Min 200Lux Ave. ) & power shall be provided to all agencies during execution with the following requirements | Lot | 1 | 1 |  |  | 0 | 0 | 0 | Testing & Commissioning | 1 - MS Movable Stand (For Temporary Industrial Power Box), 1 - 3 Pin 16A Industrial Socket and Plug, 1 - 2CX1.5 SQMM CU FLEX CABLE - LOCAL MAKE, 1 - Temporary Power - Industrial Socket Panel, 1 - GI Base Saddle - 10MM, 1 - 16 Gauge GI Wire, 1 - LED Flood Light 50W, 1 - 3CX2.5SQMM CU FLEX CABLE - LOCAL MAKE, 1 - 2 PIN MALE + FEMALE PLUG - LOCAL, 1 - 16A SWITCH - ANY MAKE, 1 - 16A POWER SOCKET - ANY MAKE, 1 - 8M PVC BOX - ANY MAKE, 1 - 8M FACE PLATE - ANY MAKE, 1 - TEMP LED FIRE EXIT SIGNAGE, 1 - 4CX10SQMM AL AR CABLE - LOCAL MAKE, 1 - TEMP POWER SUPPLY INDUSTRIAL SOCKET BOX, 1 - 2CX1SQMM CU FLEX CABLE - LOCAL MAKE, 1 - EMERGENCY TUBE LIGHT, 1 - T5 LED TUBE LIGHT - 20W - ANY MAKE
| 1. Considering 24/7 lighting for all the equal distance (minimum 15 feet ) . , All the passage with the 4feet (40w)Patti/tube light fittings on equal distance and all the enclosed area to be provided with light fixtures until the project works are completed. | [5 empty] | 0 | 0 | 0
| 2. A main panel built up with all the safety protection features having 10 feeders for the main contractors (HVAC/INTERIOR/ELECTRICAL/FIRE FIGHTING) capacity of feeding 6welding machines /20drilling machines with energy meter ,main incoming feeder with energy meter and 2 Feeders to all the floors PDB and lighting DB with energy meter. | [5 empty] | 0 | 0 | 0
| 3. All the floor office area to be provided with 4PDB distributed in equal distance & each should be equipped with the 8nos industrial socket with all the safety protection features. | [5 empty] | 0 | 0 | 0
| 4. Halogen lights (200w) to be provided wherever necessary as per the project requirement (sufficient numbers to be stocked) | [5 empty] | 0 | 0 | 0
| 5. All the entry/temporary toilets/ path ways ,staircases, vendor store area, material stacking place to be provided with adequate lighting with 4feet Patti fitting on the equal distance | [5 empty] | 0 | 0 | 0
| 6. Cabling from the main Incomer feeder to the main panel and all the floors PDBs and lighting controls and DB to be considered and the cabling to be routed in the ceiling level. | [5 empty] | 0 | 0 | 0
| 7. Temporary earthing to the main panel & DG's to be considered. | [5 empty] | 0 | 0 | 0
| 8. Above installation works to be completed within an given period of time in all the work area. | [5 empty] | 0 | 0 | 0
| 9. A dedicated qualified electrician with tools to be provided 24/7 for maintaining the temporary lighting and DG. | [5 empty] | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
11.1 | Supply, installation, testing & commissioning of 100KVA DG sets along with AMF panel on rental basis. The price shall include temporary arrangement of exhaust system, fuel system and necessary statutory approvals to run the DG set. The price also include maintenance of DG set, removing of DG set & its associated works in all respect once the rental agreement is expired. The price shall be quoted on monthly basis. | Month |  |  |  |  | 0 | 0 | 0 | Testing & Commissioning | 1 - MS Movable Stand (For Temporary Industrial Power Box), 1 - 3 Pin 16A Industrial Socket and Plug, 1 - 2CX1.5 SQMM CU FLEX CABLE - LOCAL MAKE, 1 - Temporary Power - Industrial Socket Panel, 1 - GI Base Saddle - 10MM, 1 - 16 Gauge GI Wire, 1 - LED Flood Light 50W, 1 - 3CX2.5SQMM CU FLEX CABLE - LOCAL MAKE, 1 - 2 PIN MALE + FEMALE PLUG - LOCAL, 1 - 16A SWITCH - ANY MAKE, 1 - 16A POWER SOCKET - ANY MAKE, 1 - 8M PVC BOX - ANY MAKE, 1 - 8M FACE PLATE - ANY MAKE, 1 - TEMP LED FIRE EXIT SIGNAGE, 1 - 4CX10SQMM AL AR CABLE - LOCAL MAKE, 1 - TEMP POWER SUPPLY INDUSTRIAL SOCKET BOX, 1 - 2CX1SQMM CU FLEX CABLE - LOCAL MAKE, 1 - EMERGENCY TUBE LIGHT, 1 - T5 LED TUBE LIGHT - 20W - ANY MAKE
[7 empty] | 0 | 0 | 0
11.2 | Supply, installation, testing & commissioning of 62.5KVA DG sets along with AMF panel on rental basis. The price shall include temporary arrangement of exhaust system, fuel system and necessary statutory approvals to run the DG set. The price also include maintenance of DG set, removing of DG set & its associated works in all respect once the rental agreement is expired. The price shall be quoted on monthly basis. | Month |  |  |  |  | 0 | 0 | 0 | Testing & Commissioning | 1 - MS Movable Stand (For Temporary Industrial Power Box), 1 - 3 Pin 16A Industrial Socket and Plug, 1 - 2CX1.5 SQMM CU FLEX CABLE - LOCAL MAKE, 1 - Temporary Power - Industrial Socket Panel, 1 - GI Base Saddle - 10MM, 1 - 16 Gauge GI Wire, 1 - LED Flood Light 50W, 1 - 3CX2.5SQMM CU FLEX CABLE - LOCAL MAKE, 1 - 2 PIN MALE + FEMALE PLUG - LOCAL, 1 - 16A SWITCH - ANY MAKE, 1 - 16A POWER SOCKET - ANY MAKE, 1 - 8M PVC BOX - ANY MAKE, 1 - 8M FACE PLATE - ANY MAKE, 1 - TEMP LED FIRE EXIT SIGNAGE, 1 - 4CX10SQMM AL AR CABLE - LOCAL MAKE, 1 - TEMP POWER SUPPLY INDUSTRIAL SOCKET BOX, 1 - 2CX1SQMM CU FLEX CABLE - LOCAL MAKE, 1 - EMERGENCY TUBE LIGHT, 1 - T5 LED TUBE LIGHT - 20W - ANY MAKE
[7 empty] | 0 | 0 | 0
11.3 | Diesel consumption for 100 KVA DG & Price will be paid as per actuals. | Hrs |  |  |  |  | 0 | 0 | 0 | Testing & Commissioning | 1 - MS Movable Stand (For Temporary Industrial Power Box), 1 - 3 Pin 16A Industrial Socket and Plug, 1 - 2CX1.5 SQMM CU FLEX CABLE - LOCAL MAKE, 1 - Temporary Power - Industrial Socket Panel, 1 - GI Base Saddle - 10MM, 1 - 16 Gauge GI Wire, 1 - LED Flood Light 50W, 1 - 3CX2.5SQMM CU FLEX CABLE - LOCAL MAKE, 1 - 2 PIN MALE + FEMALE PLUG - LOCAL, 1 - 16A SWITCH - ANY MAKE, 1 - 16A POWER SOCKET - ANY MAKE, 1 - 8M PVC BOX - ANY MAKE, 1 - 8M FACE PLATE - ANY MAKE, 1 - TEMP LED FIRE EXIT SIGNAGE, 1 - 4CX10SQMM AL AR CABLE - LOCAL MAKE, 1 - TEMP POWER SUPPLY INDUSTRIAL SOCKET BOX, 1 - 2CX1SQMM CU FLEX CABLE - LOCAL MAKE, 1 - EMERGENCY TUBE LIGHT, 1 - T5 LED TUBE LIGHT - 20W - ANY MAKE
[7 empty] | 0 | 0 | 0
11.4 | Diesel consumption for 62.5 KVA DG & Price will be paid as per actuals. | Hrs |  |  |  |  | 0 | 0 | 0 | Testing & Commissioning | 1 - MS Movable Stand (For Temporary Industrial Power Box), 1 - 3 Pin 16A Industrial Socket and Plug, 1 - 2CX1.5 SQMM CU FLEX CABLE - LOCAL MAKE, 1 - Temporary Power - Industrial Socket Panel, 1 - GI Base Saddle - 10MM, 1 - 16 Gauge GI Wire, 1 - LED Flood Light 50W, 1 - 3CX2.5SQMM CU FLEX CABLE - LOCAL MAKE, 1 - 2 PIN MALE + FEMALE PLUG - LOCAL, 1 - 16A SWITCH - ANY MAKE, 1 - 16A POWER SOCKET - ANY MAKE, 1 - 8M PVC BOX - ANY MAKE, 1 - 8M FACE PLATE - ANY MAKE, 1 - TEMP LED FIRE EXIT SIGNAGE, 1 - 4CX10SQMM AL AR CABLE - LOCAL MAKE, 1 - TEMP POWER SUPPLY INDUSTRIAL SOCKET BOX, 1 - 2CX1SQMM CU FLEX CABLE - LOCAL MAKE, 1 - EMERGENCY TUBE LIGHT, 1 - T5 LED TUBE LIGHT - 20W - ANY MAKE
[7 empty] | 0 | 0 | 0
[7 empty] | 0 | 0 | 0
XII | Professional Charges: | [5 empty] | 0 | 0 | 0
| Professional charges towards filing application, preparation of drawings in necessary formats for approval, follow up and arranging approval of drawings, scheme by Local electricity authority / Electrical Inspectorate, obtaining clearance from electricity authority / Electrical Inspectorate/ CEIG. All necessary charges shall be part of contractor scope only. client will not pay any charges for the same | LS | 1 | 1 |  | 225000 | 0 | 225000 | 225000 | Testing & Commissioning
[7 empty] | 0 | 0 | 0
XIII | Supply, installation, testing and commissioning (SITC) of 3kVA inverter, Single phase input / Single phase output, complete with SMF batteries suitable for providing minimum 90 minutes backup for emergency lighting system. The item includes inverter unit, battery bank, interconnecting cables, battery rack (if required), protection devices, earthing, charging system, all accessories, testing and commissioning complete as per specifications, drawings | No. | 1 | 1 | 60000 | 10000 | 60000 | 10000 | 70000
[7 empty] | 0 | 0 | 0
| TOTAL - ELECTRICAL LT WORKS | [5 empty] | 4042010 | 746730 | 4788740