## Summary
Project | : Inovalon
Location | : Gurugram
Title | : Electrical BOQ Summary
S No | PARTICULARS | SUPPLY AMOUNT IN INR | INSTALLATION AMOUNT IN INR | TOTAL AMOUNT IN INR
1 | CIRCUIT / SUB MAINS | 1633190 | 347560 | 1980750
2 | POWER RECEPTACLES. | 449353 | 88754 | 538107
3 | CONDUITING WORKS | 127864 | 21028 | 148892
4 | EARTHING | 180502 | 21813 | 202315
5 | LT CABLE & TERMINATION | 614256 | 55866 | 670122
6 | RACEWAYS AND CABLE TRAYS | 704321 | 127710 | 832031
7 | DISTRIBUTION BOARDS | 303463 | 24001 | 327464
8 | SUB DISTRIBUTION PANELS | 456135 | 32900 | 489035
9 | MISCELLANEOUS WORKS | 186990 | 29798 | 216788
10 | FUNCTIONAL LIGHT FIXTURE INSTALLATION | 0 | 718400 | 718400
11 | DECORATIVE LIGHT FIXTURE INSTALLATION | 0 | 16700 | 16700
| TOTAL AMOUNT (EXCL TAXES) | 4656074 | 1484530 | 6140604
Assumptions Inclusion & Exclusions
1 | Only conduit / raceways are considered for networking. Active components, I/O ports and cables are not considered.
2 | AV realated components are not considered in the BOQ.
3 | Earthing cable / strip might be change as per the allocated space by the builder / As per the site condition for earth pits.
4 | Cost for Wedge Clamps to be considered for all services support for Deck slab.
5 | Supply of Light fixtures not included in scope. Only installation included in Electrical scope.
6 | UPS related works are not inculded in the BOQ.
7 | Builder panel related modification work is not captured in the BOQ. Builder to make necessary provision as per client requirement.
8 | Cable length, Cable tray & earth strip for HVAC units might vary as per site condition.
9 | Raceway length from network provider location to server room location might vary as per site condition.
10 | Raceway for networking for workstation is designed considering 2nos data per work station.
11 | Recieving, Shifting to the designated store & from store to the site floors wooden blocks, screws ,hardware's as required as per the site conditions (including the earthing of fixture) for Light fixtures
12 | Taxes not included.

## Electrical
Project | : Inovalon
Location | : Gurugram
Title | : Electrical BOQ Summary
S. NO | Item Description | UOM | Total Qty | Rate in INR |  | Amount in INR
|  |  |  | Supply | Installation | Supply | Installation
A. | POINT WIRING
All sockets to be checked with a Check Plug socket tester for live-neutral reverse, no earth,neutral fault, live earth reverse, neutral earth reverse.
The Circuit No. and DB no. label shall be provided on all UPS ,RAW sockets and switchboards with label printer.
Colour coding for conduits to be done for different systems. The whole length of conduits to be painted.
All circuit & point wiring shall be colour coded & shall have ferruling on both end for circuit identification complete as required etc.Labelling on all the switches and sockets to be done with respect to DB reference, phase and circuit no.
Earth loop Impedance Test to be performed. RCD test to be done. Cable Insulation Tests to be done.
Wherever the occupancy sensor is provided in the cabin/ meeting rooms the circuit wires from Distribution Board to occupancy sensor and sensor to switch are inclusive in the point wiring rate.
1 | CIRCUIT / SUB MAINS:
Supply, drawing, testing and commissioning of circuit mains wiring using 1.1 kV grade PVC insulated copper conductor (MSCC) wires or PVC insulated, PVC sheathed three‑core copper cables, drawn in 1.6 mm thick PVC conduits or in existing raceways, complete as per approved drawings, specifications, and relevant Indian Standards. Rates quoted shall include supply of cables only (Conduits, Raceway related accessories shall be considered separately). All terminations shall be provided with solderless crimping type copper lugs/sockets, ferrules indicating source code on load side and load code on source side. No joints shall be permitted in circuit wiring; only looping shall be allowed at terminal blocks, switches, sensors, and socket outlets.
Lighting Circuit mains using 3C × 2.5 sq.mm copper cable or 2R x 2.5 sq.mm + 1R x 1.5 sq.mm Cu FRLS wire Measurement from respective DB to the switches / sensors, including looping between switches / sensors. Looping from sensors/switch to light fixtures will be 3Cx1.5Cu cable or 2R x 1.5 sq.mm + 1R x 1.5 sq.mm Copper FRLS wire as per approved drawings, specifications and project requirement. For RP & UPS circuit mains shall be measured from respective DB to the last point, looping from switch / Socket to another switch / socket board will not be paid separately.
NOTE:
1) Conduits running above false ceilings in multiple runs shall be supported using slotted GI ‘C’ channels or spacers & saddles at intervals not exceeding 0.5 m.
2) Accessories shall include bends, collars, junction boxes, spacers, saddles, screws, and flexible conduits.
3) Conduits shall be ISI marked
4) Number of wires drawn in each conduit shall comply with IS 694.
5) Different phases shall not be drawn in the same conduit.
6) Conduit joints shall be made using threading and proper accessories only.
7) Each circuit shall be provided with yellow ferrules indicating circuit numbers.
8) The color coding for conduits shall be: (Exposed Conduits to match ceiling color) i. Raw power and Lighting : Black ii. UPS Power : White iii. Data and Voice : Grey iv. Other systems : Black
1.1 | 2R x 2.5 sq.mm + 1R x 1.5 sq.mm Cu FRLS wire in 20 mm dia MS conduit / Wire ways. (Lighting Circuits) | Rmt | 1950 | 159 | 38 | 310050 | 74100
1.2 | 3C x 2.5 sqmm Multi Core Copper FRLS cable in existing raceway/conduit (Ltg Circuit Main) (measurement of conduit and raceway will be separate) | Rmt | 20 | 141 | 29 | 2820 | 580
1.3 | 3C x 1.5 sqmm Teflon insulated Transparent cable | Rmt | 20 | 88 | 19 | 1760 | 380
1.4 | 2R x 1.5 sq.mm + 1R x 1.5 sq.mm Copper FRLS wire in 20 mm dia MS conduit / Wire ways. (Point wiring) | Rmt | 1250 | 123 | 29 | 153750 | 36250
1.5 | 4R x 4 sq.mm + 1R x 2.5 sq.mm Copper FRLS wire in 32mm dia MS conduit / Wire ways. | Rmt | 30 | 377 | 85 | 11310 | 2550
1.6 | 3C x 6 sq.mm cable with PVC-FRLS insulated outer sheath & multi strand copper conductors, unarmoured, cable to be laid in raceways / conduits (cost of raceways/conduits to exclude). | Rmt | 250 | 316 | 29 | 79000 | 7250
1.7 | 2R x 4 sq.mm + 1R x 2.5 sq.mm Copper FRLS wire in 25 mm dia FR PVC conduit / PVC Sleeve. | Rmt | 350 | 219 | 57 | 76650 | 19950
1.8 | 3C x 4 sqmm Multi Core Copper FRLS cable in existing raceway/conduit (measurement of conduit and raceway will be separate) | Rmt | 250 | 215 | 47 | 53750 | 11750
1.9 | 3C x 2.5 sqmm Multi Core Copper FRLS cable in existing raceway/conduit (measurement of conduit and raceway will be separate) | Rmt | 6600 | 141 | 29 | 930600 | 191400
1.1 | 3C x 1.5 sqmm Multi Core Copper FRLS cable (1st ON/OFF driver light to LMS module) | Rmt | 100 | 88 | 19 | 8800 | 1900
1.11 | Supply, Laying, Testing and Commissioning of 2Core x 1.5 Sqmm Dali cable for connection and looping of light fixtures (exclusive of power cable) | Rmt | 50 | 94 | 29 | 4700 | 1450
| TOTAL CARRIED OVER TO SUMMARY |  |  |  |  | 1633190 | 347560
2 | POWER RECEPTACLES.
Supply, Installation, Testing and Commissioning of the following Modular/Industrial Switch, sockets with modular front plate, and accessories as per the site conditions.
The quoted rate for power socket outlets shall include a. Socket outlets - round / round cum flat / flat multi pin socket outlets b. Switches c. 14SWG metal boxes with knockout on all sides d. Front plate of required colours with accessories e. Fixing accessories like wooden screws, self threading screw, gripper, etc.
Industrial type sockets shall be of Metal clad / Polycarbonate body with plug top. All switch / sockets shall be provided with printed labels / stickers indicating source code. Colour code for UPS socket plates : White/ as per architect. Colour code for RP socket plates : Black/Grey/ as per architect. All switch / sockets including front plate & frame which will be mounted on the metal boxes shall have removable film coat to protect from scratches & paint during installation.
Note: Safety shutters to prevent accidental contact with live parts shall be provided. No indicator shall be provided for switches
Modular : Round multipin type With Box
5.1 | 1 no 6/16A socket controlled by 16A switch. | Nos | 53 | 348 | 76 | 18444 | 4028
5.2 | 1 no 6A universal socket controlled by 6A SP switch. | Nos | 75 | 264 | 57 | 19800 | 4275
5.3 | 1 no 16A Universal socket controlled by a 16A switch | Nos | 45 | 348 | 76 | 15660 | 3420
The word UPS shall be printed on all UPS sockets.
The word RAW shall be printed on all RAW sockets.
The Circuit No. and DB no. label shall be provided on all UPS ,RAW sockets and switchboards with label printer.
Contractor is required to submit samples of all types of switches and sockets to Consultant and Architects representative for approval before ordering the material.
21 | Providing and fixing of 1 Nos.6 amp flush type 3 pin socket and 1 No. 6 amps switch cover plate, 5 sided G.I. Boxes for housing switches and sockets and earthing complete as required (for UPS). GI Box to have earth pin for body earthing (UPS/Raw Power) | Nos. | 260 | 264 | 57 | 68640 | 14820
22 | Providing and fixing of 2 Nos.6 amp flush type 3 pin socket and 1 No. 16 amps switch cover plate, 5 sided G.I. Boxes for housing switches and sockets and earthing complete as required. GI Box to have earth pin for body earthing (UPS/Raw Power) | Nos. | 40 | 480 | 104 | 19200 | 4160
23 | Providing and fixing of 3 Nos.6 amp flush type 3 pin socket and 1 No. 16 amps switch +1 No. USB Port cover plate, 5 sided G.I. / PVC moulded Boxes for housing switches and sockets and earthing complete as required (for UPS/RAW). GI Box to have earth pin for body earthing | Nos. | 220 | 621 | 132 | 136620 | 29040
24 | Providing and fixing of 1 Nos.USB Port (UPS) cover plate, 5 sided G.I. / PVC moulded Boxes for housing switches and sockets and earthing complete as required (for UPS/RAW). GI Box to have earth pin for body earthing | Nos. | 20 | 950 | 226 | 19000 | 4520
25 | Providing and fixing of 1 No.16 amps flush type 6 pin socket and 1 No. 16 amps switch with indicator, cover plate, 5 sided G.I. Boxes for housing switches and sockets and earthing complete as required (for UPS) GI Boxes to have earth pin for body earthing | Nos. | 5 | 348 | 76 | 1740 | 380
26 | Providing and fixing Underfloor Access Outlets 1Trap including providing 2 Nos. 6 Amps sockets and 2 no. 6/16 Amps switch(RAW/UPS) and space for 2 Nos data. | Nos. | 12 | 7050 | 940 | 84600 | 11280
27 | Supply and fixing of the following sizes of thermoplastic moulded plug and socket IEC 309 type in PVC Box of suitable size flush / surface and making connections complete as required. The box shall be IP 44.
a | 3 pin 16/20 A 1 phase industrial socket with mcb & plug top | Nos. | 0 |  |  | 0 | 0
b | 3 pin 32 A 1 phase industrial socket plug top | Nos. | 6 | 5358 | 1128 | 32148 | 6768
c | 3 pin 63 A 1 phase industrial socket with mcb & plug | Nos. | 0 |  |  | 0 | 0
28 | For Kitchen Equipments the degree of protection shall be- IP-67
a | 3 pin 25/20 /16 A 1 phase industrial socket with mcb & plug IP 67 | Nos. | 3 | 5170 | 799 | 15510 | 2397
b | 3 pin 32 A 1 phase industrial socket with mcb & plug IP 67 | Nos. | 2 | 5358 | 1128 | 10716 | 2256
c | 5 pin 32 A 3 phase industrial socket with mcb & plug IP 67 | Nos. | 1 | 7275 | 1410 | 7275 | 1410
d | 5 pin 6/16 A 3 phase industrial socket with mcb & plug IP 67 | Nos. | 0 |  |  | 0 | 0
| TOTAL CARRIED OVER TO SUMMARY |  |  |  |  | 449353 | 88754
B. | CONDUITING WORKS
2 | FOR POWER , LIGHTING CIRCUIT & POINT WIRING
Providing and fixing in position the following M.S. conduits including all accessories concealed in F. ceiling/wall/floor as required including 1.6 mm thick M.S. junction or pull boxes with 3mm thick perspex sheet cover plate compl­te with 1.6 mm dia. G.I. pull wires in the length of conduit.
a. | 20 mm dia conduit ( 1.6 mm thick) | RM | 30 | 94 | 19 | 2820 | 570
b. | 25 mm dia conduit (1.6 mm thick) | RM | 550 | 118 | 19 | 64900 | 10450
c. | 32 mm dia conduit (2.0 mm thick) | RM | 30 | 170 | 19 | 5100 | 570
2 | FOR TELEPHONE, COMPUTER & CONDUITING AND WIRING FOR T.V. SYSTEM.
Providing and fixing in position the following M.S. conduits including all accessories concealed in F. ceiling/wall/floor as required including 1.6mm thick M.S. junction or pull boxes with 3mm thick perspex sheet cover plate compl­ete with 1.6 mm dia G.I. pull wires in the length of conduit.
a. | 20 mm dia conduit ( 1.6 mm wall thickness) | RM | 30 | 94 | 19 | 2820 | 570
b. | 25 mm dia conduit ( 1.6 mm wall thickness) | RM | 350 | 118 | 19 | 41300 | 6650
c. | 32 mm dia conduit ( 1.6 mm wall thickness) | RM | 30 | 170 | 19 | 5100 | 570
2 | Providing and fixing in position suitable 1.2 mm thick G.I./ PVC outlet box for RJ- 45 computer outlet with all fixing accessories as required. | Nos. | 50 | 57 | 19 | 2850 | 950
3 | Supply and fixing of 1.2 mm thick G.I Box along with RG 11 TV Co axial socket with Cover Plate | Nos. | 2 | 57 | 19 | 114 | 38
4 | Supply drawing connecting testing and commissioning of TV Coaxial cable RG 6 in existing conduit | RM | 110 | 26 | 6 | 2860 | 660
| TOTAL CARRIED OVER TO SUMMARY |  |  |  |  | 127864 | 21028
C. | EARTHING
1 | Providing laying and fixing in position the following copper strips and wires including providing all fixing accessories and effecting proper connections,PVC sleeve etc as requried. earth strips with PVC sleeves - Insulation Sleeving Cylindrical Earthing Strip PVC Sleeve,
a. | Copper tape 25mm x 3 mm | RM | 0 |  |  | 0 | 0
b. | Copper wire 8 SWG | RM | 50 | 198 | 19 | 9900 | 950
b. | Copper wire 12 SWG | RM | 50 | 85 | 19 | 4250 | 950
2 | Providing,laying and fixing in position the following G.I. strips and wires including providing all fixing accessories and effecting proper connections etc as required.
a. | G.I. tape 25 mm x 6 mm | RM | 50 | 118 | 19 | 5900 | 950
b. | G.I. wire 8 SWG | RM | 150 | 57 | 19 | 8550 | 2850
c. | G.I. wire 12 SWG | RM | 120 | 38 | 19 | 4560 | 2280
3 | Supply installation , and making of Exothermic weld suitable to bond GI strip of 25x5 mm with Copper Strip of 25x5 mm with 75mm extensions on either side | Nos. | 2 | 6110 | 940 | 12220 | 1880
3 | Supply and laying, effecting proper connec­tions, testing & commissioning of the following sizes of 1.1 KV armoured XLPE/ unarmoured Cross linked polyethylene insulated, PVC sheathed (XLPE), conforming to IS: 7098 (Part-1)- 1988 ( 90 deg C) aluminium /copper conductor cables conforming to IS : 1554 and IS 694 for Flexible copper cable Part I - 1976 with latest amendments laid over MS supports in existing RCC ducts/ laid in ground /laid on Cable Trays including clamping the cables to sup­ports in an approved manner as required complete with all accessories.All cables shall have thermo setting insulation XLPE and low emission of smoke and corrosive gas when affected by fire
a | 1c x 35 sq.mm FR XLPE insulated flexible copper conductor cables | RM | 80 | 729 | 38 | 58320 | 3040
b | 1c x 25 sq.mm FR XLPE insulated flexible copper conductor cables | RM | 30 | 522 | 29 | 15660 | 870
c | 1c x 16 sq.mm FR XLPE insulated flexible copper conductor cables | RM | 110 | 335 | 29 | 36850 | 3190
d | 1 x 10 Sq. mm FR XLPE insulated flexible copper conductor cables (Green Colour for UPS DB Sub-main Earthing) | RM | 30 | 202 | 29 | 6060 | 870
e | 2 Nos 1 x 10 Sq. mm FR XLPE insulated flexible copper conductor cables (Green Colour for UPS DB Sub-main Earthing) | RM | 30 | 373 | 85 | 11190 | 2550
4 | Supplying and making of end termination for the following size of compression lugs and PG Threaded Nylon Flexible cable glands complete with all fixing accessories as required
a | 1c x 35 sq.mm FR XLPE insulated flexible copper conductor cables | Sets | 4 | 367 | 94 | 1468 | 376
b | 1c x 25 sq.mm FR XLPE insulated flexible copper conductor cables | Sets | 8 | 123 | 38 | 984 | 304
c | 1c x 16 sq.mm FR XLPE insulated flexible copper conductor cables (For Server & UPS SDB Earthing ) | Sets | 8 | 76 | 19 | 608 | 152
0
d | 1 x 10 Sq. mm FR XLPE insulated flexible copper conductor cables (Green Colour for UPS DB Sub-main Earthing) | Sets | 6 | 76 | 19 | 456 | 114
7 | Supply, Installation, testing and commissioning of Maintenance Free Earthing of make Electrolytic Earthing comprising of type 'K' copper 2.4 mm wall thickness, hollow tube 10 feet long, 2.125 inches outer diameter completely filled with non hazardous metallic salts (Terrafill 25 KG Min.) to achieve an earth resistance of less than 1 ohms. Provide masonry chamber with concrete base, CI man­hole cover (cover to be heavy duty) with frame (300mm x 300mm) and make earth pit sign/ identifcation no in each earth station. for UPS & Server | Nos. | 0 |  |  | 0 | 0
8 | Supply, installation, testing and commissioning of sheet metal enclosed 300 x 200 x 150 ( D) mm insulated earth distribution board with 1 nos. 50 x 6 mm copper tinned earth bars on SMC insulator suitable for 6/8 nos connections complete with all fixing accessories as required | Nos. | 0 |  |  | 0 | 0
9 | Supply, installation, testing and commissioning of sheet metal enclosed 150 x 100 x 125 ( D) mm insulated earth distribution board with 1 nos. 32 x 6 mm copper tinned earth bars on SMC insulator suitable for 6/8 nos connections complete with all fixing accessories as required. | Nos. | 3 | 452 | 99 | 1356 | 297
10 | Supply, installation, testing and commissioning of bare earth G.I. bus bar 32 x 6 mm and 300 mm long for body earth connection. Provide suitable size of supporting arrangement to fixing on wall / cable trays , the bus bar shall be suitable for 6/8 nos connections. complete with all fixing accessories as required. | Nos. | 0 |  |  | 0 | 0
11 | Supplying and laying of the following sizes of Heavy duty PVC Pipes below paved area including chase cutting and back filling.
a. | 100 mm outer dia | RM | 0 |  |  | 0 | 0
b. | 80 mm outer dia | RM | 5 | 170 | 19 | 850 | 95
12 | Providing and fixing in position the following G.I. Pipe including all accessories concealed in F. ceiling/wall/ surfaces as required including Suitable size of junction or pull boxes with cover compl­ete
a. | 50 mm dia conduit ( 2.0 mm wall thickness) | RM | 5 | 264 | 19 | 1320 | 95
b. | 75 mm dia conduit ( 2.0 mm wall thickness) | RM | 0 |  |  | 0 | 0
| TOTAL CARRIED OVER TO SUMMARY |  |  |  |  | 180502 | 21813
D | CABLES, MAINS & SUBMAINS
1 | Supply and laying, effecting proper connec­tions, testing & commissioning of the following sizes of 1.1 KV armoured XLPE / unarmoured Cross linked polyethylene insulated, PVC sheathed (XLPE), conforming to IS: 7098 (Part-1)- 1988 ( 90 deg C) aluminium /copper conductor cables conforming to IS : 1554 and IS 694 for Flexible copper cable Part I - 1976 with latest amendments laid over MS supports in existing RCC ducts/ laid in ground /laid on Cable Trays including clamping the cables to sup­ports in an approved manner as required complete with all accessories.All cables shall have thermo setting insulation XLPE and low emission of smoke and corrosive gas when affected by fire
Note: All cables to be glanded and crimped with suitable sized lugs. All Cable trays to be double earthed. All raceways and cable glands to be earthed with brass round earth clips and wires.
Earthing ring to be included in all the cable glands.
Sub main cables should be labelled at both ends
Joints shall be allowed only at the 2 ends of the cables and not in between.
a | 3.5 c x 300 sq.mm 1.1 KV grade XLPE Insulated FRLS sheathed armoured aluminium conductor cable | RM | 0 |  |  | 0 | 0
b | 3.5 c x 240 sq.mm 1.1 KV grade XLPE Insulated FRLS sheathed armoured aluminium conductor cable | RM | 0 |  |  | 0 | 0
c | 3.5 c x 185 sq.mm1.1 KV grade XLPE Insulated FRLS sheathed armoured aluminium conductor cable | RM | 0 |  |  | 0 | 0
d | 3.5 c x 150 sq.mm1.1 KV grade XLPE Insulated FRLS sheathed armoured aluminium conductor cable | RM | 0 |  |  | 0 | 0
e | 3.5 c x 120 sq.mm 1.1 KV grade XLPE Insulated FRLS sheathed armoured aluminium conductor cable | RM |  |  |  | 0 | 0
f | 3.5 c x 95sq.mm 1.1 KV grade XLPE Insulated FRLS sheathed armoured aluminium conductor cable | RM | 50 | 586 | 85 | 29300 | 4250
g | 3.5 c x 70 sq.mm 1.1 KV grade XLPE Insulated FRLS sheathed armoured aluminium conductor cable | RM | 0 |  |  | 0 | 0
h | 4 c x 35 sq.mm1.1 KV grade XLPE Insulated FRLS sheathed armoured aluminium conductor cable | RM | 0 |  |  | 0 | 0
i | 4 c x 25 sq.mm 1.1 KV grade XLPE Insulated FRLS sheathed armoured aluminium conductor cable | RM | 0 |  |  | 0 | 0
j | 4 c x 25 sq.mm 1.1 KV grade XLPE Insulated FRLS sheathed armoured copper conductor cable | RM | 0 |  |  | 0 | 0
k | 4 c x 16 sq.mm 1.1 KV grade XLPE Insulated FRLS sheathed armoured aluminium conductor cable | RM | 0 |  |  | 0 | 0
l | 4 c x 16 sq.mm 1.1 KV grade XLPE Insulated FRLS sheathed armoured copper conductor cable | RM | 435 | 175 | 38 | 76125 | 16530
m | 4 c x 10 sq.mm 1.1 KV grade XLPE Insulated FRLS sheathed armoured aluminium conductor cable | RM | 0 |  |  | 0 | 0
n | 4 c x 10 sq.mm 1.1 KV grade XLPE Insulated FRLS sheathed armoured copper conductor cable | RM | 230 | 735 | 29 | 169050 | 6670
o | 4 c x 6 sq.mm 1.1 KV grade XLPE Insulated FRLS sheathed armoured copper conductor cable | RM | 120 | 452 | 29 | 54240 | 3480
p | 3 c x 16 sq.mm 1.1 KV grade XLPE Insulated FRLS sheathed armoured copper conductor cable | RM | 0 |  |  | 0 | 0
q | 3 c x 6 sq.mm 1.1 KV grade XLPE Insulated FRLS sheathed armoured copper conductor cable | RM | 65 | 346 | 29 | 22490 | 1885
r | 3 c x 16 sq.mm 1.1 KV grade XLPE Insulated FRLS sheathed Flex. copper conductor cable | RM | 0 |  |  | 0 | 0
s | 2 c x 10 sq.mm 1.1 KV grade XLPE Insulated FRLS sheathed armoured copper conductor cable | RM | 245 | 399 | 19 | 97755 | 4655
t | 1c x 6 sq.mm FRLS XLPE insulated flexible copper conductor cables | RM | 120 | 115 | 19 | 13800 | 2280
u | 1c x 16 sq.mm FRLS XLPE insulated flexible copper conductor cables | RM | 450 | 312 | 29 | 140400 | 13050
v | 1c x 25 sq.mm FRLS XLPE insulated flexible copper conductor cables | RM | 0 |  |  | 0 | 0
2 | Supplying and making of end termination for the following size of 1.1 KV XLPE insulated copper conductor armoured cables including providing heavy duty copper terminal crimping lugs, solder, insulation tape, approved sealing epoxy compound, double compression brass cable glands, effecting gland connec­tions and effecting terminal connections to the equipment complete as required. Use compression lugs and PG Threaded Nylon Flexible cable glands for single core flexible cables
a | 3.5 c x 300 sq.mm 1.1 KV grade XLPE Insulated FRLS sheathed armoured aluminium conductor cable | Sets |  |  |  | 0 | 0
b | 3.5 c x 240 sq.mm 1.1 KV grade XLPE Insulated FRLS sheathed armoured aluminium conductor cable | Sets |  |  |  | 0 | 0
c | 3.5 c x 185 sq.mm1.1 KV grade XLPE Insulated FRLS sheathed armoured aluminium conductor cable | Sets | 0 |  |  | 0 | 0
d | 3.5 c x 150 sq.mm1.1 KV grade XLPE Insulated FRLS sheathed armoured aluminium conductor cable | Sets | 0 |  |  | 0 | 0
e | 3.5 c x 120 sq.mm 1.1 KV grade XLPE Insulated FRLS sheathed armoured aluminium conductor cable | Sets |  |  |  | 0 | 0
f | 3.5 c x 95sq.mm 1.1 KV grade XLPE Insulated FRLS sheathed armoured aluminium conductor cable | Sets | 2 | 1072 | 273 | 2144 | 546
g | 3.5 c x 70 sq.mm 1.1 KV grade XLPE Insulated FRLS sheathed armoured aluminium conductor cable | Sets | 0 |  |  | 0 | 0
h | 4 c x 35 sq.mm1.1 KV grade XLPE Insulated FRLS sheathed armoured aluminium conductor cable | RM | 0 |  |  | 0 | 0
i | 4 c x 25 sq.mm 1.1 KV grade XLPE Insulated FRLS sheathed armoured aluminium conductor cable | Sets | 0 |  |  | 0 | 0
j | 4 c x 25 sq.mm 1.1 KV grade XLPE Insulated FRLS sheathed armoured copper conductor cable | Sets | 0 |  |  | 0 | 0
k | 4 c x 16 sq.mm 1.1 KV grade XLPE Insulated FRLS sheathed armoured aluminium conductor cable | Sets | 0 |  |  | 0 | 0
l | 4 c x 16 sq.mm 1.1 KV grade XLPE Insulated FRLS sheathed armoured copper conductor cable | Sets | 20 | 123 | 38 | 2460 | 760
m | 4 c x 10 sq.mm 1.1 KV grade XLPE Insulated FRLS sheathed armoured aluminium conductor cable | Sets | 0 |  |  | 0 | 0
n | 4 c x 10 sq.mm 1.1 KV grade XLPE Insulated FRLS sheathed armoured copper conductor cable | Sets | 8 | 94 | 29 | 752 | 232
o | 4 c x 6 sq.mm 1.1 KV grade XLPE Insulated FRLS sheathed armoured copper conductor cable | Sets | 6 | 94 | 29 | 564 | 174
p | 3 c x 6 sq.mm 1.1 KV grade XLPE Insulated FRLS sheathed armoured copper conductor cable | Sets | 6 | 76 | 19 | 456 | 114
q | 3 c x 4 sq.mm 1.1 KV grade XLPE Insulated FRLS sheathed armoured copper conductor cable | Sets | 2 | 66 | 19 | 132 | 38
r | 3 c x 16 sq.mm 1.1 KV grade XLPE Insulated FRLS sheathed copper conductor cable | Sets | 10 | 94 | 29 | 940 | 290
s | 2 c x 10 sq.mm 1.1 KV grade XLPE Insulated FRLS sheathed armoured copper conductor cable | Sets | 6 | 76 | 19 | 456 | 114
t | 1c x 6 sq.mm FRLS XLPE insulated flexible copper conductor cables | Sets | 12 | 76 | 19 | 912 | 228
u | 1c x 16 sq.mm FRLS XLPE insulated flexible copper conductor cables | Sets | 30 | 76 | 19 | 2280 | 570
v | 1c x 25 sq.mm FRLS XLPE insulated flexible copper conductor cables | Sets | 0 |  |  | 0 | 0
| TOTAL CARRIED OVER TO SUMMARY |  |  |  |  | 614256 | 55866
E | RACEWAYS AND CABLE TRAYS
Note :-
1 | Fabricating supplying to site of installation, installation on ceiling/ surface 1.6 mm thick G.I raceways of height 50 mm and 1.2 mm thick openable cover, totally enclosed, the joints between two lengths of channels or between channel and junction box shall be joined together with 3 mm thick G.I coupler plates to make it dust and water proof. The cost shall including all supporting and fixing accessories including dash fasteners.
a | 250 mm (wide) x 50 mm (height) | RM | 185 | 903 | 127 | 167055 | 23495
b | 150 mm (wide) x 50 mm (height) | RM | 50 | 658 | 99 | 32900 | 4950
c | 100 mm (wide) x 50 mm (height) | RM | 110 | 546 | 85 | 60060 | 9350
d | 100 mm (wide) x 100 mm (height) | RM | 0 |  |  | 0 | 0
2 | Fabricating supplying to site of installation, Junction boxes for Ceiling raceways made from 2 mm thick, with 2.5 mm thick M.S. powder coated cover including providing neoprene gaskets between the cover and the junction box, cadmium plated flat/round head screws, height as per site condition,totally enclosed. Proper cutouts shall be made in the side walls for raceway entry wherever required. The junction box shall be all side walls should be welded expect top cover and all side walls shall have suitable size of rectangular knock out holes for taking raceways / conduits as required and not a complete cut out. The top cover should be sealed with M Seal to make it dust and water proof complete as required etc.
a | 300 mm x 300 x 60 mm (height) | Nos. | 15 | 837 | 170 | 12555 | 2550
b | 200 mm x 200 x 60 mm (height) | Nos. | 5 | 489 | 104 | 2445 | 520
c | 150 mm x 150 x 60 mm (height) | Nos. | 6 | 395 | 85 | 2370 | 510
3 | Fabricating supplying to site of installation, in floor including chase cutting of floor,leveling, refilling and making good the same from 1.6 mm thick and 2 mm thick cover GI duly galvanised, totally enclosed, height 40 mm . The two lengths of raceways shall be fitted with Collars , 50 mm wide, 3 mm thick , press fit type. The raceways shall be clamped to the floor slab with GI clamps , 3mm thick and shall be screwed to the floor slab. The joint between raceway and junction box will be made with GI flexible strip( 3 nos), 3 mm thick, 4 inches long ,15 mm wide which will be nut bolted to the Junction box complete as required etc.
a | 250 mm (wide) x 40 mm (height) | RM | 60 | 762 | 127 | 45720 | 7620
b | 150 mm (wide) x40 mm (height) | RM | 110 | 527 | 99 | 57970 | 10890
c | 100 mm (wide) x 40 mm (height) | RM | 100 | 405 | 85 | 40500 | 8500
5 | Fabricating supplying to site of installation, Junction boxes for floor raceways made from 2 mm thick, with 2.5 mm thick GI duly galvanised cover including providing neoprene gaskets between the cover and the junction box, cadmium plated flat/round head screws, height as per site condition,totally enclosed. Proper cutouts shall be made in the side walls for raceway entry wherever required. The junction box shall be all side walls should be welded expect top cover and all side walls shall have suitable size of rectangular knock out holes for taking raceways / conduits as required and not a complete cut out. The top cover should be sealed with M Seal to make it dust and water proof complete as required etc.
a | 300 mm x 300 x 50 mm (height) | Nos. | 21 | 837 | 170 | 17577 | 3570
b | 200 mm x 200 x 50 mm (height) | Nos. | 38 | 489 | 104 | 18582 | 3952
c | 150 mm x 150 x 50 mm (height) | Nos. | 35 | 395 | 85 | 13825 | 2975
d | 100 mm x 100 x 50 mm (height) | Nos. | 43 | 329 | 66 | 14147 | 2838
6 | Design manufacture , supply and fixing in position the cable trays of the following sizes for supporting 1.1 KV grade armoured/unarmoured aluminium /copper conductor cables. Fabricate the cable trays from perforated 1.6/2mm thick M.S. CRCA sheet duly galvanised with expansion coupler plates duly galvanised, with bolts, washer and nuts. Knock out holes for cable connections as per approved design. The tray should comply with the specification of NEC (National Electric Codes) and NEMA (National Electric Manufacturers Association). The steel should be as per IS:226 and galvanising as per IS :2629/BS 729/ASTM 123. The rate shall also include for supporting steel , fish plates , fixing accessories , nuts bolts, supporting down rods , dash fastener, cutting the RCC etc. complete as required. (the horizontal and vertical bends, T's should be factory fabricated and the rate should include for the same)
a | 150 mm wide x 40 mm x 1.6 mm Thickness | RM | 110 | 508 | 99 | 55880 | 10890
b | 300 mm wide x 40 mm x 1.6 mm Thickness | RM | 40 | 724 | 156 | 28960 | 6240
c | 450 mm wide x 40 mm x 2.0 mm Thickness | RM | 65 | 940 | 240 | 61100 | 15600
d | 600 mm wide x 40 mm x 2.0 mm Thickness | RM | 20 | 1157 | 268 | 23140 | 5360
e | 450 mm wide x 100 mm x 2.0 mm Thickness | RM | 0 |  |  | 0 | 0
7 | Design manufacture , supply and fixing in position the Ladder Type cable trays of the following sizes for supporting 1.1 KV grade armoured/unarmoured aluminium /copper conductor cables. Fabricate the cable trays to from Ladder Type 2.0 mm thick M.S. Flat/ Angle iron with bolts, washer and nuts. as per approved design. The tray should comply with the specification of NEC (National Electric Codes) and NEMA (National Electric Manufacturers Association). The steel should be as per IS:226 and galvanising as per IS :2629/BS 729/ASTM 123. The rate shall also include for supporting steel ,jointing fish plates , fixing accessories, nuts bolts, supporting down rods, dash fastener, cutting the RCC etc. complete as required.
a | 300 mm wide x 50 mm x 2.0 mm thk | RM | 5 | 527 | 156 | 2635 | 780
b | 600 mm wide x 50 mm x 2.0 mm thk | RM | 0 |  |  | 0 | 0
8 | Fabricating, supplying to site of installation, installation of 500 mm size of 105 mm height mesh type EZ-Electroplated Zinc ( Legrand -Cablofil make ) cable tray including threaded G.I. down rods, dash fasteners, cablofil fixing accesories etc. complete as required. Cablofil make | RM | 10 | 2350 | 217 | 23500 | 2170
9 | Supporting brackets for cable trays, switch board etc. fabricated out of MS angle, channels & flats duly painted complete with necessary hardware. | KG | 150 | 156 | 33 | 23400 | 4950
| TOTAL CARRIED OVER TO SUMMARY |  |  |  |  | 704321 | 127710
F | DISTRIBUTION BOARDS
1 | Supply,inginstalling, connecting testing and commissioning of the following double door 1/4 rows vertical type 1.6 mm thick and 1. 4 thick door sheet steel enclosed fully recessed type, TPN Miniature Circuit Breakers Distribution Boards dust proof, verm­in proof, with hinged and lockable doors complete with DP MCB's and inter-connection with copper wire , insulated copper bus bar , cable glands­/conduit entry bushes, bonding to earth and paint­ing. Also provide separate neutral busbar for each phase. Provide separate Earth Links for each phase. Use brass thimbles for connections of all wires. 1 row for single phase and 4 rows for 3 phase. Provide separate 4 way 63 A main neutral link also. The phase busbar links shall be factory pre insulated.
Note :- The IP rating of the DB should be IP 43 .
Provide DB charts in laminated sheets in all Distribution Boards
1 | Light & Power Distribution Board(All MCB's in DB's should be C Curve)
a | 6 Way TPN DB, each phase consisting of 4 Nos. 10/20 AMP SP MCB’s and controlled by one number 30 mA sensitivity 40 AMPS DP RCCB backed up with 1 no 40 Amps 4 pole MCB. | Nos | 0 |  |  | 0 | 0
b | 10 Way TPN DB, each phase consisting of 8 Nos. 10/20 AMP SP MCB’s and controlled by one number 30 mA sensitivity 63 AMPS DP RCCB backed up with 1 no 63 Amps 4 pole MCB. | Nos | 0 |  |  | 0 | 0
c | 12 Way TPN DB, each phase consisting of 10 Nos. 10/20 AMP SP MCB’s and controlled by one number 30 mA sensitivity 63 AMPS DP RCCB backed up with 1 no 63 Amps 4 pole MCB. For Lighting DB | Nos | 3 | 21150 | 1410 | 63450 | 4230
d | 14 Way TPN DB, each phase consisting of 12 Nos. 10/20 AMP SP MCB’s and controlled by one number 30 mA sensitivity 63 AMPS DP RCCB backed up with 1 no 63 Amps 4 pole MCB. For Light,Power DB | Nos | 4 | 23782 | 1692 | 95128 | 6768
e | 12 Way SPN DB, consisting of 8 Nos. 10/20 AMP SP MCB’s and controlled by one number 30 mA sensitivity 40 AMPS DP RCCB backed up with 40 Amps DP MCB. For VRV DB | Nos | 1 | 6120 | 705 | 6120 | 705
g | 12 Way SPN DB, consisting of 8 Nos. 10/20 AMP SP MCB’s and controlled by one number 30 mA sensitivity 40 AMPS DP RCCB backed up with 40 Amps DP MCB. For Emergency & Exit signage light | Nos | 2 | 6120 | 705 | 12240 | 1410
i | Fabricated Kitchen DB, consisting of 12 Nos. 32/25/20/16 AMP DP RCBO's with 4 Nos 32/25 FP RCBO and controlled by one number 100 FP MCCB. And 200 Amps 4 pole copper Bus bar , inclduing MFM and idication lamp The design of panel as approved by consultant | Nos | 0 |  |  | 0 | 0
2 | UPS Distribution Boards (All MCB's in UPS DB's should be D Curve)
a | 6 Way TPN DB, each phase consisting of 4 Nos. 10/20 AMP SP MCB’s and controlled by one number 40 AMPS DP RCCB (30 mA) for each phase and 1 no. 40 amps 4 pole MCB incomer. For Server DB | Nos. | 2 | 13724 | 1199 | 27448 | 2398
b | 10 Way TPN DB, each phase consisting of 8 Nos. 10/20 AMP SP MCB’s and controlled by one number 40 AMPS DP RCCB (30 mA) for each phase and 1 no. 40 amps 4 pole MCB incomer. | Nos. | 0 |  |  | 0 | 0
c | 12 Way TPN DB, each phase consisting of 10 Nos. 10/20 AMP SP MCB’s and controlled by one number 63 AMPS DP RCCB (30 mA) for each phase and 1 no. 63 amps 4 pole MCB incomer. For UPS DB | Nos. | 3 | 21150 | 1410 | 63450 | 4230
d | 12 Way SPN DB, consisting of 8 Nos. 10/20 AMP SP MCB’s and controlled by one number 30 mA sensitivity 63 AMPS DP RCCB backed up with 40 Amps DP MCB. For VAV DB | Nos. | 1 | 6627 | 705 | 6627 | 705
e | 14 Way SPN DB, consisting of 10 Nos. 10/20 AMP SP MCB’s and controlled by one number 30 mA sensitivity 63 AMPS DP RCCB backed up with 40 Amps DP MCB. For Tuck Shop DB & BMS DB | Nos. | 2 | 7426 | 705 | 14852 | 1410
3 | Supply, installation, testing and commissioning of sheet metal weather proof enclosure with 63 A 4P MCB . This shall include cable entry boxes both for incoming and outgoing cable) | Nos. | 1 | 2228 | 339 | 2228 | 339
4 | Supply, installation, testing and commissioning of sheet metal weather proof enclosure with 40 A 4P MCB . This shall include cable entry boxes both for incoming and outgoing cable) | Nos. | 1 | 2228 | 339 | 2228 | 339
5 | Supply, installation, testing and commissioning of sheet metal enclosure with 63 A RCBO 4P MCB. This shall include cable entry boxes both for incoming and outgoing cable) The enclosure shall be IP 44. | Nos. | 2 | 4183 | 630 | 8366 | 1260
6 | Supply, installation, testing and commissioning of sheet metal enclosure with 63 A DP MCB. This shall include cable entry boxes both for incoming and outgoing cable) . The enclosure shall be IP 42. | Nos. | 1 | 1326 | 207 | 1326 | 207
| TOTAL CARRIED OVER TO SUMMARY |  |  |  |  | 303463 | 24001
G | SUB DISTRIBUTION PANELS
LT Panels: Supply & Delivery on site of Cubical type, sheet steel enclosure 2.0 mm thick CRCA for load bearing member and partition 1.6 mm thick Aluzinc (w/o painted) , powder coated (Paint Shade: Siemens Grey), free standing indoor type extendible compartmentlized type Main LT Panel / Sub Panels with vermin proof hinged lockable doors for each compartment, bus bar interconnections for incoming and outgoing including feeders earthing and painting and as per specifications. All meters shall be digital with LED display, whereever mentioned. Energy Meters shall be dual recording (grid and DG power) and have RS 485 Modbus RTU half duplex communication interface for provision of IBMS connectivity and wired accordingly. Provide 2 NO/2NC potential free contacts wires and terminal blocks in the cable alley for IBMS operation for each DG sets, Transformer and bus coupler ACB operation status, load manager output and energy meter output TB on connection to be provided.
MLTP / Capacitor panel will have only top entry & with rear access. All other panels will have top cable entry & no rear access. Shrouding of bus bar vertical as well as horizontal and all live parts is mandatory.
Under voltage relay of all incomers of Main L.T. Panel shall have interlocking with F.A. panel so that in case of fire all panel shall be switched off automaticaly except Critical supply panel.
Vendor will have to provide technical / commissioning support to installer at site. Supply as per scope given above. & Technical Specification given below describes the desired interlocks between various incoming power sources along with operating scenarios. This should be achieved through PLC Based Control System. Provide dedicated 1KVA UPS with 10 minutes backup for powering PLC within the panel.
1 | LT PANELS & SUB DISTRIBUTION PANELS
Supplying, Receiving, Unloading, Unpacking, Shifting, Testing & Commissioning of the following Panels:
Note | Provide insulated dedicated earth link in all UPS Panels
All MCCB's 250 Amps and above shall be Microprocessor based
All Light & Power panel ,UPS and A.C. Panel incomer MCCB shall have Over current, Earth fault and short circuit protection.
All Incomer MCCB's in UPS Panels shall be microprocessor based
The microprocessor based MCCBs shall have
Over Load (Phase)
Current setting Ir(Ir=XIn) OFF 0.4 to 1.0 in steps of 0.1
Time delay , tr( Inverse) 10 sec at 6/r
Over Load (Neutral)
Current setting In (Intrl =XIr)0.5, 0.75&1.00 Intrl
Inverse 10 sec at 6 Intrl/Fixed 200ms
Short Circuit setting -2- 10
Instantaneous- 1.5-1
All MCB's in UPS Panels shall be D Curve
In all Electrical panels protective acrylic sheet to be provided in cable alley and feeders.
Outgoing meters shall be able to monitor all major power quality parameters Voltage , current , frequency , KVAH,KWH,Power factor and individual,harmonics, ethernet ready - IEC-625-22.2
Incomer meter shall Support monitoring parameters —full range of 3-phase voltage, current, power and energy measurements, power factor, frequency, total harmonic distortion (THD), individual power harmonics (up to 63rd order). Accuracy standards - use four-quadrant metering and sample current/voltage simultaneously without gaps with 128 samples per cycle (zero-blind); comply with ANSI C12.20 class 0.2 and IEC 61557-12 class 0.2 for revenue meters.
Meter shall have Waveform capture shall be available for both current and voltage waveforms. Voltage sag and swell detection with waveform capture. With a resolution of 8 cycles @ 128 cycles/ sec or more. Communications - serial RS-485 Modbus and Ethernet Modbus TCP; provide two Ethernet ports to allow wiring from meter to meter as a daisy-chain; be capable of serve data over the Ethernet network accessible through a standard web browser and on the HMI (front display); the monitor shall contain default pages from the factory.
Meter Alarming capabilities - support 29 set-point driven alarms, four (4) digital alarms, (4) unary alarms, 10 Boolean alarms and five (5) custom alarms; user definable alarm events; set-point driven alarms shall be available for voltage/current parameters, input status, and end of interval status.
Solenoid Operated ATS with AC33B utilization category, source priority selection & MODBUS port along with phase sequence protection along with genset start & stop contacts. With enclosure & extended busbar arrangements for the termination of armoured cable. Along with 50KA TPN Thermal Magnetic Based MCCB at Output. (Compatible with Communication protocol).
Provide On / Off and trip indicating lamp on main incomer only.
All MCCB breaker shall be Schneider make unless otherwise specified
Note: The breaking capacity and trip setting of the breakers shall be finalized as per the final design . The report shall be as per Etap analysis.
All MCB's Breaking Capacity shall be enhanced to 55 KA due to cascading
Provide shut trip for fire integration in the all panels. Critical & UPS panel not required.
1.1 | The SDB-1 LOC:-GROUND FLOOR shall consists of :
MAIN INCOMER
1 No. 200 A TPN MCCB (36KA/1 sec)( O/C, S/C,) and neutral isolation link 100% of rated current. Terminals suitable to receive 3.5c x 95sq. mm AL cable connection on one side and Busbar connection on the other side.
Main BUSBAR Section
300 amps TPN busbar chamber of suitable length with aluminium busbars. All busbars and interconnections shall be of suitable size aluminium strips current density of copper shall not be more than 0.8 Amps/ sq.mm.provide 50% capacity for neutral bus bar.
INDICATING PANELS
3 nos phase indicating lamps (LED type) each backed up with MCB and switch shall be provided for each incomer.
Provide on/off indication lamp on each incomer & MCCB.
Provide Intelligent Panel Meter - Schneider multifunctional meter EM-6436 NG dual with RS485 for all incoming feeder
Provide Transient Voltage Surge Suppressor Rating 40kA class II along with 100 A MCCB. Including all necessary accessories. For Switching Operation on each incomer.
OUTGOINGS
i | 4 Nos. 63 A TPN MCCB terminals to receive suitable Cable on one side and Busbar connection on the other side.
ii | 12 Nos. 63A FP MCB terminals to receive suitable Cable on one side and Busbar connection on the other side.
iii | 1 Nos. 40A 4P MCB terminals to receive suitable Cable on one side and Busbar connection on the other side.
iv | 3 Nos. 63A DP MCB terminals to receive suitable Cable on one side and Busbar connection on the other side.
v | 1 Nos. 40A 4P RCBO terminals to receive suitable Cable on one side and Busbar connection on the other side.
| The SDB-1 (L,P & AC) as described above and specifications complete | Set | 1 | 245810 | 18800 | 245810 | 18800
1.2 | THE UPS Panel SDB UPS shall consists of :
MAIN INCOMER
3 No. 63 A 4P MCCB (36KA/1 sec)( O/C, S/C,E/F) and neutral isolation link 200% of rated current. Terminals suitable to receive 4R x1Cx 16 sq. mm XLPE Cu. cable connection on one side and Busbar connection on the other side.
BUSBAR-Section
150 amps 4P busbar chamber of suitable length with Copper busbars. All busbars and interconnections shall be of suitable size copper strips current density of copper shall not be more than 1.6 Amps/ sq.mm.provide 200% capacity for neutral bus bar.
INDICATING PANELS
3 nos phase indicating lamps (LED type) each backed up with MCB and switch shall be provided for each incomer.
Provide on/off indication lamp on each incomer and MCCB.
Provide Intelligent Panel Meter - multifunctional meter EM 6436 with RS485 for all incoming feeder
Provide Transient Voltage Surge Suppressor Rating 40kA class II along with 100 A MCCB. Including all necessary accessories. For Switching Operation on each incomer.
OUTGOINGS
i | 6 Nos. 63A FP MCB terminals to receive suitable AL Arm Cable on one side and Busbar connection on the other side.
ii | 2 Nos. 63A DP MCB terminals to receive suitable AL Arm Cable on one side and Busbar connection on the other side.
| The UPS Panel SDB UPS as described above and specifications complete. | Set | 1 | 210325 | 14100 | 210325 | 14100
| TOTAL CARRIED OVER TO SUMMARY |  |  |  |  | 456135 | 32900
H | MISCELLANEOUS ITEMS
1 | The Electrical Contractor shall provide sufficient temporary lighting for working in the Building total area 17200 sq. ft. divided in 3 floor each area is approx and maintain the same till completion of the project.It shall include replacement of all fused/faulty lamps.It shall include providing 15 A plug sockets (industrial type with ON/OFF switch/MCB) on 4 sides walls one plug at every 5-8 meter distance. The Contractors will tap off supply from these plugs for his use. Tubelights to maintain a lighting level of 150 lux on the floor,.Each 15 A socket and each Light circuit shall be protected by suitable MCBs.Use three core PVC Insulated PVC sheathed copper conductor cables for wiring.The contractor shall salvage the complete wiring and take it back at the end of the project. | L.S. | 1 | 80840 | 16168 | 80840 | 16168
2 | Thermal scanning with Thermal Imaging camera, of all the cable and wiring joints in all the panels and MCB Distribution Boards after commissioning . | LS | RO |  |  | 0 | 0
3 | Providing & fixing in position 1000 mm wide, Electrical Insulating Mats as per IS 15652:2006, 2mm thick, suitable up to 1.1 KV, fire retardant,no effect of acids, alkalies and transformer oils, moisture proof, high tensile strength and texture finish / cloth impression (Anti slip, marking on top). | RM | 5 | 3008 | 470 | 15040 | 2350
4 | Supply & fixing in position approved shock treatment chart written in English, Hindi and Local language. These charts shall be framed in wooden frame & covered with clear glass. | Nos. | 1 | 1410 | 470 | 1410 | 470
5 | Supply & fixing in position the best quality danger notice boards of approved shape & size as reqd. by the local Electrical Inspecting Authority written in English, Hindi & local language. | Nos. | 1 | 1410 | 470 | 1410 | 470
6 | Supply & fixing in position the Electrical A 1 Size SLD chart in the UPS/electrical room. These charts shall be framed in wooden frame & covered with clear glass. | Nos. | 1 | 1410 | 470 | 1410 | 470
7 | Supplying the first aid box as approved by John Ambulance society. | Nos. | 1 | 1880 | 470 | 1880 | 470
8 | Automatic Fire Extinguisher for Panels - Automatic Direct Low Pressure Fire Suppression. Extinguisher and Valve for Electrical Panel, Electrical room and UPS room Panel with Clean Agent FE 36/FM 200 type fire extinguisher of 2 kgs with Pressure Switch to monitor Pressure in the tube, switch point min 11 Bars. Capacity, Tube Attachment for Heat Sensor Tube, Heat Sensor Tube for automatic fire suppression system, end of line adapter with mounting brackets and triangle type auto glow fire extinguisher sign board etc. complete confirming to IS Standards and as per technical specification with all mounting accessories complete as required. Fire extinguisher and required connectors and associated Tube of 15 mtrs and accessories connection from cylinder to the inside of the panel. | Nos. | 1 | 85000 | 9400 | 85000 | 9400
9 | Thermal Imaging to be done for all the Panels including the busbars, cable joints etc. after all the connections have been done and before and after final commissioning. | Nos. | RO |  |  | 0 | 0
| TOTAL CARRIED OVER TO SUMMARY |  |  |  |  | 186990 | 29798
| GRAND TOTAL (EXCL TAX) |  |  |  |  | 4656074 | 749430

## Functional Light Install
Project | :Inovalon
Location | : Gurugram
Title | : Functional Light Fixture Installation BOQ
S.no | Model No | Image | Description | Product Specifications | QTY | UOM | Installation Rate | Amount | Remark
Recieving, Shifting to the designated store & from store to the site floors, Installation, Testing and Commissioning of Light fixtures and lamps with all accessories, wooden blocks, screws ,hardware's, wedge clamps as required as per the site conditions (including the earthing of fixture)
Asset reconciliation shall be submitted
Any loss & damage shall be in scope of Electrical Contractor till final testing & commissioning.
Self interlocking connector blocks for connecting the wires from fixtures to the points.
Earthing of fixtures with PVC insulated copper conductor FR wire.
Approved colour powder coated down rods, clamps, 8mm wedge clamp nut with bolt washer and other components and fixing accessories wherever required.
Testing of fixtures before Installation.
The lighting lux level report to be submit while testing and commissioning.
Identification tags with a distance not more 3 meters to be used for circuit identification
1 | PBLM22364 |  | LED Base Light 2X2 Recessed Back LIT Low Depth 36W 4000K IP20 | Installation, Testing and Commissioning of recess-mounted 2x2 low height light fixture comprising CRCA powder-coated housing with a PS diffuser. The luminaire shall be suitable for general-purpose applications like offices, hospitals, software centres, and banks. The system wattage shall be maximum 36W, providing system luminous flux 3900 lumens (minimum) respectively with a luminaire efficacy of > 110 lm/W. It should have a beam angle of 120°, Correlated colour temperature options around 5700K/4000K, and CRI greater than 80. Lumen maintenance should achieve L70B50 at 50,000 hours. Electrical parameters should include 240V AC input, Power Factor > 0.95 , and THD < 10%. Driver shall be Constant Current, Non-Integral, Isolated, Withstand high voltage up to 360V AC for 2hrs, Class I Insulation Level, Operating Temperature: 0°C TO 45°C, Protection ratings shall include IP20 and IK05 with surge protection up to 3kV. should be of same make & must have separate BIS approval. Luminaire manufacture shall provide LM79 report from in house NABL accredited lab & LM80 report issued by LED manufacturer. CAT NO: PBLM22364 PANASONIC or equivalent | 55 | Nos | 300 | 16500
2 | PDLM35154 |  | LED Down Light AL Circular Recessed 15W 4000K IP20 | Installation, Testing and Commissioning of aluminium recessed-mounted round down light comprising powder-coated die-cast aluminium housing with PS diffuser and stainless steel springs. The luminaire shall be suitable for offices, classrooms, shops, reception areas, and meeting rooms. It shall have wattage 15W, providing system luminous flux 1700 lumens (minimum) respectively with luminous efficacy of > 115 lm/W and correlated colour temperature options around 5700K/6500K/4000K. CRI shall be greater than 80 with beam angle at 120°. Lumen maintenance should achieve L70B50 at 50,000 hours. Diameter of 165mm & Height 53mm. Electrical parameters should include 240V AC input, Power Factor > 0.90 , and THD < 10%. Driver shall be Constant Current, Non-Integral, Isolated, Withstand high voltage up to 360V AC for 2hrs, Class I Insulation Level, Operating Temperature: 0°C TO 45°C, Protection ratings shall include IP20 and IK05 with Built-in Surge protection up to 4kV. should be of same make & must have separate BIS approval. Internal wiring should have PVC/Teflon coated multistrand wire. Luminaire manufacture shall provide LM79 report from in house NABL accredited lab & LM80 report issued by LED manufacturer. CAT NO: PDLM35154 PANASONIC or equivalent | 120 | Nos | 250 | 30000
3 | PDLM58184 |  | LED Down Light Surface Rimless Round 18W 4000K IP20 | Installation, Testing and Commissioning of Surface-mounted down light comprising of die cast aluminum housing white powder coated, PC molded diffuser suitable for Surface mounting arrangement. The luminaire shall be suitable for offices, classrooms, shops, reception areas, and meeting rooms.It shall have wattage 18W, providing system luminous flux 2000 lumens (minimum) respectively with luminous efficacy of > 120 lm/W and correlated colour temperature options around 5700K/6500K/4000K. CRI shall be greater than 80 with beam angle at 120°. Lumen maintenance should achieve L70B50 at 50,000 hours. Diameter of 170mm & Height 50mm, Electrical parameters should include 240V AC input, Power Factor > 0.95 , and THD < 10%. Driver shall be Constant Current, Non-Integral, Isolated, Withstand high voltage up to 360V AC for 2hrs, Class I Insulation Level, Operating Temperature: 0°C TO 45°C, Protection ratings shall include IP20 and IK02 with Built-in Surge protection up to 4kV. Should be of same make & must have separate BIS approval. Internal wiring should have PVC/Teflon coated multistrand wire. Luminaire manufacture shall provide LM79 report from in house NABL accredited lab & LM80 report issued by LED manufacturer. CAT NO: PDLM58184 PANASONIC or equivalent | 41 | Nos | 250 | 10250
4 | PLHM10284 |  | LED Suspended Fixture Linear Down Type 4ft Stand Alone 28W 4000K IP20 | Installation, Testing and Commissioning of Suspended Linear Light Stand alone 4 feet comprising of Aluminium Extrusion with PMMA Sliding Diffuser, PC End Caps and Clutch Wire Suspension Kit for Mounting arrangement. The luminaire shall be suitable for Offices, meeting rooms, cabins etc. The system wattage shall be maximum 28W, providing system luminous flux 3080 lumens respectively with a luminaire efficacy of > 110 lm/W. The luminaire shall have a beam angle of 120°, Correlated colour temperature of 5700K/4000K and CRI ≥80. Lumen maintenance should achieve L70B50 at 50,000 hours. Electrical parameters should include 240V AC input, Power Factor > 0.95, and THD < 10%. Driver shall be Constant Current, Isolated, Non Integral, Withstand high voltage up to 440V AC for 2hrs, Class I Insulation Level, Operating Temperature: 0° C TO 45° C, Protection ratings shall include IP20 and IK05 with Internal surge protection up to 3kV shall be provided. should be of same make & must have separate BIS approval. Luminaire manufacture shall provide LM79 report from in house NABL accredited lab & LM80 report issued by LED manufacturer. CAT NO: PLHM10284 PANASONIC or equivalent | 31 | Nos | 350 | 10850
5 | PDLM18124 |  | Cylindrical Downlight Suspended Mount 12W 4000K IP20 | Installation, Testing and Commissioning of Circular Cylindrical shaped Suspended mounted down light comprising of Aluminium Housing Matt powder coated in black, Special translucent diffuser used for better lighting distribution and Suspension Kit for Suspended Mounting arrangement. It shall have wattage 12W providing luminous efficacy of 85 lm/W and correlated colour temperature options around 5700K/4000K. CRI shall be greater than 80 with beam angle at 120°. Lumen maintenance should achieve L70B50 at 50,000 hours. Electrical parameters should include 240V AC input, Power Factor > 0.90 , and THD < 10%. Driver shall be Constant Current, Integral, Non-Isolated, Withstand high voltage up to 360V AC for 2hrs, Class I Insulation Level, Operating Temperature: 0°C TO 45°C, Protection ratings shall include IP20 and IK02 with Built-in Surge protection up to 2.5kV. Should be of same make & must have separate BIS approval. Internal wiring should have PVC/Teflon coated multistrand wire. Luminaire manufacture shall provide LM79 report from in house NABL accredited lab & LM80 report issued by LED manufacturer. CAT NO: PDLM18124 PANASONIC or equivalent | 79 | Nos | 300 | 23700
6 | PBTM24104 |  | Led Mirror 10W batten 4000K IP20 | Installation, Testing and Commissioning of surface mounted 2 feet length LED Batten for Mirror Light with PC housing with PC Diffuser with engg-plastic end caps and Clamps for Surface Mounting arrangement with groove inside for PCB. LED populated on PCB comprising of LED’s connected. The luminaire shall be suitable for offices, factories, warehouses areas. The system wattage shall be 10W, providing system luminous flux 1000 lumens respectively with a luminaire efficacy of > 100 lm/W. The fixture shall have a beam angle of 120°, Correlated colour temperature of 6500K/5700K and CRI ≥80. Lumen maintenance should achieve L70B50 at 25,000 hours. Electrical parameters should include 240V AC input, Power Factor > 0.90, and THD < 20%. Driver shall be Constant Current, Non-Isolated, Integral, Class II Insulation Level, Operating Temperature: 0° C TO 45° C, Protection ratings shall include IP20 and IK02 with Internal surge protection up to 3kV shall be provided. should be of same make & must have separate BIS approval. Luminaire manufacture shall provide LM79 report from in house NABL accredited lab & LM80 report issued by LED manufacturer. CAT NO: PBTM24104 PANASONIC or equivalent | 16 | Nos | 150 | 2400
7 | PLRM04104 |  | LED Recessed Fixture Linear Down Type 2ft Continues 10W 4000K IP20 | Installation, Testing and Commissioning of Recessed Linear Light 2 feet length suitable for continuous arrangement to be cascaded along with Loop In/Loop out electrical connections comprising of Aluminium Extrusion with PMMA Diffuser, Aluminium End Caps and SS Clamps for Mounting arrangement. The luminaire shall be suitable for Offices, meeting rooms, cabins etc. The system wattage shall be maximum 10W, providing system luminous flux 1250 lumens (minimum) respectively with a luminaire efficacy of > 125 lm/W. The luminaire shall have a beam angle of 120°, Correlated colour temperature of 5700K/4000K and CRI ≥80. Lumen maintenance should achieve L70B50 at 50,000 hours. Electrical parameters should include 240V AC input, Power Factor > 0.95, and THD < 10%. Driver shall be Constant Current, Isolated, Non Integral, Withstand high voltage up to 440V AC for 2hrs, Class I Insulation Level, Operating Temperature: 0° C TO 45° C, Protection ratings shall include IP20 and IK05 with Built-in Surge protection up to 3kV shall be provided. should be of same make & must have separate BIS approval. Internal wiring should have PVC/Teflon coated multistrand wire. Luminaire manufacture shall provide LM79 report from in house NABL accredited lab & LM80 report issued by LED manufacturer. CAT NO: PLRM04104 PANASONIC or equivalent | 16 | Nos | 350 | 5600
8 | PLRM04184 |  | LED Recessed Fixture Linear Down Type 4ft Continues 18W 4000K IP20 | Installation, Testing and Commissioning of Recessed Linear Light 4 feet length suitable for continuous arrangement to be cascaded along with Loop In/Loop out electrical connections comprising of Aluminium Extrusion with PMMA Diffuser, Aluminium End Caps and SS Clamps for Mounting arrangement. The luminaire shall be suitable for Offices, meeting rooms, cabins etc. The system wattage shall be maximum 18W, providing system luminous flux 2400 lumens (minimum) respectively with a luminaire efficacy of > 125 lm/W. The luminaire shall have a beam angle of 120°, Correlated colour temperature of 5700K/4000K and CRI ≥80. Lumen maintenance should achieve L70B50 at 50,000 hours. Electrical parameters should include 240V AC input, Power Factor > 0.95, and THD < 10%. Driver shall be Constant Current, Isolated, Non Integral, Withstand high voltage up to 440V AC for 2hrs, Class I Insulation Level, Operating Temperature: 0° C TO 45° C, Protection ratings shall include IP20 and IK05 with Built-in Surge protection up to 3kV shall be provided. should be of same make & must have separate BIS approval. Internal wiring should have PVC/Teflon coated multistrand wire. Luminaire manufacture shall provide LM79 report from in house NABL accredited lab & LM80 report issued by LED manufacturer. CAT NO: PLRM04184 PANASONIC or equivalent | 4 | Nos | 350 | 1400
9 | PLHM09184 |  | LED Suspended Fixture Linear Down Type 4ft Continues 18W 4000K IP20 | Installation, Testing and Commissioning of Suspended Linear Light 4 feet length suitable for continuous arrangement to be cascaded along with Loop In/Loop out electrical connections comprising of Aluminium Extrusion with PMMA Sliding Diffuser, PC End Caps and Clutch Wire Suspension Kit for Mounting arrangement. The luminaire shall be suitable for Offices, meeting rooms, cabins etc. The system wattage shall be maximum 18W, providing system luminous flux 2250 lumens (minimum) respectively with a luminaire efficacy of > 110 lm/W. The luminaire shall have a beam angle of 120°, Correlated colour temperature of 5700K/4000K and CRI ≥80. Lumen maintenance should achieve L70B50 at 50,000 hours. Electrical parameters should include 240V AC input, Power Factor > 0.95, and THD < 10%. Driver shall be Constant Current, Non Isolated, Integral, Withstand high voltage up to 440V AC for 2hrs, Class II Insulation Level, Operating Temperature: 0° C TO 45° C, Protection ratings shall include IP20 and IK05 with Built-in Surge protection up to 3kV shall be provided. should be of same make & must have separate BIS approval. Internal wiring should have PVC/Teflon coated multistrand wire. Luminaire manufacture shall provide LM79 report from in house NABL accredited lab & LM80 report issued by LED manufacturer. CAT NO: PLHM09184 PANASONIC or equivalent | 128 | Nos | 350 | 44800
10 | PLHM09104 |  | LED Suspended Fixture Linear Down Type 2ft Continues 10W 4000K IP20 | Installation, Testing and Commissioning of Suspended Linear Light 2 feet length suitable for continuous arrangement to be cascaded along with Loop In/Loop out electrical connections comprising of Aluminium Extrusion with PMMA Sliding Diffuser, PC End Caps and Clutch Wire Suspension Kit for Mounting arrangement. The luminaire shall be suitable for Offices, meeting rooms, cabins etc. The system wattage shall be maximum 10W, providing system luminous flux 1125 lumens (minimum) respectively with a luminaire efficacy of > 110 lm/W. The luminaire shall have a beam angle of 120°, Correlated colour temperature of 5700K/4000K and CRI ≥80. Lumen maintenance should achieve L70B50 at 50,000 hours. Electrical parameters should include 240V AC input, Power Factor > 0.95, and THD < 10%. Driver shall be Constant Current, Non Isolated, Integral, Withstand high voltage up to 440V AC for 2hrs, Class II Insulation Level, Operating Temperature: 0° C TO 45° C, Protection ratings shall include IP20 and IK05 with Built-in Surge protection up to 3kV shall be provided. should be of same make & must have separate BIS approval. Internal wiring should have PVC/Teflon coated multistrand wire. Luminaire manufacture shall provide LM79 report from in house NABL accredited lab & LM80 report issued by LED manufacturer. CAT NO: PLHM09104 PANASONIC or equivalent | 57 | Nos | 350 | 19950
11 | PACM10004 |  | End Cap | End Cap Accessory suitable for mounting with Linear Suspended Luminaire CAT NO: PACM10004 PANASONIC or equivalent | 74 | Nos | 150 | 11100
12 | PACM10005 |  | Suspension wire | Suspension wire in Stainless Steel suitable for suspension of Linear Suspended Luminaire CAT NO: PACM10005 PANASONIC or equivalent | 185 | Nos | 150 | 27750
13 | PACM10006 |  | Joinery kit | Joinery kit suitable for mounting with Linear Suspended Luminaire CAT NO: PACM10006 PANASONIC or equivalent | 130 | Nos | 150 | 19500
14 | PACM10007 |  | AC Power Supply | AC Power Supply suitable for mounting with Linear Suspended Luminaire CAT NO: PACM10007 PANASONIC or equivalent | 37 | Nos | 4000 | 148000
15 |  |  |  | Supply & installation of Passive infra-red presence detector for lighting control to set the parameters of all meeting rooms and cabin (ON/OFF selection of lights) ( Lights switch OFF in steps of 1 minute) | 85 | Nos | 4000 | 340000
16 |  |  |  | Supply, installation, testing commissioning of recessed ceiling mounted photo cell switching units to provide ON/OFF switching of lighting in response to ambient light levels. | 22 | Nos | 300 | 6600
Switches lighting OFF when sufficient daylight is present.
Used as on ON/OFF daylight dependant switch or in series with a wall switch
|  |  |  | GRAND TOTAL |  |  |  | 718400
Option-2 for board room with japan tech product
17 | KPGL0112 554NW |  | Led Float Linear Suspended light fixture 25W 4000K IP20 | Installation, Testing and Commissioning of LGP based suspended Standalone Electronic Switchable 25W linear Luminaire with LGP optic complete with built in micro lens. The LGP should be made from high quality PMMA and should be UL94 certified. Test report for UL94 should be submitted with the technical document. LGP shall be designed such a way that is able to give more volumetric light & higher vertical illumination. The required nominal system lumen output of 2875 lumens at 4000K with Downward light output and a minimum system lumen efficacy of ≥ 115 lm/W. The driver should be integrated within the luminaire and should be maintainable from top. The luminaire shall have a colour temperature of 3000K / 4000K / 5000K and CRI (Ra) ≥ 80 and SDCM < 3. The luminaire shall be made up of extruded aluminium with screwless end cap. Reflector should made from CRCA Reflector with high reflectivity power coating. The light source should not be visible at all. Fixture should be of IP20 Rating with THD ≤ 10% and PF ≥ 0.90. Built in driver Surge protection of 4KV (DM & CM) should be provided in the fixture. Complete fixture should be RoHS compliant and suitable for Green building application. All accessories including screws, terminations etc should be made from Non corrosive, Stainless steel SS 304 grade. All internal wiring should be from LSZH (Low smoke Zero halogen) wires only. Test certificate should be submitted during technical submission. The complete fixture should be warranted for L70 B50 life of 50000Hrs @ 25 degree C. The LM80 report should be submitted for testing of minimum 10,000 hours. Recommended LED make - Nichia, Lumileds/ Osram only. The driver should be flicker free and the ripple should be less than 5%. The LED driving current should be less than 50% of the maximum current to ensure driver life of more than 50000 burning hours. Driver efficiency should be more than 85%. The driver should withstand high voltage upto 360V AC for 2 hours. The total Power Consumption should not exceed 25 W (including Driver). Operating voltage should be 180-264V / 50Hz. CAT NO: FLOAT Linear Suspended Single LGP Linear Light 25W Electronic PANASONIC make or equivalent | 8 | Nos | 450 | 3600 | Option-2 for board room with japan tech product
18 | KRLD0201 534NW |  | Japan tech Soft LED Down Light AL Circular Recessed 11W 4000K IP20 | Installation, Testing and Commissioning of LED based recessed mounted circular shaped downlight standalone Electronic Switchable 11W Luminaire with minimum system efficacy of 100 lm/W offering a nominal luminous flux of 1100 Lumens with beam angle of 70 degree complete with specially designed cone shape reflector which integrates with the ceiling and makes the fixture disappear. Diffuser should be made from high quality PMMA. The driver should be non integral & provided with individual luminaire. The luminaire shall have a colour temperature of 3000K / 4000K / 5000K and Ra>= 80 with SDCM <3. The luminaire shall be made up of Spun Aluminium Reflector with high reflectivity power coating along with Die cast Aluminium Heat Sink. Fixture should be of IP20 Rating with THD ≤ 10% and PF ≥ 0.90. Built in driver Surge protection of 4KV (DM & CM) should be provided in the fixture. Dimensions of the luminaire should be Dia Ø170mm and Height 113mm. Complete fixture should be RoHS compliant and suitable for Green building application. All accessories including screws, terminations etc should be made from Non corrosive, Stainless steel, SS 304 grade. All internal wiring should be from LSZH (Low smoke Zero halogen) wires only. Test certificate should be submitted during technical submission. The complete fixture should be warranted for L70 B50 life of 50000Hrs @ 25 degree C. The LM80 report should be submitted for testing of minimum 10,000 hours. Recommended LED make - Nichia, Lumileds/ Osram only. The driver should be flicker free and the ripple should be less than 5%. The LED driving current should be less than 50% of the maximum current to ensure driver life of more than 50000 burning hours. Driver efficiency should be more than 85% . The driver should withstand high voltage upto 360V AC for 2 hours. The total Power Consumption should not exceed 11 W (including Driver). Operating voltage should be 140-270V / 50Hz. CAT NO: SoftLight Recessed Downlight 11W Electronic PANASONIC make or equivalent | 8 | Nos | 450 | 3600
|  |  |  | TOTAL FOR BOARD ROOM OPTION-2 |  |  |  | 7200

## Deco Light Install
Project | :Inovalon
Location | : Gurugram
Title | : Functional Light Fixture Installation BOQ
S.no | Description | QTY | UOM | Reference Image | Installation Rate | Amount | Remark
Recieving, Shifting to the designated store & from store to the site floors, Installation, Testing and Commissioning of Light fixtures and lamps with all accessories, wooden blocks, screws ,hardware's, wedge clamps as required as per the site conditions (including the earthing of fixture)
Asset reconciliation shall be submitted
Any loss & damage shall be in scope of Electrical Contractor till final testing & commissioning.
Self interlocking connector blocks for connecting the wires from fixtures to the points.
Earthing of fixtures with PVC insulated copper conductor FR wire.
Approved colour powder coated down rods, clamps, 8mm wedge clamp nut with bolt washer and other components and fixing accessories wherever required.
Testing of fixtures before Installation.
The lighting lux level report to be submit while testing and commissioning.
Identification tags with a distance not more 3 meters to be used for circuit identification
Installation, testing & commissioning of light fixture complete with Electronic or Dali ballast as specified below for cold start, holders, louvers, inter connecting wires, terminals, lamps, etc., complete Erection with supporting hardware.
1 | Linear Light Type Size -1200mm(L)X75 mm(W) At Cafeteria & Exe. Cabin Area. | Nos | 30 |  | 350 | 10500
2 | Designer Light Type-01 Size -1200mm Dia, 75 mm wide At Reception, Lounge & Workpoint Area | Nos | 2 |  | 350 | 700
3 | Designer Light Type-01 Size -400mm Dia, At Collabs Area | Nos | 6 |  | 350 | 2100
4 | Designer Light Type-04 Size -450mm Dia, At Cafeteria Area | Nos | 3 |  | 350 | 1050
5 | Designer Light Type-06 Size -450mm Dia, At Tuck Shop | Nos | 3 |  | 350 | 1050
6 | Designer Wall Light Type Size -300mm Dia, At Cafeteria | Nos | 2 |  | 350 | 700
7 | Stretch Fabric Light Type Area -8.60 Sq.ft At Reception & Lounge Area | Nos | 1 |  | 600 | 600
| GRAND TOTAL |  |  |  |  | 16700

## Approved make list
Project | :Inovalon
Location | : Gurugram
Title | : Approved make list
Electrical, IT & UPS
No | Item | Make / Brand
1 | MS. Conduits | AKG / BEC / NIC
2 | M.S. accessories | AKG / BEC / NIC
3 | FRLS P.V.C. conduits and accessories | National / Universal / Precision
4 | FRLS P.V.C. insulated copper conductor wires 1100 volts grade | Power-Flex / Polycab / Varsha
5 | FRLS PVC insulated Aluminium/copper conductor armoured cables of 1100 V grade | Power-Flex / Polycab / Varsha
6 | FRLS PVC insulated flexible copper conductor cables of 1100 volt grade | Power-Flex / Polycab / Varsha
7 | FRLS PVC insulated Twisted / shielded / Fire survival Copper L.V. Cable | Power-Flex / Polycab / Varsha
8 | MCCB,s and Accessories | Schneider / Legrand / ABB
9 | Miniature circuit breakers/RCCBs/ DB | Schneider / Legrand / ABB
10 | Switches sockets | Legrand / Panasonic (Anchor Roma)
11 | Floor Box | Legrand / MK India
12 | G.I. Pipe | Tata / Jindal
13 | Cable Glands | HMI / Dowells
14 | Cable Lugs | HMI / Dowells
15 | Indicating Lamps | L&T / Techno / Minilec
16 | Terminals | Elmex / Schneider
17 | Energymeter | Secure / Rishabh / Elmeasure
18 | SPD (Surge Protection Device) | Mersen / Zotup / Emerson
19 | Industrial socket outlet & top | Scame / Legrand / Neptune
20 | Maintenance Free Earthing | Ashlok / Indelec
21 | Cable Tray | Cable-Tech / Pushpak / Profab
22 | Raceway – with sheet steel | Cable-Tech / Pushpak / Profab
23 | Electrical panels / Distribution Boards | Powerflow controls / Pace-switchgear / S.V Karanth
24 | Presence sensor with PIR / Ambient Sensor | Legrand / MK
25 | UPS Units | Make / Brand
26 | Battery | Delta
27 | Isolation Transformer | Datson / Magnetic / KryKard