## HVAC SUMMARY
PROJECT | TS-T2- WEX - BANGLORE
SUB | SUMMARY
Sl. No. | DESCRIPTION | Amount
|  | Supply | Installation | Total
LOW SIDE WORK
C | INSTALLATION OF CHW AHU , FCU & PIPING WORK | 0 | 0 | 0
D | SHEET METAL WORK & AIR TERMINATION | 0 | 0 | 0
E | INSULATION WORK | 0 | 0 | 0
F | TOTAL OF VRF WORK | 0 | 0 | 0
G | ELECTRICAL WORK | 0 | 0 | 0
H | TOTAL OF VAV WORKS -01 | 0 | 0 | 0
I | TOTAL OF VAV WORKS -02 | 0 | 0 | 0
| TOTAL HVAC OF LOW SIDE WORK | 0 | 0 | 0
| GST @18% | 0 | 0 | 0
| GRAND TOTAL WITH GST ( LOW SIDE WORK) | 0 | 0 | 0

## HVAC LOW SIDE
PROJECT | TS-T2 - WEX- BANGLORE
Sl. No. | DESCRIPTION | Office | COMMON AREA | TOTAL | Unit | Rate |  | AMOUNT
|  | QTY |  |  |  | SUPPLY | INSTALLATION | SUPPLY | INSTALLATION
A | CHW AHU /CASSETTE/HIWALL & PIPING WORKS
1 | Installation, testing & commissioning of Floor mounted AHU (Double Skin) as per specification
Fan section with DIDW type centrifugal impeller with the motor shall be permanent magnet external rotor motor with integrated electronics and suitable for continuous operation, Chilled water coils of copper tube and aluminum fins construction section with six rows deep having 12-13 FPI with coil face velocity of 500 FPM, Filter section with synthetic fiber filters in corrugated shape rated for filter face velocity 500 FPM Prefilter, & MERV 13 Rating filters.IE-3 motor (inside AHU casing), , spring mounted vibration Isolators, Limit Switch, Emergency Light, UV Emitter section with UVC Lamps, Guard for Inspection Door. AHU motor should be minimum IE3 grade along with the necessary controller hosed in a panel. The internal wiring between the limit switches,without UV lamp & interlock to be part of AHU vendor scope. Fan Vendor should also provide the BacNet card for each AHU for BMS integration.
The air-handling units shall be as per specifications with extruded aluminum framework having panels with outer pre-plasticised 0.6mm G.I / Galvalume sheets & inner plain 0.6mm GI / Galvalume sheet having injected 23- 25 mm PUF of 38 -kg/Cum density in between. The drain pan shall be of 18 G SS with 13mm thick nitrile rubber insulation. The frame for AHU shall be extruded aluminum. The entire AHU shall be mounted on GI base of min 70mm.
Drain pan: 1.2 mm thick SS304 with 25mm Nitrile rubber sandwiched. Provide 40 mm SS threaded drain nipple.
Dampers: Al. anodized low leakage aerofoil.
Filter section: With Prefilter , Non-Combustible Filter, access doors filters in extruded al. box type frames with gasket arrangements around filter frames. This should include one set of commissioning filters
Coil Section: Cu coils with hydrophilic coated al. fins,6 Row coil , CHW COIL
Fan section: Centrifugal fans with access doors on both sides, inspection windows, limit switch to shut off fan on door opening, Emergency Light,UV Emitter section with UVC Lamp, VFD Starter Panel & cabling from control to fans shall be scope of HVAC VENDOR.
Drive: IE-3 motor
Vibration Isolators: For fans and mounting arrangements - Rust resistant spring
Flexible connectors: Non flammable, weather and fungus proof
| FLOOR MOUNTED ESP-40 mm |  |  | 0 |  |  |  | 0 | 0
1.1 | 16000 CFM with VFD & bypass starter |  |  | 0 | Nos |  |  | 0 | 0
1.2 | 12000 CFM with bypass starter |  |  | 0 | Nos |  |  | 0 | 0
|  |  |  | 0 |  |  |  | 0 | 0
1.3 | CEILING SUSPENDED AHU ESP 25 mm |  |  | 0 |  |  |  | 0 | 0
| 12000 CFM with starter Panel |  |  | 0 | Nos |  |  | 0 | 0
|  |  |  | 0 |  |  |  | 0 | 0
|  |  |  | 0 |  |  |  | 0 | 0
1.4 | CEILING SUSPENDED AHU ESP 20 mm |  |  | 0 |  |  |  | 0 | 0
| 4400 CFM/20.0 TR with starter Panel |  |  | 0 | Nos |  |  | 0 | 0
|  |  |  | 0 |  |  |  | 0 | 0
1.3 | DECORATIVE WALL MOUNTED FAN COIL UNITS |  |  | 0 |  |  |  | 0 | 0
| Installation, Testing, Commissioning of Decorative High Wall Mounted type Chilled Water based Fan Coil Units with energy efficient 3 speed motor, ABS plastic decorative casing, Low noise fan-motor combination, Synthetic washable filter, Semi Circular Chilled Water Cooling Coil & aluminium fins with corrossion resistant coating blue or golden, minimum 13 FPI, Copper tubes minimum 7mm dia, multi step design Coil section with minimum 2 Rows, an in-built factory fitted 2 way On/ Off control valve of minimum PN16 rating duly connected and wired, with combination of pair of brass ball valve with "Y" strainer set fixed outside FCU, flexible pipe/hose with required couplings to fit CHW field In/Out piping; All piping are to be insulated with closed cell elastomeric rubber insulation. Unit shall be equipped with self diagnostic function, temperature display and supplied with Digital Display type cordless remote with 3 speed fan switch & Temp Edit facility & Digital Temp Display, supplied with relevant power supply cable from nearest point to to FCU as required. Inbuilt BMS provision in the units, no additional equipments should be required for Backnet IP connectivity |  |  | 0 |  |  |  | 0 | 0
| 2.0 TR (Hub room & IT Room) |  |  | 0 | Nos |  |  | 0 | 0
| 1.6 TR (UPS room) |  |  | 0 | Nos |  |  | 0 | 0
| 1.0 TR (Battery room) |  |  | 0 | Nos |  |  | 0 | 0
| 1.0 TR (IT STORE room ) |  |  | 0 | Nos |  |  | 0 | 0
|  |  |  | 0 |  |  |  | 0 | 0
1.4 | HIGH STATIC DUCT FAN COIL UNIT ( FCU ) |  |  | 0 |  |  |  | 0 | 0
| Supply, installation, testing and commissioning of ceiling concealed type High Static Duct type Fan Coil Units, Eurovent Certified, single skin, draw through type with minimum 3 speed fan motor, minimum 3 row chilled water coil, with Al fins with corrossion resistant coating blue or gold, metallic centrifugal blower, washable filter minimum 20 micron, insulated enclosed double skin drain tray, hanging rods and accessories, copper piping connections, etc. of the following capacities. Starter panel with necessary controls, incoming cable from starter panel to unit, connected with Pressure Independent Control cum Balancing Valve DN25, with minimum 24V Modulating Actuators IP54 with 0-10VDC control, Digital Thermostat with Modbus connectivity, Fire retardant canvass connections with GI powdercoated finish angle flanges on both sides, etc. Additional auxillary tray should accommodate all valves as per the specifications and approved drawings. The external static pressure shall be as per specifictions below. he unit shall have provision for complete control and monitoring over BMS using Modbus/ Bacnet protocol, additional items and controllers if required shall also be provided. |  |  | 0 |  |  |  | 0 | 0
| 3.0 TR ( Server Room) |  |  | 0 | Nos |  |  | 0 | 0
|  |  |  | 0 |  |  |  | 0 | 0
2 | Insulated chilled water piping, MS heavy duty 'C' Class (as per IS 1239 - Part I 2004) complete with bends, elbows, tees, vibration isolators, hangers, full round PU / rubber supports insulated with 25mm Thick Nitrile Rubber Insulation with 7 mil Cloth Pipe thickness: 6.3 mm thick for 200 - 250 dia pipes 8 mm thick for 300 - 350 dia pipes 10 mm thick for 400 - 600 dia pipes 12 mm thick for 650 - 1000 dia pipes Insulation thickness exposed to sun - 75 mm |  |  | 0 |  |  |  | 0 | 0
2.1 | 80mm dia |  |  | 0 | Rmt |  |  | 0 | 0
2.2 | 50mm dia |  |  | 0 | Rmt |  |  | 0 | 0
2.3 | 32mm dia |  |  | 0 | Rmt |  |  | 0 | 0
2.4 | 25mm dia |  |  | 0 | Rmt |  |  | 0 | 0
|  |  |  | 0 |  |  |  | 0 | 0
3 | Supply, Installation, Testing and commissioning of AHU Manifold including all valves and accessories |  |  | 0 |  |  |  | 0 | 0
3.1 | 80mm dia |  |  | 0 | Nos |  |  | 0 | 0
3.2 | 50mm dia |  |  | 0 | Nos |  |  | 0 | 0
3.3 | 40mm dia |  |  | 0 | Nos |  |  | 0 | 0
3.4 | 32mm dia |  |  | 0 | Nos |  |  | 0 | 0
3.5 | 25mm dia |  |  | 0 | Nos |  |  | 0 | 0
|  |  |  | 0 |  |  |  | 0 | 0
4 | Supply, Installation, Testing and commissioning of Insulated Butterfly Valves with flanges, gaskets, bolts etc. |  |  | 0 |  |  |  | 0 | 0
4.1 | 80mm dia |  |  | 0 | Nos |  |  | 0 | 0
4.2 | 50mm dia |  |  | 0 | Nos |  |  | 0 | 0
4.3 | 40mm dia |  |  | 0 | Nos |  |  | 0 | 0
4.4 | 32mm dia |  |  | 0 | Nos |  |  | 0 | 0
4.5 | 25mm dia |  |  | 0 | Nos |  |  | 0 | 0
|  |  |  | 0 |  |  |  | 0 | 0
5 | Supply, Installation, Testing and commissioning of Insulated balancing type control-cum-balancing valves complete with flanges measuring ports etc. |  |  | 0 |  |  |  | 0 | 0
5.1 | 50mm dia |  |  | 0 | Nos |  |  | 0 | 0
5.2 | 40mm dia |  |  | 0 | Nos |  |  | 0 | 0
5.3 | 32mm dia |  |  | 0 | Nos |  |  | 0 | 0
5.4 | 25mm dia |  |  | 0 | Nos |  |  | 0 | 0
|  |  |  | 0 |  |  |  | 0 | 0
|  |  |  | 0 |  |  |  | 0 | 0
6 | Supply, Installation, Testing and commissioning of I BTU meter with all necessary flanges etc Complete with PIPE SPOOL piece. |  |  | 0 |  |  |  | 0 | 0
6.1 | 80mm dia |  |  | 0 | Nos |  |  | 0 | 0
6.2 | 50mm dia |  |  | 0 | Nos |  |  | 0 | 0
6.3 | 32mm dia |  |  | 0 | Nos |  |  | 0 | 0
6.4 | 25mm dia |  |  | 0 | Nos |  |  | 0 | 0
|  |  |  | 0 |  |  |  | 0 | 0
|  |  |  | 0 |  |  |  | 0 | 0
| Total of CHW AHU /CASSETTE/HIWALL & PIPING WORKS | [6 empty] | 0 | 0
B | SHEET METAL WORK & AIR TERMINATION |  |  | 0
0
1 | DUCTING , INSULATION WORKS & AIR TERMINALS |  |  | 0
| Rectangular Duct : Galvanizing shall be Class VIII – light coating of zinc, nominal 120 gsm / sqm surface area and Lock Forming Quality prime material alongwith mill test certificates. In addition, if deemed necessary, samples of raw material, selected at random by owner’s site representative shall be subject to approval and tested for thickness and zinc coating at contractor’s expense. |  |  | 0
| All duct construction and installation shall be in accordance with SMACNA standards. In addition ducts shall be factory fabricated utilizing the following machines to provide the requisite quality of ducts. |  |  | 0
| The ducts shall be provided with Stiffner rods & Guide vanes for the ducts more than 800 mm |  |  | 0
| All ducts shall be fabricated and installed in workmanlike manner, conforming to relevant SMACNA codes. |  |  | 0
| The Duct shall be supported with specified Supports at regular intervalas as mentioned in the technical specifications. The sheet metal ducting running inside AHU Rooms& near AHU rooms should be supported with special acoustic hangers to avoid transmission of vibaration from AHU Room to adjacent sensitive areas. The insulation executed on the ducts inside the AHU Room shall be further finished with fiber glass cloth for mechanical protection.(To ensure the air tightness, all ducts shall be checked with Smoke Test after completion of installation but before applying insulation) |  |  | 0 |  |  |  | 0 | 0
1.1 | 24 gauge galvanized sheet steel TDF flanges (0.63mm) (0-750mm) | 65 | 40 | 105 | Sqm |  |  | 0 | 0
1.2 | 22 gauge galvanized sheet steel /TDF flanges(0.80mm) (751-1200mm) | 65 | 40 | 105 | Sqm |  |  | 0 | 0
1.3 | 20 gauge galvanized sheet steel /TDF flanges(1.00mm)(1201-1800mm) | 90 | 25 | 115 | Sqm |  |  | 0 | 0
0
|  |  |  | 0 |  |  |  | 0 | 0
2 | Supply & applying of spray painting for exposed rectangular & Elliptical ducts(colour will be confirmed by PMC/ARCH at later date) -2 coats of primer to be considered as first level. Further based on finalized color one set of painting to be done. And final coat to be applied, including support painting. | 350 | 25 | 375 | Sqm |  |  | 0 | 0
|  |  |  | 0 |  |  |  | 0 | 0
3 | FACTORY FABRICATED POWDER COATED SPIRAL ELLIPTICAL/OVAL DUCTS |  |  | 0 |  |  |  | 0 | 0
| ELLIPTICAL / SPIRAL OVAL DUCTS (internal 9mm thick thermal insulation to be considered cost. Insulation should be done at factory for all elliptical ducts).All ducts should be supported with wire supports & painted inline with duct colour . Supports should be provide within 2m distance .All ducts should be supplied with primer & without any patches & damages |  |  | 0 |  |  |  | 0 | 0
| Please note that all elliptical duct should be delivered to the site with zinc cromate primer & required H frames for the elliptical duct connections, cost should be included in the same ducting cost. C ring should be with 18 G only. |  |  | 0 |  |  |  | 0 | 0
3.1 | 24 gauge galvanized sheet steel (0.63mm) (0"-24") | 150 | 25 | 175 | Sqmt |  |  | 0 | 0
3.2 | 22 gauge galvanized sheet steel (0.8mm) (25"-48") | 150 |  | 150 | Sqmt |  |  | 0 | 0
3.3 | 20 gauge galvanized sheet steel (1.0 mm) (49"-70") | 50 |  | 50 | Sqmt |  |  | 0 | 0
|  |  |  | 0 |  |  |  | 0 | 0
4 | Supply & Installation of double skin plenum of 40-45mm thick with puf insulation (factory fabricated ) of following sizes -Plenum Mouth Size to be cordinated with final Shop drawings for number of openings . Also scope covers for supply and fixing of double reinforced fire rated canvass. The scope also includes necessary hanging arrangements for plenum boxes,plenum cutouts as per HVAC layout . Color of plenum to match to nearest color of AHU body .Density of PUF 40+/-2 Kg/Cum. Note Quoted rate includes MS 50x50x6 mm angular support for plenum with suspension from dia 10mm threaded rods | 50 |  | 50 | Sqm |  |  | 0 | 0
|  |  |  | 0 |  |  |  | 0 | 0
5 | Sound Attenuators for Supply air Duct & Return | 23 | 8 |  | Sqm |  |  | 0 | 0
| Sound Attenuators of dissipative type to be provided on the supply & Return air duct entering the AHU Room,Sound attenuator qty shall be on surface area basis. |  |  | 0 |  |  |  | 0 | 0
| Sound Attenuators shall consist of outer casing, sound absorbing material and internal baffles, splitters and supports as expalined in the technical specifications. |  |  | 0 |  |  |  | 0 | 0
| Casing shall be of galavanised steel of not less than 20G in thickness. Casings shall be tested to 150mmwg and shall show no leakage or distortion in this condition. |  |  | 0 |  |  |  | 0 | 0
| Sound absorbing material shall be high density fibre glass held in place with at least 5% compression to prevent voids due to settling. Absorption material density shall be minimum 48 kg/cum. Fibreglass faced with minimum 26 g perforated galvanised sheet metal of minimum 40% open area. Combustion ratings shall be as expalined in the tender specifications |  |  | 0 |  |  |  | 0 | 0
|  |  |  | 0 |  |  |  | 0 | 0
6 | Supply, installation, testing & commissioning of multi blade, motorised fire & smoke dampers with spring return actuator. The damper shall be of atleast 2 hr. fire rating with 450 mm duct sleeve. The damper shall be as per UL Classified and CBRI approved. The damper shall be constructed out of 16G galvanised sheet steel. It shall be complete with control panel, actuator, sensor and inter-locking / wiring / connection for tripping of AHU fan motor.All the fire dampers should be of factory flanged (four bolt system) connections. The regulanr thin flange connection is not acceptable. | 4 | 1 | 5 | Sqm |  |  | 0 | 0
|  |  |  | 0 |  |  |  | 0 | 0
7 | ACTUATOR FOR FIRE DAMPER |  |  | 0 |  |  |  | 0 | 0
7a | UL Approved Spring loaded Actuator of required torque assembled in factory with required accessories to operate fire damper, step-down transformer, auxiliary switch, controller, necessary wiring & mounting arrangement. The actuator shall be equipped for 230V AC operation. The actuator also operates based on the input from BMS & pass on the status output to BMS and communicate to BMS System with an RS 485 port. | 8 | 2 | 10 | nos
0
7b | Supply ,installation, testing and commissioning of control panel with maximum 6 outgoing feeders for Actuators and incomer from AHU starter panel, Control panel should have necessary provisions to take BMS contacts for each actuator status and also show local display with reset option. Necessary Terminal block to be provided for fire interlocking complete as per technical specification & drawing detailshe rate quoted shall include the cost of all accessories like power and control cable to communicate ( soft Integration )to Building Management System through RS485 port for status, |  |  | 0
| Control panel with maximum 6 outgoing feeders for Actuators |  | 2 | 2 | nos
| Control panel with maximum 5 outgoing feeders for Actuators |  |  | 0 | nos
| Control panel with maximum 4 outgoing feeders for Actuators |  |  | 0 | nos
|  |  |  | 0 |  |  |  | 0 | 0
8 | Supply, installation, testing & commissioning of Volume Control Dampers made out of 100 x 40 x 1.55 mm thick galavanised steel frame and blades of 1.55 mm galavanised sheet steel with TDF flenges .Also suitable leavers for manual control and stickers/ engraving for open/ close identification should be consider post air balancing SMACNA standards to be followed for damper selection | 2.5 | 1 | 3.5 | Sqm |  |  | 0 | 0
0
9 | Supply, erection of 26 G GSS factory fabricated return air transfer duct piece . The return air transfer piece duct to be insulated with 10mm thick Class 1, open cell insulation | 55 |  | 55 | Sqm |  |  | 0 | 0
|  |  |  | 0 |  |  |  | 0 | 0
10 | Aluminium Grilles |  |  | 0 |  |  |  | 0 | 0
| Note - Grilles, Slot and diffuser colors as per architects approval at site |  |  | 0 |  |  |  | 0 | 0
10.1 | Powder Coated linear grilles for supply and return distribution ( colour for the grill to b confirmed by Arch/ PMC team before placing the order) . Deflection of the grille shall be 0 / 15 / 30. same will be confirmed later. deflection shall be considered as mentioned below & approved shop dwgs. for Cross talk attinuator grille should be flush with partition towards open ceiling. Length of grille should follow as per shop dwg (width can be 50/100/150/200/250/600mm). Single/one way | 13 | 1 | 14 | Sqm |  |  | 0 | 0
10.2 | Supply and installation of aluminium curved grilles,With collar dampers , Single / double deflection , grille with high quality extruded aluminium frame and bars, front horizontal and rear vertical, pitch of blade will be 19 mm for both front and rear blades , collar damper blades can be placed vertically or horizontally . Frame thickness shall be 1.2 mm thick, 45 mm deep and 20 mm wide, Bars shall be 3 mm thick from front side , Powder coated with a uniform thickness of 30-50 microns | 14 | 5 | 19 | Sqm |  |  | 0 | 0
10.3 | Supply ,and installation of Aluminium collar dampers | 5 | 2 | 7 | Sqm |  |  | 0 | 0
|  |  |  | 0 |  |  |  | 0 | 0
11 | Spill Air Boxes with butterfly damper - Expansion Plenum |  |  | 0 |  |  |  | 0 | 0
11.1 | 550x 550 x 400 mm High Sheet Metal Spill air boxes made out of 26 GI sheet for connecting the diffuser outlet & flexible with internal acoustic by 10mm open cell nitrile rubber |  |  | 0 | Nos |  |  | 0 | 0
11.1 | 900x 150 x 400 mm High Sheet Metal Spill air boxes made out of 26 GI sheet for connecting the diffuser outlet & flexible with internal acoustic by 10mm open cell nitrile rubber | 40 | 20 | 60 | Nos |  |  | 0 | 0
|  |  |  | 0 |  |  |  | 0 | 0
12 | Supply and Installation of round type supply air diffusers of below mentioned dia . The diffusers should be with suitable opposed blade collar dampers |  |  | 0 |  |  |  | 0 | 0
12.1 | Dia 450mm |  |  | 0 | Nos |  |  | 0 | 0
12.2 | Dia 400mm |  |  | 0 | Nos |  |  | 0 | 0
12.3 | Dia 375mm |  |  | 0 | Nos |  |  | 0 | 0
12.4 | Dia 200 mm |  |  | 0 | Nos |  |  | 0 | 0
12.5 | Dia 150 mm |  |  | 0 | Nos |  |  | 0 | 0
12.6 | Round duct, It should be of 24G ,Note -Duct Dropper of length 100/ 150mm for round diffuser connection and 9mm thick Nitrile rubber insulation also to be include |  |  | 0 |  |  |  | 0 | 0
| 150 mm dia |  |  | 0 | Rmt |  |  | 0 | 0
| 200 mm dia |  |  | 0 | Rmt |  |  | 0 | 0
| 250 mm dia |  |  | 0 | Rmt |  |  | 0 | 0
| 350 mm dia |  |  | 0 | Rmt |  |  | 0 | 0
| 400 mm dia |  |  | 0 |  |  |  | 0 | 0
|  |  |  | 0 |  |  |  | 0 | 0
12.2 | SITC of powder coated Extruded Aluminium 4-way diffusers Supply in accordance with the approved shop drawings and specifications. The diffuser Neck size shall be as given below. Outer size shall be as per the F/c grid, Diffuser shall be removable core type, shall have concealed fixing screw. Color code shall be as per architect approval. Supply diffuser with colar damper to be include. |  |  | 0 |  |  |  | 0 | 0
| 600 x 600 Outer Size (525x 525 Neck size in mm) |  |  | 0 |  |  |  | 0 | 0
| 600 x 600 Outer Size (450 x 450 Neck size in mm) |  |  | 0 |  |  |  | 0 | 0
| 600 x 600 Outer Size (375 x 375 Neck size in mm) | 5 | 5 | 10 | Nos |  |  | 0 | 0
| 600 x 600 Outer Size (300x 300 Neck size in mm) |  |  | 0 |  |  |  | 0 | 0
| 600 x 600 Outer Size (225 x 225 Neck size in mm) |  |  | 0 |  |  |  | 0 | 0
| 600 x 600 Outer Size (150 x 150 Neck size in mm) |  |  | 0 |  |  |  | 0 | 0
|  |  |  | 0 |  |  |  | 0 | 0
12.3 | SITC of powder coated Extruded Aluminium 4-way diffusers Return in accordance with the approved shop drawings and specifications. The diffuser Neck size shall be as given below. Outer size shall be as per the F/c grid, Diffuser shall be removable core type, shall have concealed fixing screw,. Color code shall be as per architect approval. |  |  | 0 |  |  |  | 0 | 0
12.4 | 600 x 600 Outer Size (525x 525 Neck size in mm) |  |  | 0 |  |  |  | 0 | 0
12.5 | 600 x 600 Outer Size (450 x 450 Neck size in mm) |  |  | 0 |  |  |  | 0 | 0
12.6 | 600 x 600 Outer Size (375 x 375 Neck size in mm) | 5 | 5 | 10 | Nos |  |  | 0 | 0
12.7 | 600 x 600 Outer Size (300x 300 Neck size in mm) |  |  | 0 |  |  |  | 0 | 0
12.8 | 600 x 600 Outer Size (225 x 225 Neck size in mm) |  |  | 0 |  |  |  | 0 | 0
12.9 | 600 x 600 Outer Size (150 x 150 Neck size in mm) |  |  | 0 |  |  |  | 0 | 0
|  |  |  | 0 |  |  |  | 0 | 0
|  |  |  | 0 |  |  |  | 0 | 0
13 | Supply and Installation of 3/2 slot Aluminium diffusers with white colored wings and white mesh from internal area | 15 |  | 15 | Rmt |  |  | 0 | 0
|  |  |  | 0 |  |  |  | 0 | 0
14 | Supply and Fixing -Hit and Miss Damper - with anodised matt black finish for slot grilles. The dampers should be such that it can be able to throttle the air quantity |  |  | 0 | Sqm |  |  | 0 | 0
|  |  |  | 0 |  |  |  | 0 | 0
15 | Supply and Fixing of double reinforced fire rated canvass for AHUs ,fans & DX Acs - Size shall be as per AHU capacity listed |  | 2 | 2 | Nos |  |  | 0 | 0
|  |  |  | 0 |  |  |  | 0 | 0
16 | Insulated Flexible Ducting |  |  | 0 |  |  |  | 0 | 0
| Factory Fabricated Insulated Flexible made out aluminium for connecting from main duct to diffuser box. The length of the flexible duct shall be around 1.0 to 1.5 mtr |  |  | 0 |  |  |  | 0 | 0
| The flexible duct shall me made of double lamination of aluminium foil, polyester and metalised polyester film permanently bonded to a coated spring steel wire helix. The exterior shal be wrapped with 25mm thick 16 kg / cum fibreglass insulation. The outer insulation jacket / vapour barrier made of fibreglass reinforced metalised polyester film laminate. |  |  | 0 |  |  |  | 0 | 0
16.1 | 250 mm dia insulated flexible duct | 40 | 20 | 60 | Rmt |  |  | 0 | 0
16.1 | 150 mm dia insulated flexible duct |  |  | 0 | Rmt |  |  | 0 | 0
|  |  |  | 0 |  |  |  | 0 | 0
17 | Supply and fixing of aluminium non return dampers / Back Draft dampers |  |  | 0 | Sqmt |  |  | 0 | 0
|  |  |  | 0 |  |  |  | 0 | 0
18 | Supply and fabrication of 300x50mm MS powder coated Perforated tray / Raceway with necessary supports and bends. Tray supports also to be painted as per architects approval | 100 |  | 100 | Rmt |  |  | 0 | 0
|  |  |  | 0 |  |  |  | 0 | 0
|  |  |  | 0 |  |  |  | 0 | 0
19 | Supply and Installation of round disc valve of dia 150 mm with suitable complete GSS box and necessary neck connections and clamps |  |  | 0 | Nos |  |  | 0 | 0
|  |  |  | 0 |  |  |  | 0 | 0
20 | Supply, Installation, testing and commissioning of EXHAUST & FRESH AIR FANS - Cabinet type single skin 0.8 mm thick outdoor mountable type, ceiling/floor mounted type fan with outlet velocity not more than 10 m/sec with all necessary supports.with NC/ NC contacts for IBMS compitbility wit IP Protocol. |  |  | 0 |  |  |  | 0 | 0
20.1 | 1200 CFM, Inline15-20mm ESP Exhaust fan |  |  | 0 | Nos |  |  | 0 | 0
20.2 | 800 CFM, Inline15-20mm ESP Exhaust fan | 1 | 0 | 1 | Nos |  |  | 0 | 0
20.3 | 1800 CFM, Inline15-20mm ESP Fresh air fan |  |  | 0 | Nos |  |  | 0 | 0
20.4 | 250 CFM, Inline15-20mm ESP Fresh air fan |  |  | 0 | Nos |  |  | 0 | 0
|  |  |  | 0 |  |  |  | 0 | 0
21 | Supply installation testing commisioning of inline -micro processor based explosion proof exhauxt fan of 500 cfm 25mm ESP exhaust fan for battery room with suitable canvass connections. Scope also includes supply and installation fo micro processor based exhauxt fan hydrogen gas sensor with control panel and suitable cabling complete solutions . | 1 |  | 1 | No |  |  | 0 | 0
|  |  |  | 0 |  |  |  | 0 | 0
22 | Air balancing activity for entire floor with calibrated air hood , with required tools and subsequent air balancing report with consultants approval for entire project |  |  | 1 | No |  |  | 0 | 0
|  |  |  | 0 |  |  |  | 0 | 0
23 | Supply and installation of 9 mm thick insulated GSS drain tray near Hiwall AC/Ducted AC. | 4 | 2 | 6 | Nos |  |  | 0 | 0
|  |  |  | 0 |  |  |  | 0 | 0
24 | Supply , Erection of factory fabricated Elliptical /spiral round VCDs | 3 | 0.5 | 3.5 | Sqmt |  |  | 0 | 0
|  |  |  | 0 |  |  |  | 0 | 0
25 | Supply installation testing commissioning of duct type Co2 Sensor with control panel to measure the return air CO2 level in the AHU room . Carbon dioxide transmitters shall accurately monitor the CO2 concentration in the indoor environment to help achieve energy savings . The sensor shall only be with a single beam dual wavelength nondispersive infrared (NDIR) sensor , the unit to be integerated to fresh air fan/Motorized vcd Actuator . Provided system complete to have Led display. Above mentioned control panel should be able to write any logic with respect to CO2 level. Logic should be discussed with consultants , scope also includes complete cabling and hardwares required for complete system including from sensor to control panel, fans and motorised VCD , Co2 sensor to be integerated to Motorized VCD |  | 0 | 0 | Nos |  |  | 0 | 0
|  |  |  | 0 |  |  |  | 0 | 0
26 | Supply, installation and adjusting of GSS made fresh motorized volume contol damper with actuators . opposed blades , frame shall be made of 18G and blades shall be made of 20G with prefilters for the louvers in all AHU room |  |  | 0 | Sqm |  |  | 0 | 0
|  |  |  | 0 |  |  |  | 0 | 0
27 | VENTIALTION UNITS |  |  | 0 |  |  |  | 0 | 0
| SITC Inline type cabinet Exhasut fan - low noise Inline EC fan with motor duly installed complete with mounting , spring type vibration isolator & supporting arrangement with bird wire mesh suitable for ceiling mounting,complete in all respects of design requirment, suitable to install in duct work.Inline fans shall be single phase.All instrument and control of Inline Fan must be suitable for construction 25 mm static Pressure, Canvas connection to be included ,Unit shall have controller Auto change over option ,auto restart option and need to be integrated with Backnet /Modbus with BMS |  |  | 0 |  |  |  | 0 | 0
| 200 Cfm |  |  | 0 | Nos |  |  | 0 | 0
| 300 Cfm |  |  | 0 | Nos |  |  | 0 | 0
| 400 Cfm |  |  | 0 | Nos |  |  | 0 | 0
| 500 Cfm ith hydrogen sensor for battery room Note: Inlinefan with H2 sensor , timer & hooter with 40 mm static pressure, requried panel & electrical works to be included in the same line item. Should generate an alarm if the H2 LEVEL in the room temperature goes beyond the set point .H2 Sensor panel should be provided with BMS compatibility. |  |  | 0 | Nos |  |  | 0 | 0
| 600 Cfm |  |  | 0 | Nos |  |  | 0 | 0
| 800 Cfm |  |  | 0 | Nos |  |  | 0 | 0
| 1000 Cfm |  |  | 0 | Nos |  |  | 0 | 0
| 1250 Cfm |  |  | 0 | Nos |  |  | 0 | 0
| 1500 Cfm |  |  | 0 | Nos |  |  | 0 | 0
| 2000 Cfm |  |  | 0 | Nos |  |  | 0 | 0
| 3000 Cfm |  |  | 0 | Nos |  |  | 0 | 0
| 5000 Cfm |  |  | 0 | Nos |  |  | 0 | 0
| SISW kItchen Exhaust fan 80mm ESP |  |  | 0 | Nos |  |  | 0 | 0
| Supply, installation, testing and commissioning of (SISW) Double Skin units, complete with double skin (45±2 mm) insulated Rockwool insulation material of density 60 kg/cum. The sheet thickness shall be minimum 0.8 mm for the outer skin and 0.8 mm thickness for the inner skin of GI . Single inlet single width backward fan fireproof fans with VFD . Each fan shall be complete with totally enclosed fan cooled IE5 motor , direct drive, motor shall be placed outside from the airflow path ,pulley mounted on motor & fan shaft ,Unit should include vibration isolator. The motor shall be suitable for 415 V + 10% volts 3 phase 50 cycles, AC supply & suitable for operating through VFD. The motor selected shall be energy efficient having efficiency at full load ranging between 82.5% to 92% in accordance with motor rating as per specification ,Kitchen exhaust Connectors ,fan and Junction boxes must be fireproof |  |  | 0 |  |  |  | 0 | 0
| 17000 cfm |  |  | 0 | Nos |  |  | 0 | 0
| 10000 cfm |  |  | 0 | Nos |  |  | 0 | 0
| 5000 cfm |  |  | 0 | Nos |  |  | 0 | 0
|  |  |  | 0 |  |  |  | 0 | 0
38 | SITC Inline type cabinet /inline Fresh air fan - low noise EC fan with motor duly installed complete with mounting , spring type vibration isolator & supporting arrangement with bird wire mesh suitable for ceiling mounting,complete in all respects of design requirment, suitable to install in duct work.Inline fans shall be single phase.All instrument and control of Inline Fan must be suitable for construction 25 mm static Pressure (with prefilter) ,Canvas connection to be included ,MERV 8 filter to be considere ,Unit shall have controller Auto change over option ,auto restart option and need to be integrated with Backnet /Modbus with BMS |  |  | 0 |  |  |  | 0 | 0
38.1 | 300 Cfm |  |  | 0 | Nos |  |  | 0 | 0
38.2 | 400 Cfm |  |  | 0 | Nos |  |  | 0 | 0
38.3 | 600 Cfm |  |  | 0 | Nos |  |  | 0 | 0
38.4 | 700 Cfm |  |  | 0 | Nos |  |  | 0 | 0
38.5 | 800 Cfm |  |  | 0 | Nos |  |  | 0 | 0
38.6 | 1000 Cfm |  |  | 0 | Nos |  |  | 0 | 0
38.7 | 1500 Cfm |  |  | 0 | Nos |  |  | 0 | 0
38.8 | 2000 Cfm |  |  | 0 | Nos |  |  | 0 | 0
38.9 | 4000 Cfm |  |  | 0 | Nos |  |  | 0 | 0
39 | 5000 Cfm |  |  | 0 | Nos |  |  | 0 | 0
39.1 | 10000 Cfm |  |  | 0 | Nos |  |  | 0 | 0
39.2 | 15000 Cfm |  |  | 0 | Nos |  |  | 0 | 0
0
40 | CAV |  |  | 0 |  |  |  | 0 | 0
40.1 | Supply ,Installation,testing & commisoning of CAV with nessarry supporting meaterilas for the 150 to 200 CFM for phone Booth |  |  | 0 | Set |  |  | 0 | 0
[8 empty] | 0 | 0
| Total of SHEET METAL WORK & AIR TERMINATION | [6 empty] | 0 | 0
C | INSULATION WORK |  |  | 0
0
1 | Supply and installation Thermal (Insulation) of specified thickness of Elastromeric Rubber Insulation manafactured as per ASTM E 84 test & which should also meet NFPA 90A supplementary materials for air distribution system which should not absorbs less 0.2% water by volume (ASTM c 209), should not support microbial growth (ASTM C1071, G21, G22) and should emit objectionable odors (ASTM C 665) and should have thermal conductivity of 0.27 ( R - 2.78 in 3.4" thickness) and water vapor permeance of 0.10. Joints should be sealed with 50 mm wide 3 mm thick self adhesive tape (Black Cotton Tape not acceptable). Class "O" Material- 9 mm thick | 170 | 85 | 255 | Sqm |  |  | 0 | 0
1.1 | Class "O" Material- 20 mm thick |  | 20 | 20 | Sqm |  |  | 0 | 0
|  |  |  | 0 |  |  |  | 0 | 0
2 | Supply and installation of (Accoustic) Duct liner (Insulation) of specified thickness of Elastromeric Rubber Insulation manafactured as per ASTM E 84 test & which should also meet NFPA 90A supplementary materials for air distribution system which should not absorbs less 0.2% water by volume (ASTM c 209), should not support microbial growth (ASTM C1071, G21, G22) and should emit objectionable odors (ASTM C 665) and should have thermal conductivity of 0.27 ( R - 2.78 in 3.4" thickness) and water vapor permeance of 0.10. - Class "1" Material-.All joints of the Insulation material should be further covered with 50 mm wide 3 mm thick self adhesive tape made of similar material & Black Cotton Tape shall not be used. | 50 | 20 | 70 | Sqm |  |  | 0 | 0
|  |  |  | 0 |  |  |  | 0 | 0
3 | AHU ceiling and wall insulation:Providing and fixing Supplying of acoustic lining on wall and ceiling of AHU rooms with (UP TWIGA MAKE/ISOVER MAKE) 25mm thick Rigid Board of Glass wool one side aluminum faced and other side black glass cloth lamination, density 70 to 80 kg/cu.m |  | 80 | 80 | Sqm |  |  | 0 | 0
[8 empty] | 0 | 0
| Total of Insulation works | [6 empty] | 0 | 0
[8 empty] | 0 | 0
D | VRV/HI BRID AIR-CONDITIONING EQUIPMENTS:(100% INVERTER TYPE ONLY TO BE QUOTED) - R410A refrigerant |  |  | 0 |  |  |  | 0 | 0
|  |  |  | 0 |  |  |  | 0 | 0
1 | Supply & Installation of VRV /VRF airconditioning system comprising of Modular type high efficiency Twin Rotary Multiple Compressor with inverter, High efficiency heat transfer Cooling Coil suitable for Environment friendly R410a refrigerant,Air cooled propeller type condenser fan with DC motor drive,interconnecting piping, suction line insulation etc., Micro-processor control panel suitable for automatic operation,High speed calculation inverter control, active oil control mechanism incorporating all safety functions as per equipment specifications & other points as listed below: |  |  | 0 |  |  |  | 0 | 0
| The unit mounted starter panel shall be complete with IP-55 protection consisting of power disconnecting switches with fuses, soft starters, for compressor motors, under/over voltage trip, single phase preventers, communication card which can accept 4-20 mA or 2-10 Vdc analog signal. |  |  | 0 |  |  |  | 0 | 0
| All components shall be mounted on welded steel base frame, structural steel profiles/panels made out of galvanized sheet steel, protected with primary coat & finished with epoxy paint. |  |  | 0 |  |  |  | 0 | 0
| Modular type outdoor units equipped with highly efficient scroll compressors, with inverter type compressor(s),special acryl precoated heat exchanger,low noise condenser fan,auto check function for connection error, auto address & UNIT Price shall be inclusive of outdoor stand price.Shifting & Installing of ODU as per shop drawing is part VRV vendor scope.(ODU Location & Capacity mentioned below).Shifting of Out door units from GF to Terrace floor is part of VRF vendor scope |  |  | 0 |  |  |  | 0 | 0
| All VRV units should be compatible for third party BMS integration .necessary integrator should be consider in part HVAC/VRF vendor scope |  |  | 0 |  |  |  | 0 | 0
1.1 | Top Discharge Outdoor Unit(ODU) : Cooling Capacity : 6 HP (T2 server room) |  |  | 0 | Nos |  |  | 0 | 0
1.2 | Top Discharge Outdoor Unit(ODU) : Cooling Capacity : 4 HP | 2 | 2 | 4 | Nos |  |  | 0 | 0
1.3 | Top Discharge Outdoor Unit(ODU) : Cooling Capacity :25HP |  |  | 0 | Nos |  |  | 0 | 0
1.3 | Top Discharge Outdoor Unit(ODU) : Cooling Capacity : 28 HP |  |  | 0 | Nos |  |  | 0 | 0
1.3 | Top Discharge Outdoor Unit(ODU) : Cooling Capacity : 62HP |  |  | 0 | Nos |  |  | 0 | 0
|  |  |  | 0 |  |  |  | 0 | 0
2 | DOUBLE SKIN CABINET TYPE AIR HANDLING UNITS WITH EC FANS ( VRF TYPE) |  |  | 0
| CASING: |  |  | 0
| Supply Installation of Factory Fabricated double skin SA plenum with dampered outlet made out of 50 mm thick double skin PUF panel with powder coated 0.6 mm sheet as outer skin and 0.6 mm plain GSS sheet as inner skin with aluminium frame. The plenum is required to connect the outlets of Existing Air Handling Units & the proposed supply air duct branches. The colour of the plenum to be as per the architect's requirement. Plenums has to be installed in the required location |  |  | 0
| Access / plenum Section shall be with 600 mm deep. All Access door shall be of hinged type & provided with view glass. |  |  | 0
| FAN: |  |  | 0
| Direct driven backward curved EC fan (Electronically commutated) with permanent magnet brushless DC motor for stepless variation of speed of fan based on sensor inputs (temperature / pressure). The fan section shall be provided with limit switch for safety to shut off fan during Opening of access door. The fans shall be mounted on a supporting frame. |  |  | 0
| The limit Switch shall be provided for all sections |  |  | 0
| VRF COIL: |  |  | 0
| AHRI certififed, VRF coil section with 6/4 rows deep construction with Aluminum fins & copper tube and MS header with flanges . The coil section shell be supplied with 18 gauge SS 314 drain pan with 13 mm thick nitrile rubber insulation with adequate slope The face velocity of the coil shall not exceed 500 fpm,. |  |  | 0
| FILTER SECTION |  |  | 0
| Filter Section with complete supporting arrangement for Rough filters with panel type filters of 80 to 85% efficiency down to 20 microns particle size MERV-8, 1 set of commissioning filters , MERV 13 filter to be considered |  |  | 0
| ELECTRICAL PANEL |  |  | 0
| Electrical panel suitable for Power Distribution with one incomer & multiple MPCB outgoing feeder as per EC Fans , Heater , Humidifier UVGI Lamp along with required number of cable from starter panel to EC Fans . The Starter Panel shall also be suitable for supplying the required power for control valve , UV lamp , electronic filters, AHU light . Design shall include the, Interlock between AHU door limit switch and starter. (Starter to trip if door opened and start disabled with door open) and AHU lighting. The Starter shall also have provision to trip the complete system in case of fire signal from fire panel / BMS / Fire Damper. Necessary contactors, transformers, relays, power & control cables etc., to be supplied along with the Starter Panel.Potentiometer to control AHU manually along with auto manual switch The specifications for the panel enclosure shall be same as for MCCs in additional to required terminals to support for control and monitoring of AHUs through BMS system. |  |  | 0
| The rate quoted shall include power termination arrangement mounted on the external surface of the AHU & provision shall be made to switch ON / OFF the AHUs on the AHU cabinet surface. |  |  | 0
| The noise from the AHU should not exceed 65 dBA at a distance of 1m (without connection of ducts) at rated air quantity. |  |  | 0
| The sealant used should be of low VOC & not to exceed 420 gms/ltr. |  |  | 0
| AHU to to be quoted along with AHU Kit in between indoor & outdoor unit ' |  |  | 0
| TR, total air, outside air, cooling coil face area, number of rows of cooling coil, External static pressure, number of fans, fan motor KW (each) and fan motor speed. |  |  | 0
| AHU - Type - 1 Office |  |  | 0
| 40 TR, 7548 lps (16000 cfm), 710 lps (1500 Cfm), 2.98 Sqm., 6 rows, 30 mmwg, 3 Nos , 2.2 KW & 1450 rpm |  |  | 0 | 0
0
| AHU - Type - 2 |  |  | 0
| 35 TR, 6605 lps (14000 cfm), 945 lps (2000 Cfm), 4.0 Sqm., 6 rows, 30 mmwg, 3 nos., 2.2 KW & 1450 rpm |  |  | 0
0
2 | INDOOR UNITS |  |  | 0 |  |  |  | 0 | 0
| Indoor Unit(IDU): Cooling type : All the units should be supplied with Cordless remote control. The following Indoor unit capacities are required for each type of Room.Drycontact should be considered for Auto change over,failure status,overload sequencing etc.. |  |  | 0 |  |  |  | 0 | 0
0
2.1 | HI WALL |  |  | 0 |  |  |  | 0 | 0
| 2.0 TR |  |  | 0 | Nos |  |  | 0 | 0
| 1.5 TR | 2 |  | 2 | Nos |  |  | 0 | 0
| 1.0 TR |  | 2 | 2 | Nos |  |  | 0 | 0
| 2.5 TR | 0 | 2 | 2 | Nos |  |  | 0 | 0
|  |  |  | 0 |  |  |  | 0 | 0
2.2 | Ductable Unit |  |  | 0 |  |  |  | 0 | 0
| 3.0 TR |  |  | 0 | Nos |  |  | 0 | 0
| 6.0TR |  |  | 0 | Nos |  |  | 0 | 0
| 7.0TR |  |  | 0 | Nos |  |  | 0 | 0
| 8.0TR |  |  | 0 | Nos |  |  | 0 | 0
| 11.0TR |  |  | 0 | Nos |  |  | 0 | 0
| 18.0TR |  |  | 0 | Nos |  |  | 0 | 0
|  |  |  | 0 |  |  |  | 0 | 0
2.3 | Cassette Unit |  |  | 0 |  |  |  | 0 | 0
| 0.6TR |  |  | 0 | Nos |  |  | 0 | 0
| 0.8TR |  |  | 0 | Nos |  |  | 0 | 0
| 1.0TR |  |  | 0 | Nos |  |  | 0 | 0
| 1.2TR |  |  | 0 | Nos |  |  | 0 | 0
| 1.5TR (huddle room) |  |  | 0 | Nos |  |  | 0 | 0
| 2 TR |  |  | 0 | Nos |  |  | 0 | 0
| 2.5 TR |  |  | 0 | Nos |  |  | 0 | 0
| 2.8 TR |  |  | 0 | Nos |  |  | 0 | 0
| 3.0TR |  |  | 0 | Nos |  |  | 0 | 0
| 3.5TR |  |  | 0 | Nos |  |  | 0 | 0
| 4.0TR |  |  | 0 | Nos |  |  | 0 | 0
| 5.0TR |  |  | 0 | Nos |  |  | 0 | 0
|  |  |  | 0 |  |  |  | 0 | 0
3 | Centralised Remote Controller system (CRC) - The cost shall include below line itmes |  | 1 | 1 | Nos |  |  | 0 | 0
3.1 | Supply of Centralised Remote Controller system of VRV system for all the indoor & outdoor units. |  |  | 0 |  |  |  | 0 | 0
3.2 | Only ON/OFF Type Centralised Remote Controller system |  |  | 0 |  |  |  | 0 | 0
3.3 | Centralised Remote Controller system |  |  | 0 |  |  |  | 0 | 0
3.4 | LCD Touch Panel Type Centralised Remote Controller system |  |  |  | Nos |  |  | 0 | 0
3.5 | BACNET protocol for BMS interface BACnet gateway with required control cabling to Central BMS with suitable software and accessories. Necessary integrator, convertor, software, hardware, license's etc. as applicable for the VRF / VRVs / SET FREE / MMS to interact & be controllable thru' central BMS. Necessary protocol for connecting with MODBUS RTU, BACNET, LOW WORKS etc. shall also be included. |  | 1 | 1 | Nos |  |  | 0 | 0
|  |  |  | 0 |  |  |  | 0 | 0
4 | REFRIGERANT PIPING |  |  | 0 |  |  |  | 0 | 0
| Interconnecting copper refrigerant pipe work duly insulated with elastomeric nitrile rubber type tubular insulation with SEVEN MILL CLOTH between indoor & outdoor units as per specifications . All piping inside the room shall be properly supported with hanger and all piping should be run in perforated cably tray. Cable tray qty specified seperately.. MS supports for refrigerant piping & cables, using angles, channels, Tees, flats, etc should be considered as part of scope.All MS supports shall be given a coat of red-oxide primer and two coats of synthetic enamel paint of approved colour. |  |  | 0 |  |  |  | 0 | 0
4.1 | 41.3mm OD (insulation =13 mm thick) |  |  | 0 | Rmt |  |  | 0 | 0
4.2 | 34.3mm OD (insulation =13 mm thick) |  |  | 0 | Rmt |  |  | 0 | 0
4.3 | 28.6mm OD (insulation =13 mm thick) |  |  | 0 | Rmt |  |  | 0 | 0
4.4 | 22.2mm OD (insulation =13 mm thick) |  |  | 0 | Rmt |  |  | 0 | 0
4.5 | 19.1mm OD (insulation =13 mm thick) | 80 | 40 | 100 | Rmt |  |  | 0 | 0
4.6 | 15.9mm OD (insulation =13 mm thick) | 40 | 20 | 100 | Rmt |  |  | 0 | 0
4.7 | 12.7mm OD (insulation =13 mm thick) | 40 | 20 | 60 | Rmt |  |  | 0 | 0
4.8 | 9.5mm OD (insulation =13 mm thick) | 40 | 40 | 80 | Rmt |  |  | 0 | 0
4.9 | 6.4mm OD (insulation =13 mm thick) | 40 | 40 | 80 | Rmt |  |  | 0 | 0
|  |  |  | 0 |  |  |  | 0 | 0
5 | DRAIN PIPE |  |  | 0 |  |  |  | 0 | 0
| Insulated Condensate Drain Piping |  |  | 0 |  |  |  | 0 | 0
| Supply Insulated PVC Condensate Drain piping as per specification as mentioned in the document insulated same as chilled water piping but without polyshield covering.Consider drip pans with drian pipe .Entire draine pipe needs to be insulated with 9mm thick Nitrile rubber insulation. |  |  | 0 |  |  |  | 0 | 0
5.1 | 65 mm dia |  |  | 0 | Rmt
5.1 | 40 mm dia | 30 |  | 30 | Rmt |  |  | 0 | 0
5.2 | 32 mm dia | 10 | 10 | 20 | Rmt |  |  | 0 | 0
5.3 | 25 mm dia | 10 | 10 | 20 | Rmt |  |  | 0 | 0
| Note:Cable from Electrical panel to isolator excluded in VRV vendor scope.same should capture in Electrical vendor scope. Cable from Isolator to ODU is part of VRV Vendorscope. |  |  | 0 |  |  |  | 0 | 0
|  |  |  | 0 |  |  |  | 0 | 0
6 | Imported fittings like Y-Joints and headers etc as per the layout( additional supports should consider for both ends of the Y joint) | 5 | 3 | 8 | Nos |  |  | 0 | 0
|  |  |  | 0 |  |  |  | 0 | 0
8 | Supply & providing of MS stand for VRV ODU along with proper supports-suitable for above configuration | 2 | 2 | 4 | Set |  |  | 0 | 0
|  |  |  | 0 |  |  |  | 0 | 0
9 | Filling, testing, commissioning including topping up of R410 A Refrigerant. |  |  | 0 | Kg |  |  | 0 | 0 |  | To be quoted from vendor
|  |  |  | 0 |  |  |  | 0 | 0
9.1 | SITC of Auto Sequential control panel for automatic change over between working unit and stand by unit in case of failure running unit based on the temperature, in Critical/Boardrooms/Server room units. Air conditioning units shall be able to restart automatically after power failure/interruption. Scheduling shall be possible between working AHU and stand by DX/VRF Hiwall split units. The panel shall be provided with potential free contact for fire protection. | 1 | 2 | 3 | Nos |  |  | 0 | 0 | #REF!
10 | DRAIN PUMP |  |  | 0 |  |  |  | 0 | 0
| Supply installation testing & commissioning of drain pump with all necessary supports |  |  | 0 |  |  |  | 0 | 0
10.1 | The condensate pump capable of pumping water to a height of 10m and a maximum flow of 1250L/hour. It should run continuous and be rated at 0.38A, with a normally closed, 4.0A safety cut out switch wired to the AC unit. The outlet should be 10mm with a non-return valve fitted. All as manufactured by Aspen Pumps model HD10 – FP2066/2 or equal and approved. (one working & one stand by) | 2 | 4 | 6 | Set |  |  | 0 | 0
| (Please note that required digital control logic panel with hooter should be included in the same line item) - Vendor has to select Pump for |  |  | 0 |  |  |  | 0 | 0
[8 empty] | 0 | 0
| Total of VRF works | [6 empty] | 0 | 0
E | ELECTRICAL WORKS |  |  | 0
0
1 | POWER CABLING |  |  | 0
| Note all copper cables to be FRLS |  |  | 0
| Supply, laying, affecting connections & Testing of the following sizes of 1.1 KV armoured PVC insulated aluminium/ copper conductor cables. Cables shall be inclusive of all clamps, saddles, screws, cable identification tags, cable terminal joints including terminal lugs, insulating tapes, affecting terminal connections to the equipment as per the specifications and as required. |  |  | 0 |  |  |  | 0 | 0
1.1 | 4C x 10 Sqmm cable (Copper) | 100 | 100 | 200 | Rmt |  |  | 0 | 0
1.2 | 4C x 6 Sqmm cable (Copper) | 50 | 50 | 100 | Rmt |  |  | 0 | 0
|  |  |  | 0 |  |  |  | 0 | 0
2 | CONTROL WIRING ( To be shielded cable) |  |  | 0 |  |  |  | 0 | 0
| Supply, laying, affecting connections & testing of the following sizes of control cables between indoor units and outdoor units. Between Panel and AC Equipments, VRV Units |  |  | 0 |  |  |  | 0 | 0
| 2C x1.5 Sqmm copper cable ( Multicore) | 150 | 150 | 300 | Rmt |  |  | 0 | 0
| 3C x1.0 Sqmm copper cable ( Multicore) | 50 | 50 | 100 | Rmt |  |  | 0 | 0
| 4C x1.5 Sqmm copper cable ( Multicore) | 50 | 50 | 100 | Rmt |  |  | 0 | 0
| Control Cable between IDU to ODU -Supply and Laying of 2C X 1 Sq.mm Shielded Communication cable with PVC Conduit pipe ( Dia 25 mm ) with necessary supports and fiitings for looping all the indoor Units with outdoor units. | 240 | 160 | 400 | Rmt |  |  | 0 | 0
| Electrical Cable between MCB to ODU -Supply and Laying of 4C X 4 Sq.mm aluminium cable with with necessary supports and fiitings for looping from MCB to outdoor units. | 40 | 40 | 80 | Rmt |  |  | 0 | 0
|  |  |  | 0 |  |  |  | 0 | 0
3 | EARTHING |  |  | 0 |  |  |  | 0 | 0
| Providing & fixing in position the following bare GI tape/ Cu wire including providing all fixing accessories & effecting proper connections. | 120 | 120 | 240 | Rmt |  |  | 0 | 0
a | 8G GI Wire |  |  | 0 |  |  |  | 0 | 0
|  |  |  | 0 |  |  |  | 0 | 0
4 | Supply and fixing of 5 A Plug top with 3m of 3cx2.5 Sqmm Multicore copper cable |  |  | 0 | Set |  |  | 0 | 0
[8 empty] | 0 | 0
| Total of ELECTRICAL WORKS | [6 empty] | 0 | 0
F | VAV WORKS-PART-01 |  |  | 0
1 | Eliptical type - SITC of VAVs with digital thermostat,suitable wiring |  |  | 0
| All VAV Suite to Duct Supplied shall be Factory Assembled, Lab Calibration & Testing with verifiable test data for performance.Customer witnessing of the above (if required).Each VAV termnals should have barcode by having the exact shedule as per the shop drawing and this should have scaned for fatory test results. |  |  | 0
| Variable Air Volume (VAV) Units are fabricated out of heavy gauge steel, mechanically sealed with gasketed & leak resistance construction.VAV shall be of Flat Oval type with seamless connection to Flat Oval Ducts for duct continuity. VAV should come with plug and play terminations for power, communication and temperature sensor outside of the controller enclosure .Power indicator and connection provison must be outside for better visibility.Cross velocity sensor probe should be replacable type if in case it broken at site, Damper position indicator outside of the VAV box is must. |  |  | 0
| The boxes shall be supplied with all internal attenuation treatment and acoustical damped casing necessary to achieve the required noise criteria. Casing shall be 22G GI sheet with 25mm thicknes of fibreglass insulation with aluminum foil,mechanically locked at all the side of casing inside. |  |  | 0
| Maximum allowable static pressure to the boxes for its satisfactory operation shall not exceed 0.20” WG |  |  | 0
| A suitable device shall be provided for the field adjustment of minimum/maximum air flow. All boxes shall be initially factory set at minimum air quantity of 20% to 120% of the design requirements. Under shut-off conditions, the VAV boxes shall not have air leakage more than 20% of the maximum air quantity. |  |  | 0
| VAV Unit shall be ceiling suspended with hanger brackets. |  |  | 0
| All accessories listed under specifications should be considered for pricing VAVs |  |  | 0
| The VAV controller shall be of native Bacnet MS/TP, with 4 universal inputs & 4 universal outputs, ports complying to B-ASC device and shall be BTL certified and UL listed. These shall have integrated differential pressure transmiter, inbuilt actuator with a min torque of 5Nm. VAV controller & Actuator should be integral type.VAV Controller must be able to hold Distance Factor to support Demand based Fan Speed control. |  |  | 0
| Direct Output temperature sensor comprising of high quality thermistor or platinum sensing element should be supplied with VAVs.The look of the sensor should be rectangular in shape as shown in our schedule drawings showing vav box quantities.the controller to support MODBUS / BACNET , Scope includes 5 Rmt Multicore power cable with plug top |  |  | 0
0
| Size of the VAV Boxes is as under:- |  |  | 0 |  |  |  | 0 | 0
| 70 -230 CFM VAV BOX |  |  | 0 | Nos |  |  | 0 | 0
| 100 -520 CFM VAV BOX |  |  | 0 | Nos |  |  | 0 | 0
| 125 -710 CFM VAV BOX |  |  | 0 | Nos |  |  | 0 | 0
| 185 -925 CFM VAV BOX |  |  | 0 | Nos |  |  | 0 | 0
| 290 -1450 CFM VAV BOX |  |  | 0 | Nos |  |  | 0 | 0
| 420 -2100 CFM VAV BOX |  |  | 0 | Nos |  |  | 0 | 0
| 580 - 2900 CFM VAV BOX |  |  | 0 | Nos |  |  | 0 | 0
| 3700 CFM above VAV BOX |  |  | 0 | Nos |  |  | 0 | 0
| Note : Eliptical VAV is part of scope |  |  | 0 |  |  |  | 0 | 0
|  |  |  | 0 |  |  |  | 0 | 0
2 | Supply, Installation, Testing and commissioning of Duct static pressure tarnsducer, Scope includes integration of duct pressure sensors into respective VFD with suitable control cabling and suitable hardwares addition if required to integrate AHU starter panel with VFD . Scope includes necessary cabling and hardwares |  |  | 0 | Nos |  |  | 0 | 0
|  |  |  | 0 |  |  |  | 0 | 0
3 | All the VAVs to be interlinked with LAN connectivity should be provided to monitor all the VAV status , temperature status & % of opening. The vendor should load the software for the proper integration. Scope includes complete software and necessary routers . VAV router to be placed inside the AHU room. Vendor to calculate loops and router according to OEM selection, Quoted rate includes required routers, with moniter display / PC to be provided by vendor. |  |  | 0 | Nos |  |  | 0 | 0
|  |  |  | 0 |  |  |  | 0 | 0
4 | Supply and laying of CAT-6 cables 19 mm thick FRLS PVC conduit. - should be shielded cable |  |  | 0 | Rmt |  |  | 0 | 0
| Note Color of conduits as per Architect Approvals |  |  | 0 |  |  |  | 0 | 0
|  |  |  | 0 |  |  |  | 0 | 0
5 | Supply, Installation, Testing and commissioning of Router |  |  | 0 | Nos |  |  | 0 | 0
[8 empty] | 0 | 0
| Vav works-PART-01 | [6 empty] | 0 | 0
1 | Vav works-PART-02 (Rectangular & Bypass Type) SITC of VAVs with digital thermostat,suitable wiring |  |  | 0
| Supply, Assembly, Installation, Testing, Balancing & Commissioning of VAV boxes in supply air duct, VAV shall be fabricated out of 22 G GI sheet and shall be insulated with 10 mm thk open cell nitrile rubber,The VAV unit shall be pressure independent, complete ,controller for receiving Temp. & DP Signal, actuator, associated acessories etc. |  |  | 0 |  |  |  | 0 | 0
| Up to 650 CFM | 11 |  | 11 | Nos |  |  | 0 | 0
| From 651 to 1350 CFM | 3 |  | 3 | Nos |  |  | 0 | 0
| From 1351 to 2100 CFM | 1 |  | 1 | Nos |  |  | 0 | 0
| From 2101 to 3200 CFM |  |  | 0 | Nos |  |  | 0 | 0
| Above 3200 CFM |  |  | 0 | Nos |  |  | 0 | 0
|  |  |  | 0 |  |  |  | 0 | 0
2 | Supply, Installation, Testing and Commissioning of VAV integrators for integrating the VAVs with third party BMS. Integrators shall be located in the AHU Rooms. Each integrator shall be capable of integrating minimum 40 no. VAVs. Integrators shall be placed in the AHU room. | 1 |  | 1 | Nos |  |  | 0 | 0
| Note :- VAV sizing & qty - VAV size shall vary with respect to final approved scheme. Contractor to order VAVs based on approved drawing. |  |  | 0 |  |  |  | 0 | 0
|  |  |  | 0 |  |  |  | 0 | 0
3 | Cables & Conduits |  |  | 0 |  |  |  | 0 | 0
3.1 | 2core, 1.5 Sqmm, screened ATC/shielded twisted pair cable for communication looping between VAV’s (VAV to VAV) & BMS. | 300 |  | 300 | RMT |  |  | 0 | 0
3.2 | 4core, 1.5 Sqmm, screened ATC/shielded /Flexible twisted pair cable for communication looping between VAV’s (VAV to Thermostats) & BMS. | 80 |  | 80 | RMT |  |  | 0 | 0
3.3 | 3core, 1 Sqmm, screened ATC/shielded twisted pair cable for communication looping between VAV’s & BMS. (for analogue thermostats) | 100 |  | 100 | RMT |  |  | 0 | 0
3.4 | 6core, 1 Sqmm, screened ATC/shielded twisted pair cable for communication looping between VAV’s & BMS. (fro digitial thermostats) | 80 |  | 80 | RMT |  |  | 0 | 0
[8 empty] | 0 | 0
| Vav works-PART-02 | [6 empty] | 0 | 0
[8 empty] | 0 | 0
0