## OVERALL SUMMARY
| PROJECT NAME | SNITCH ,BANGALORE
| LEASABLE AREA | 32937.37 | SFT
| PROJECT AREA (Incl. Part - Basement & Terrace) | 30000 | SFT
3) BUDGET MAKES
PART | DESCRIPTION | BoQ | RATE/SFT
| MEP AND LV SYSTEMS: |  | 0
6) | ELECTRICAL | 0 | 0
| TOTAL - MEP AND LV SYSTEMS | 0 | 0
EXCLUSIONS:
1. Washrooms and related works
2. Fire Hydrants and other bulidng central systems
3. DG Sets
4. Any External Building, Elevation and facade work
5. Main Builidng Electrical Source and Panel
6. Terrace Flooring
7. Finishing works in lift lobby, stair cases
8. Any exterior building works incl. renovation, services, structure, branding etc.

## SUMMARY MEP
| PROJECT AREA |  | Sqft
S.No. | Cost Heads
|  | Amount | Cost/Sft
A | Electrical Works | 0 | 0
A1 | POINT WIRING | 0 | 0
A2 | CONDUITING FOR LV SYSTEM | 0 | 0
A3 | EARTHING | 0 | 0
A4 | CABLES, MAINS & SUBMAINS | 0 | 0
A5 | RACEWAYS AND CABLE TRAYS | 0 | 0
A6 | DISTRIBUTION BOARDS | 0 | 0
A7 | SUB DISTRIBUTION PANELS | 0 | 0
A8 | LIGHTING SENSORS | 0
A9 | LIGHT FIXTURES | 0 | 0
| GRAND TOTAL (EXCLUSIVE OF TAXES) | 0 | 0

## 6. Electrical
Sl.No. | Description | UNIT | QTY | Supply Rate | Installation Rate | Total Rate (Rs.) | As per SNITCH Approved RC Rates | AMOUNT (Rs.) | Remarks
A. | POINT WIRING | [6 empty] | 0
B. | CONDUITING FOR TELEPHONE, COMPUTER & CONDUITING AND WIRING FOR T.V. SYSTEM. | [6 empty] | 0
C. | EARTHING | [6 empty] | 0
D | CABLES, MAINS & SUBMAINS | [6 empty] | 0
E | RACEWAYS AND CABLE TRAYS | [6 empty] | 0
F | DISTRIBUTION BOARDS | [6 empty] | 0
G | SUB DISTRIBUTION PANELS | [6 empty] | 0
H | LIGHTING SENSORS | [6 empty] | 0
| TOTAL - ELECTRICAL WORKS | [6 empty] | 0
A. | POINT WIRING
All Bulbs/any other consumables should be branded .It should have atleast one year replacement guarantee.
Point wiring rates are inclusive of 3 x 1.5 sq mm FRLS PVC insulated stranded copper conductor wires for circuit. The Light & power Distribution Boards location and switch board locations has been shown in the drawing. The switch board location may be changed as per the interior finish
All sockets to be checked with a Check Plug socket tester for live-neutral reverse, no earth,neutral fault, live earth reverse, neutral earth reverse.
The Circuit No. and DB no. label shall be provided on all UPS ,RAW sockets and switchboards with label printer.
Colour coding for conduits to be done for different systems. The whole length of conduits to be painted.
Wherever the occupancy sensor is provided in the cabin/ meeting rooms the circuit wires from Distribution Board to occupancy sensor and sensor to switch are inclusive in the point wiring rate.
All circuit & point wiring shall be colour coded & shall have ferruling on both end for circuit identification complete as required etc.
Earth loop Impedance Test to be performed. RCD test to be done. Cable Insulation Tests to be done.
1 | Wiring for the following light points with 3x1.5 Sq.mm FRLS PVC insulated stranded copper conductor wires in concealed PVC conduits in F.ceiling/walls/ceiling as directed including providing and fixing of 6 amps flush type switches, 5 sided G.I Boxes for housing switc­hes and earth­ing complete as required. Rates are inclusive of 3 x 1.5 sq mm FRLS PVC insulated stranded copper conductor wires for circuit.
a. | First point controlled by one no. 6 amp switch. | Nos. | 45 |  |  | 0 |  | 0
b. | First point controlled by one no. 6 amp switch. For Emergency Light | Nos. |  |  |  | 0
0
2 | Same as item No. 1a above but LOOP POINT i.e. wiring of point looped from first point with 3 x 1.5 sq. mm FRLS PVC insulated copper conductor wire in concealed/exposed PVC conduit and earthing | Nos. | 350 |  |  | 0 |  | 0
0
3 | Wiring for the following light points controlled by MCB in DB (Cost of MCB has been taken elsewhere in the tender) with 2 x 2.5 + 2.5 sq. mm FRLS PVC insulated copper conductor wires in concealed/exposed PVC conduits as called for and earthing.Rates are inclusive of 3 x 1.5 sq mm FRLS PVC insulated stranded copper conductor wires for circuit |  |  |  |  | 0
[6 empty] | 0 |  | -
a. | First point controlled by existing MCB in D.B. To first light | Nos. | 20 |  |  | 0 |  | 0
b. | First point controlled by existing MCB in D.B. For Emergency Light | Nos. | 40 |  |  | 0 |  | 0
0
4 | Same as item No. 3 above but LOOP POINT i.e. wiring of point looped from first point with 3 x 1.5 sq. mm FRLS. insulated copper conductor wire in concealed/exposed PVC conduit and earthing for Emergency Light | Nos. |  |  |  | 0 |  | 0
0
5 | Wiring for 6/16 amps light plug outlets with 3 X 2.5 sq.mm FRLS PVC insulated copper conductor wires in PVC Conduits in ceiling/walls/floor as direc­ted incl­u­ding providing and fixing of 6/13 amps flush type 5 pin socket and 16 amps switch with cover plate, 5 sided G.I boxes for housing switches, sockets and earthi­ng complete as required. (for general areas) | Nos. | 40 |  |  | 0 |  | 0
0
6 | Wiring for inline fan points with 2 x 2.5 sq.mm FRLS PVC insulated stranded copper con­ductor wires in concealed PVC conduits in F.ceiling/ walls/ Ceiling as directed including providing providing and fixing of 16 amps flush type switches 16 amps 3 pin socket near inline fan, 5 sided G.I. boxes for housing switches and 16 amps 3 pin socket outlet and earthing and complete as required.(including body earth for GI boxes) | Nos. | 4 |  |  | 0 |  | 0
0
7 | Wiring for projector / Geyser points with 2 x 4 + 1 x 4 sq mm FRLS PVC insulated copper conductor wires in concealed PVC conduits in F.ceiling/ walls/ Ceiling as directed including providing 16 amps flush type switch near the white board and 6/16 amps 6 pin socket near the projector in ceiling , 5 sided G.I. boxes for housing switches and 6/16 A 6 pin socket outlet , earthing and complete as required.(including body earth for GI boxes) ( 1 point per circuit) | Nos. | 6 |  |  | 0 |  | 0
0
8 | Wiring for VRV Indoor units with 3 x 2.5 sq.mm FRLS PVC insulated stranded copper conductor wires in concealed PVC conduits in F.ceiling/ walls/ Ceiling as directed including providing providing and fixing of 6 amps flush type switches 16 amps 3 pin socket near VRV points, 5 sided G.I. boxes for housing switches and 16 amps 3 pin socket outlet and earthing and complete as required.(including body earth for GI boxes) ( 2 to 3 points per circuits) | Nos. | 25 |  |  | 0 |  | 0 | *Quoted for 1primary and 2 Secondary
0
9 | Wiring for VAV /fire damper points with 3 x 1.5 sq.mm FRLS PVC insulated copper conductor wires in concealed PVC conduits in F.ceiling/ walls/ Ceiling as directed including providing 6 amps flush type switches, 6 amps 3 pin socket near VAV points, 5 sided G.I. boxes for housing switches and 6 A sockets earthing and complete as required. The sockets to be fused spur type (MK make). (including body earth for GI boxes) ( 8 to 10 points per circuits) | Nos. | 6 |  |  | 0 |  | 0 | *Quoted for 1primary and 9 Secondary
[6 empty] | 0 |  | -
10 | Wiring for 16 amps power outlet poi­nts with 4 sq.mm FRLS PVC insulated stranded copper conductor wires in concealed/recessed PVC conduit as directed including providing providing and fixing of 16 amps flush type switch and 6 pin socket with cover plate 5 sided G.I. outlet boxes for switches and socket and earthing the third pin with 2.5 sq mm FRLS PVC PVC stranded copper wire complete as required (Only one outlet shall be connected on each circuit) (including body earth for GI boxes) | Nos. | 6 |  |  | 0 |  | 0
0
11 | Wiring for 16 amps power outlet points with 4 sq.mm FRLS PVC insulated stranded copper conductor wires for the first power outlet and 4 sq.mm FRLS PVC insu­lated stranded copper conductor wires for the second outlet, in concealed PVC cond­uits in F.ceiling/ walls/Ceiling/floor ducts as directed including providing providing and fixing of 16 amps flush type switch and 6 pin socket with cover plate, 5 sided G.I. outlet boxes for housing switches and socket, and earthing the third pin with 2.5 sq.mm FRLS PVC PVC insulated copper conductor wires complete as required (Two power out­lets shall be connected on each circuit)(including body earth for GI boxes) | Set of Two | 4 |  |  | 0 |  | 0
0
12 | Wiring for A/C outlet points with 4.0 sq mm FRLS PVC insulated stranded copper conductor wires in PVC conduitl/wall/floor ducts as directed including providing 25 A socket with 25 amps SP MCB ( Tiny Trip) 5 sided GI Outlet Box for housing and socket and MCB and earthing with 2.5 sq. mm FRLS PVC PVC insulated stranded Copper Conductor wires complete as required. | Nos. | [5 empty] | 0
0
13 | Wiring for UPS/Raw plug outlets points with three core, 2.5 sqmm FRLS PVC Insulated and PVC sheathed flexible cable with bright annealed electrolytic copper conductor, 1100 volt grade confirming to IS : 694-1990 with latest amendments, in existing Channels/ conduit in ceiling/walls/floor including all cable termination accessories) (including body earth for GI boxes). Colour Coding to be followed | RM | 7500 |  |  | 0 |  | 0
[6 empty] | 0 |  | -
14 | Wiring for UPS/Raw plug outlets points with three core, 4.0 sqmm FRLS PVC Insulated and PVC sheathed flexible cable with bright annealed electrolytic copper conductor, 1100 volt grade confirming to IS : 694-1990 with latest amendments, in existing Channels/ conduit in ceiling/walls/floor inclu­ding all cable termination accessories) Earthing of GI Box to be included. Colour Coding to be followed . | RM | 120 |  |  | 0 |  | 0
[6 empty] | 0 |  | -
15 | Wiring for UPS/Raw plug outlets points with three core, 6.0 sqmm FRLS PVC Insulated and PVC sheathed flexible cable with bright annealed electrolytic copper conductor, 1100 volt grade confirming to IS : 694-1990 with latest amendments, in existing Channels/ conduit in ceiling/walls/floor inclu­ding all cable termination accessories) Earthing of GI Box to be included. Colour Coding to be followed . | RM | 60 |  |  | 0 |  | 0
0
16 | Wiring for power plug outlets points with 4 core, 4.0 sqmm FRLS PVC Insulated and PVC sheathed flexible cable with bright annealed electrolytic copper conductor, 1100 volt grade confirming to IS : 694-1990 with latest amendments, in existing Channels/ conduit in ceiling/walls/floor inclu­ding all cable termination accessories). Colour Coding to be followed . | RM |  |  |  | 0
0
17 | Wiring for power plug outlets points with 4 core, 6.0 sqmm FRLS PVC Insulated and PVC sheathed flexible cable with bright annealed electrolytic copper conductor, 1100 volt grade confirming to IS : 694-1990 with latest amendments, in existing Channels/ conduit in ceiling/walls/floor inclu­ding all cable termination accessories). Colour Coding to be followed | RM |  |  |  | 0
0
18 | Wiring for power plug outlets points with 4 core, 10.0 sqmm FRLS PVC Insulated and PVC sheathed flexible cable with bright annealed electrolytic copper conductor, 1100 volt grade confirming to IS : 694-1990 with latest amendments, in existing Channels/ conduit in ceiling/walls/floor inclu­ding all cable termination accessories). Colour Coding to be followed | RM |  |  |  | 0
0
19 | Wiring for 6 amps light plug outlets with 1.5 sq.mm FRLS PVC insulated stranded copper conductor wires in MS Conduits in ceiling/walls/floor as directed including providing and fixing of 6 amps flush type 5 pin socket and 6 amps with indicator type switch with cover plate, 5 sided G.I boxes for housing switches, sockets and earthing complete as required. (for toilet area sensor area urinal sensor & faucet sensor) | Nos | 20 |  |  | 0 |  | 0
0
20 | Wiring for the following Call Bell points with 1.5 Sq.mm FRLS PVC insulated copper conductor wires in concealed M.S conduits in F.ceiling / walls / ceiling as direc­ted including providing and fixing of 6 amps flush type Bell Push , 5 sided GI Boxes for housing switc­hes and earth­ing comple­te as required. For Handicap Toilet | Nos | 2 |  |  | 0 |  | 0
0
21 | Supply, installation, testing & commissioning of Emergency Buzzer & sounder of approved make. Cost to include Push button and wiring complete | Nos |  |  |  | 0 |  | 0
| Different colours to be used for 3 core cables for raw power and UPS power. |  |  |  |  | 0
0
| The word UPS shall be printed on all UPS sockets. |  |  |  |  | 0
| The word RAW shall be printed on all RAW sockets. |  |  |  |  | 0
| The Circuit No. and DB no. label shall be provided on all UPS ,RAW sockets and switchboards with label printer. |  |  |  |  | 0
| Contractor is required to submit samples of all types of switches and sockets to Consultant and Architects representative for approval before ordering the material. |  |  |  |  | 0
0
22 | Providing and fixing of 1 Nos.6 amp flush type 3 pin socket and 1 No. 6 amps switch cover plate, 5 sided G.I. Boxes for housing switches and sockets and earthing complete as required (for RAW). GI Box to have earth pin for body earthing (Raw Power) | Nos. | 50 |  |  | 0 |  | 0
0
23 | Providing and fixing of 2 Nos.6 amp flush type 3 pin socket and 1 No. 16 amps switch cover plate, 5 sided G.I. Boxes for housing switches and sockets and earthing complete as required (for UPS). GI Box to have earth pin for body earthing (UPS Power) | Nos. | 30 |  |  | 0 |  | 0
0
24 | Providing and fixing of 3 Nos.6 amp flush type 3 pin socket and 1 No. 16 amps switch cover plate, 5 sided G.I. / PVC moulded Boxes for housing switches and sockets and earthing complete as required (for UPS/RAW). GI Box to have earth pin for body earthing | Nos. | 350 |  |  | 0 |  | 0
0
25 | Providing and fixing of 1 No.16 amps flush type 6 pin socket and 1 No. 16 amps switch with indicator, cover plate, 5 sided G.I. Boxes for housing switches and sockets and earthing complete as required (for RAW/UPS) GI Boxes to have earth pin for body earthing | Nos. | 30 |  |  | 0 |  | 0
0
26 | Providing and fixing Underfloor Access Outlets 1Trap including providing 2 Nos. 6 Amps sockets and 1 no. 6 Amps switch. | Nos. | 12 |  |  | 0 |  | 0
0
27 | Supply and fixing of the following sizes of thermoplastic moulded plug and socket IEC 309 type in PVC Box of suitable size flush / surface and making connections complete as required. The box shall be IP 44. |  |  |  |  | 0
0
a | 3 pin 16/20 A 1 phase industrial socket with mcb & plug top | Nos. | 12 |  |  | 0 |  | 0
b | 3 pin 32 A 1 phase industrial socket plug top | Nos. | 4 |  |  | 0 |  | 0
0
28 | For Kitchen Equipments the degree of protection shall be- IP-67 |  |  |  |  | 0
0
a | 3 pin 25/20 /16 A 1 phase industrial socket with mcb & plug IP 67 | Nos. |  |  |  | 0 |  | 0
b | 3 pin 32 A 1 phase industrial socket with mcb & plug IP 67 | Nos. |  |  |  | 0 |  | 0
c | 5 pin 32 A 3 phase industrial socket with mcb & plug IP 67 | Nos. |  |  |  | 0 |  | 0
d | 5 pin 6/16 A 3 phase industrial socket with mcb & plug IP 67 | Nos. |  |  |  | 0 |  | 0
e | 5 pin 40 A 3 phase industrial socket with mcb & plug IP 67 | Nos. |  |  |  | 0 |  | 0
f | 5 pin 63 A 3 phase industrial socket with mcb & plug IP 67 | Nos. |  |  |  | 0 |  | 0
g | 63 A FP MCB with water proof M.S enclouser for dishwaser. Including the suitable size of cable termination box. IP 67 | Nos. |  |  |  | 0
0
29 | Providing and fixing in position of the following sizes of 2mm Thick FRLS PVC Conduit including all accessories as required. |  |  |  |  | 0
0
a. | 20 mm dia conduit ( 2 mm thick) | RM | 80 |  |  | 0 |  | 0
b. | 25 mm dia conduit (2 mm thick) | RM | 120 |  |  | 0 |  | 0
c. | 32 mm dia conduit (2 mm thick) | RM | 80 |  |  | 0 |  | 0
[6 empty] | 0 |  | -
30 | The Electrical Contractor shall provide sufficient temporary lighting for working in the Building total area 25000 sq. ft. divided in 1 floor and maintain the same till completion of the project.It shall include replacement of all fused/faulty lamps.It shall include providing 15 A plug sockets (industrial type with ON/OFF switch/MCB) on 4 sides walls one plug at every 5-8 meter distance. The Contractors will tap off supply from these plugs for his use. Tubelights to maintain a lighting level of 150 lux on the floor,.Each 15 A socket and each Light circuit shall be protected by suitable MCBs.Use three core PVC Insulated PVC sheathed copper conductor cables for wiring.The contractor shall salvage the complete wiring and take it back at the end of the project. | L.S. | 1 |  |  | 0 |  | 0
0
| TOTAL CARRIED OVER TO SUMMARY |  |  |  |  | 0 |  | 0
0
B. | CONDUITING FOR TELEPHONE, COMPUTER & CONDUITING AND WIRING FOR T.V. SYSTEM. |  |  |  |  | 0
0
1 | Providing and fixing in position of the following sizes of 2mm Thick FRLS PVC Conduit including all accessories as required. |  |  |  |  | 0
0
a. | 20 mm dia conduit ( 2 mm thick) | RM |  |  |  | 0 |  | 0
b. | 25 mm dia conduit (2 mm thick) | RM | 80 |  |  | 0 |  | 0
c. | 32 mm dia conduit (2 mm thick) | RM | 60 |  |  | 0 |  | 0
d | 40 mm dia conduit (2 mm thick) | RM |  |  |  | 0 |  | 0
0
0
| TOTAL CARRIED OVER TO SUMMARY |  |  |  |  | 0 |  | 0
0
C. | EARTHING |  |  |  |  | 0
0
1 | Providing laying and fixing in position the following copper strips and wires including providing all fixing accessories and effecting proper connections,PVC sleeve etc as requried. earth strips with PVC sleeves - Insulation Sleeving Cylindrical Earthing Strip PVC Sleeve, |  |  |  |  | 0
0
a | G.I. tape 25 mm x 6 mm | RM | 180 |  |  | 0 |  | 0
b. | Copper tape 25mm x 3 mm | RM |  |  |  | 0
c. | Copper wire 8 SWG | RM | 120 |  |  | 0 |  | 0
d. | Copper wire 12 SWG | RM | 90 |  |  | 0 |  | 0
0
2 | Supply installation , and making of Exothermic weld suitable to bond GI strip of 25x5 mm with Copper Strip of 25x5 mm with 75mm extensions on either side | Nos. |  |  |  | 0 |  | 0
0
3 | Supply and laying, effecting proper connec­tions, testing & commissioning of the following sizes of 1.1 KV armoured XLPE/ unarmoured Cross linked polyethylene insulated, PVC sheathed (XLPE), conforming to IS: 7098 (Part-1)- 1988 ( 90 deg C) aluminium /copper conductor cables conforming to IS : 1554 and IS 694 for Flexible copper cable Part I - 1976 with latest amendments laid over MS supports in existing RCC ducts/ laid in ground /laid on Cable Trays including clamping the cables to sup­ports in an approved manner as required complete with all accessories.All cables shall have thermo setting insulation XLPE and low emission of smoke and corrosive gas when affected by fire |  |  |  |  | 0
d | 1c x 70 sq.mm FR XLPE insulated flexible copper conductor cables | RM |  |  |  | 0
0
e | 1c x 50 sq.mm FR XLPE insulated flexible copper conductor cables | RM |  |  |  | 0 |  | 0
0
f | 1c x 35 sq.mm FR XLPE insulated flexible copper conductor cables | RM | 120 |  |  | 0 |  | 0
0
g | 1c x 25 sq.mm FR XLPE insulated flexible copper conductor cables | RM | 80 |  |  | 0 |  | 0
0
h | 1c x 16 sq.mm FR XLPE insulated flexible copper conductor cables | RM | 140 |  |  | 0 |  | 0
0
i | 1 x 10 Sq. mm FR XLPE insulated flexible copper conductor cables (Green Colour for UPS DB Sub-main Earthing) | RM | 160 |  |  | 0 |  | 0
0
k | 1 x 6 Sq. mm FR XLPE insulated flexible copper conductor cables (Green Colour) | RM | 140 |  |  | 0 |  | 0
0
4 | Supplying and making of end termination for the following size of compression lugs and PG Threaded Nylon Flexible cable glands complete with all fixing accessories as required |  |  |  |  | 0
0
d | 1c x 70 sq.mm FR XLPE insulated flexible copper conductor cables | Sets |  |  |  | 0
0
e | 1c x 50 sq.mm FR XLPE insulated flexible copper conductor cables | Sets |  |  |  | 0 |  | 0
0
f | 1c x 35 sq.mm FR XLPE insulated flexible copper conductor cables | Sets | 10 |  |  | 0 |  | 0
0
g | 1c x 25 sq.mm FR XLPE insulated flexible copper conductor cables | Sets | 12 |  |  | 0 |  | 0
0
h | 1c x 16 sq.mm FR XLPE insulated flexible copper conductor cables | Sets | 15 |  |  | 0 |  | 0
0
i | 1 x 10 Sq. mm FR XLPE insulated flexible copper conductor cables (Green Colour for UPS DB Sub-main Earthing) | Sets | 20 |  |  | 0 |  | 0
0
5 | Providing earthing station at loca­tion as called for including provid­ing 600 mm x 600 mm x 6.0 mm thick tinned CU electrode 2 Nos 50 x 6 mm CU strip up to ground level 20mm dia medium class GI pipe (India Tube Company make or approved equal) CI funnel with 20 gauge GI wire mesh, masonry chamber with concrete base, CI man­hole cover with frame (300mm x 300mm) and bitumastic paint and packing the fixture of charcoal and common salt around plate electrode complete as per I.S. (Minimum depth shall be 4.2 Meters) | Nos. |  |  |  | 0
0
6 | Providing earthing station at loca­tion as called for including provid­ing 600 mm x 600 mm x 6.3 mm thick G.I Plate in cluding providing 2 Nos 70 x 6 mm G.I strip up to ground level 20mm dia medium class GI pipe (India Tube Company make or approved equal) CI funnel with 20 gauge GI wire mesh, masonry chamber with concrete base, CI man­hole cover with frame (300mm x 300mm) and bitumastic paint and packing the fixture of charcoal and common salt around plate electrode complete as per I.S. (Minimum depth shall be 4.2 M ) | Nos. |  |  |  | 0
0
7 | Supply, Installation, testing and commissioning of Maintenance Free Earthing of make Electrolytic Earthing comprising of type 'K' copper 2.4 mm wall thickness, hollow tube 10 feet long, 2.125 inches outer diameter completely filled with non hazardous metallic salts (Terrafill 25 KG Min.) to achieve an earth resistance of less than 1 ohms. Provide masonry chamber with concrete base, CI man­hole cover (cover to be heavy duty) with frame (300mm x 300mm) and make earth pit sign/ identifcation no in each earth station. | Nos. | 6 |  |  | 0 |  | 0
0
8 | Supply, installation, testing and commissioning of sheet metal enclosed 300 x 200 x 150 ( D) mm insulated earth distribution board with 1 nos. 50 x 6 mm copper tinned earth bars on SMC insulator suitable for 6/8 nos connections complete with all fixing accessories as required | Nos. | 1 |  |  | 0 |  | 0
0
9 | Supply, installation, testing and commissioning of sheet metal enclosed 150 x 100 x 125 ( D) mm insulated earth distribution board with 1 nos. 32 x 6 mm copper tinned earth bars on SMC insulator suitable for 6/8 nos connections complete with all fixing accessories as required. | Nos. |  |  |  | 0
0
10 | Supply, installation, testing and commissioning of sheet metal enclosed 150 x 100 x 125 ( D) mm insulated earth distribution board with 1 nos. 25 x 6 mm copper tinned earth bars on SMC insulator suitable for 6/8 nos connections complete with all fixing accessories as required. | Nos. | 6 |  |  | 0 |  | 0
0
11 | Supplying and laying of the following sizes of Heavy duty PVC Pipes below paved area including chase cutting and back filling. |  |  |  |  | 0
0
a. | 250 mm outer dia | RM |  |  |  | 0
b. | 100 mm outer dia | RM |  |  |  | 0
c. | 80 mm outer dia | RM |  |  |  | 0
0
| TOTAL CARRIED OVER TO SUMMARY |  |  |  |  | 0 |  | 0
0
D | CABLES, MAINS & SUBMAINS |  |  |  |  | 0
0
1 | Supply and laying, effecting proper connec­tions, testing & commissioning of the following sizes of 1.1 KV armoured XLPE / unarmoured Cross linked polyethylene insulated, PVC sheathed (XLPE), conforming to IS: 7098 (Part-1)- 1988 ( 90 deg C) aluminium /copper conductor cables conforming to IS : 1554 and IS 694 for Flexible copper cable Part I - 1976 with latest amendments laid over MS supports in existing RCC ducts/ laid in ground /laid on Cable Trays including clamping the cables to sup­ports in an approved manner as required complete with all accessories.All cables shall have thermo setting insulation XLPE and low emission of smoke and corrosive gas when affected by fire |  |  |  |  | 0
0
| Note: All cables to be glanded and crimped with suitable sized lugs. All Cable trays to be double earthed. All raceways and cable glands to be earthed with brass round earth clips and wires. |  |  |  |  | 0
| Earthing ring to be included in all the cable glands. |  |  |  |  | 0
| Sub main cables should be labelled at both ends |  |  |  |  | 0
| Joints shall be allowed only at the 2 ends of the cables and not in between. |  |  |  |  | 0
a | 3.5 c x 300 sq.mm 1.1 KV grade XLPE Insulated FRLS sheathed armoured aluminium conductor cable | RM |  |  |  | 0
0
b | 3.5 c x 240 sq.mm 1.1 KV grade XLPE Insulated FRLS sheathed armoured aluminium conductor cable For Main LT panel | RM |  |  |  | 0 |  | 0
0
c | 3.5 c x 185 sq.mm1.1 KV grade XLPE Insulated FRLS sheathed armoured aluminium conductor cable. | RM |  |  |  | 0
0
d | 3.5 c x 150 sq.mm1.1 KV grade XLPE Insulated FRLS sheathed armoured aluminium conductor cable | RM | 150 |  |  | 0 |  | 0
0
e | 3.5 c x 120 sq.mm 1.1 KV grade XLPE Insulated FRLS sheathed armoured aluminium conductor cable | RM |  |  |  | 0
0
f | 3.5 c x 95sq.mm 1.1 KV grade XLPE Insulated FRLS sheathed armoured aluminium conductor cable for kitchen | RM |  |  |  | 0 |  | 0
0
g | 3.5 c x 70sq.mm 1.1 KV grade XLPE Insulated FRLS sheathed armoured aluminium conductor cable 30kva ups | RM | 75 |  |  | 0 |  | 0
0
h | 3.5 c x 50 sq.mm1.1 KV grade XLPE Insulated FRLS sheathed armoured aluminium conductor cable | RM |  |  |  | 0 |  | 0
0
i | 4 c x 35 sq.mm1.1 KV grade XLPE Insulated FRLS sheathed armoured Copper conductor cable For 12kva ups | RM |  |  |  | 0 |  | 0
0
j | 4 c x 25 sq.mm 1.1 KV grade XLPE Insulated FRLS sheathed armoured aluminium conductor cable. For Light & Power DB & outdoor | RM | 425 |  |  | 0 |  | 0
0
k | 4 c x 16 sq.mm 1.1 KV grade XLPE Insulated FRLS sheathed armoured aluminium conductor cable | RM |  |  |  | 0
0
l | 4 c x 16 sq.mm 1.1 KV grade XLPE Insulated FRLS sheathed armoured copper conductor cable | RM |  |  |  | 0
0
m | 4 c x 10 sq.mm 1.1 KV grade XLPE Insulated FRLS sheathed armoured copper conductor cable For UPS DB | RM | 275 |  |  | 0 |  | 0
0
n | 4 c x 6 sq.mm 1.1 KV grade XLPE Insulated FRLS sheathed armoured copper conductor cable | RM | 100 |  |  | 0 |  | 0
0
o | 4 c x 4 sq.mm 1.1 KV grade XLPE Insulated FRLS sheathed armoured copper conductor cable | RM | 100 |  |  | 0 |  | 0
0
p | 3 c x 6 sq.mm 1.1 KV grade XLPE Insulated FRLS sheathed armoured copper conductor cable For EM DB | RM | 210 |  |  | 0 |  | 0
0
q | 3 c x 4 sq.mm 1.1 KV grade XLPE Insulated FRLS sheathed armoured copper conductor cable | RM |  |  |  | 0
0
r | 2 c x 16 sq.mm 1.1 KV grade XLPE Insulated FRLS sheathed armoured copper conductor cable | RM |  |  |  | 0
0
s | 2 c x 10 sq.mm 1.1 KV grade XLPE Insulated FRLS sheathed armoured copper conductor cable | RM |  |  |  | 0
0
t | 1c x 10 sq.mm FRLS XLPE insulated flexible copper conductor cables For 6 KVA UPS | RM | 100 |  |  | 0 |  | 0
0
u | 1c x 16 sq.mm FRLS XLPE insulated flexible copper conductor cables 12 KVA UPS | RM |  |  |  | 0 |  | 0
0
v | 1c x 25 sq.mm FRLS XLPE insulated flexible copper conductor cables | RM |  |  |  | 0
0
w | 1c x 35 sq.mm FRLS XLPE insulated flexible copper conductor cables For 30 KVA UPS | RM | 180 |  |  | 0 |  | 0
0
x | 1c x 50 sq.mm FRLS XLPE insulated flexible copper conductor cables | RM |  |  |  | 0 |  | 0
0
y | 1c x 70 sq.mm FRLS XLPE insulated flexible copper conductor cables | RM |  |  |  | 0
0
z | 1c x 95 sq.mm FRLS XLPE insulated flexible copper conductor cables | RM |  |  |  | 0
0
aa | 1c x 120 sq.mm FRLS XLPE insulated flexible copper conductor cables | RM |  |  |  | 0
0
ab | 1c x 240 sq.mm FRLS XLPE insulated flexible copper conductor cables | RM |  |  |  | 0
0
2 | Supplying and making of end termination for the following size of 1.1 KV XLPE insulated copper conductor armoured cables including providing heavy duty copper terminal crimping lugs, solder, insulation tape, approved sealing epoxy compound, double compression brass cable glands, effecting gland connec­tions and effecting terminal connections to the equipment complete as required. Use compression lugs and PG Threaded Nylon Flexible cable glands for single core flexible cables |  |  |  |  | 0
0
a | 3.5 c x 300 sq.mm 1.1 KV grade XLPE Insulated FRLS sheathed armoured aluminium conductor cable | Sets |  |  |  | 0
0
b | 3.5 c x 240 sq.mm 1.1 KV grade XLPE Insulated FRLS sheathed armoured aluminium conductor cable For Main LT panel | Sets |  |  |  | 0 |  | 0
0
c | 3.5 c x 185 sq.mm1.1 KV grade XLPE Insulated FRLS sheathed armoured aluminium conductor cable. | Sets |  |  |  | 0
0
d | 3.5 c x 150 sq.mm1.1 KV grade XLPE Insulated FRLS sheathed armoured aluminium conductor cable | Sets | 4 |  |  | 0 |  | 0
0
e | 3.5 c x 120 sq.mm 1.1 KV grade XLPE Insulated FRLS sheathed armoured aluminium conductor cable | Sets |  |  |  | 0
0
f | 3.5 c x 95sq.mm 1.1 KV grade XLPE Insulated FRLS sheathed armoured aluminium conductor cable | Sets |  |  |  | 0 |  | 0
0
g | 3.5 c x 70sq.mm 1.1 KV grade XLPE Insulated FRLS sheathed armoured aluminium conductor cable | Sets | 10 |  |  | 0 |  | 0
0
g | 3.5 c x 50 sq.mm1.1 KV grade XLPE Insulated FRLS sheathed armoured aluminium conductor cable | Sets |  |  |  | 0
0
h | 4 c x 35 sq.mm1.1 KV grade XLPE Insulated FRLS sheathed armoured Copper conductor cable For PAC | Sets |  |  |  | 0 |  | 0
0
i | 4 c x 25 sq.mm 1.1 KV grade XLPE Insulated FRLS sheathed armoured aluminium conductor cable. For Light & Power DB | Sets | 50 |  |  | 0 |  | 0
0
l | 4 c x 16 sq.mm 1.1 KV grade XLPE Insulated FRLS sheathed armoured copper conductor cable | Sets |  |  |  | 0
0
n | 4 c x 10 sq.mm 1.1 KV grade XLPE Insulated FRLS sheathed armoured copper conductor cable For UPS DB | Sets | 12 |  |  | 0 |  | 0
0
o | 4 c x 6 sq.mm 1.1 KV grade XLPE Insulated FRLS sheathed armoured copper conductor cable | Sets | 15 |  |  | 0 |  | 0
0
o | 4 c x 4 sq.mm 1.1 KV grade XLPE Insulated FRLS sheathed armoured copper conductor cable | Sets |  |  |  | 0 |  | 0
0
p | 3 c x 6 sq.mm 1.1 KV grade XLPE Insulated FRLS sheathed armoured copper conductor cable For EM DB | Sets | 18 |  |  | 0 |  | 0
0
q | 3 c x 4 sq.mm 1.1 KV grade XLPE Insulated FRLS sheathed armoured copper conductor cable | Sets |  |  |  | 0
0
r | 2 c x 16 sq.mm 1.1 KV grade XLPE Insulated FRLS sheathed armoured copper conductor cable | Sets |  |  |  | 0
0
s | 2 c x 10 sq.mm 1.1 KV grade XLPE Insulated FRLS sheathed armoured copper conductor cable | Sets |  |  |  | 0
0
t | 1c x 10 sq.mm FRLS XLPE insulated flexible copper conductor cables For 6 KVA UPS | Sets | 6 |  |  | 0 |  | 0
0
u | 1c x 16 sq.mm FRLS XLPE insulated flexible copper conductor cables for 12 kva ups | Sets |  |  |  | 0 |  | 0
0
v | 1c x 25 sq.mm FRLS XLPE insulated flexible copper conductor cables | Sets |  |  |  | 0
0
w | 1c x 35 sq.mm FRLS XLPE insulated flexible copper conductor cables For 30 KVA UPS | Sets | 16 |  |  | 0 |  | 0
0
x | 1c x 50 sq.mm FRLS XLPE insulated flexible copper conductor cables | Sets |  |  |  | 0 |  | 0
0
y | 1c x 70 sq.mm FRLS XLPE insulated flexible copper conductor cables | Sets |  |  |  | 0
0
z | 1c x 95 sq.mm FRLS XLPE insulated flexible copper conductor cables | Sets |  |  |  | 0
0
aa | 1c x 120 sq.mm FRLS XLPE insulated flexible copper conductor cables | Sets |  |  |  | 0
0
ab | 1c x 240 sq.mm FRLS XLPE insulated flexible copper conductor cables | Sets |  |  |  | 0
0
| TOTAL CARRIED OVER TO SUMMARY |  |  |  |  | 0 |  | 0
0
E | RACEWAYS AND CABLE TRAYS |  |  |  |  | 0
| Note :- |  |  |  |  | 0
1 | Fabricating supplying to site of installation, installation on ceiling/ surface 1.6 mm thick MS Powder coated raceways of height 50 mm and 1.2 mm thick openable cover, totally enclosed, the joints between two lengths of channels or between channel and junction box shall be joined together with 3 mm thick G.I coupler plates to make it dust and water proof. The cost shall including all supporting and fixing accessories including dash fasteners. |  |  |  |  | 0
0
a | 250 mm (wide) x 50 mm (height) | RM |  |  |  | 0 |  | 0
b | 150 mm (wide) x 50 mm (height) | RM |  |  |  | 0 |  | 0
c | 100 mm (wide) x 50 mm (height) | RM |  |  |  | 0 |  | 0
d | 100 mm (wide) x 100 mm (height) | RM | 180 |  |  | 0 |  | 0
e | 150 mm (wide) x 150 mm (height) | RM | 80 |  |  | 0 |  | 0
2 | Fabricating supplying to site of installation, Junction boxes for Ceiling raceways made from 2 mm thick, with 2.5 mm thick PVC powder coated cover including providing neoprene gaskets between the cover and the junction box, cadmium plated flat/round head screws, height as per site condition,totally enclosed. Proper cutouts shall be made in the side walls for raceway entry wherever required. The junction box shall be all side walls should be welded expect top cover and all side walls shall have suitable size of rectangular knock out holes for taking raceways / conduits as required and not a complete cut out. The top cover should be sealed with M Seal to make it dust and water proof complete as required etc. |  |  |  |  | 0
0
a | 300 mm x 300 x 60 mm (height) | Nos. | 10 |  |  | 0 |  | 0
b | 200 mm x 200 x 60 mm (height) | Nos. | 30 |  |  | 0 |  | 0
c | 150 mm x 150 x 60 mm (height) | Nos. | 30 |  |  | 0 |  | 0
d | 200 mm x 200 x 200 mm (height) | Nos. | 60 |  |  | 0 |  | 0
3 | Fabricating supplying to site of installation, in floor including chase cutting of floor,leveling, refilling and making good the same if required from 1.6 mm thick and 2 mm thick cover pregalvanised GI sheet, totally enclosed, height 50 mm . The two lengths of raceways shall be fitted with Collars , 60 mm wide, 3 mm thick , press fit type. The raceways shall be clamped to the floor slab with GI clamps , 3mm thick and shall be screwed to the floor slab. The joint between raceway and junction box will be made with GI flexible strip( 3 nos), 3 mm thick, 4 inches long ,15 mm wide which will be nut bolted to the Junction box complete as required etc. |  |  |  |  | 0
0
a | 250 mm (wide) x 40 mm (height) | RM | 150 |  |  | 0 |  | 0
b | 150 mm (wide) x40 mm (height) | RM | 80 |  |  | 0 |  | 0
c | 100 mm (wide) x 40 mm (height) | RM | 75 |  |  | 0 |  | 0
0
4 | Fabricating supplying to site of installation, Junction boxes for floor raceways made from 2 mm thick, with 2.5 mm thick GI cover including providing neoprene gaskets between the cover and the junction box, cadmium plated flat/round head screws, height as per site condition,totally enclosed. Proper cutouts shall be made in the side walls for raceway entry wherever required. The junction box shall be all side walls should be welded expect top cover and all side walls shall have suitable size of rectangular knock out holes for taking raceways / conduits as required and not a complete cut out. The top cover should be sealed with M Seal to make it dust and water proof complete as required etc. |  |  |  |  | 0
0
a | 300 mm x 300 x 60 mm (height) | Nos. | 10 |  |  | 0 |  | 0
b | 200 mm x 200 x 60 mm (height) | Nos. | 10 |  |  | 0 |  | 0
c | 150 mm x 150 x 60 mm (height) | Nos. | 15 |  |  | 0 |  | 0
d | 100 mm x 100 x 60 mm (height) | Nos. | 10 |  |  | 0 |  | 0
5 | Design manufacture , supply and fixing in position the cable trays of the following sizes for supporting 1.1 KV grade armoured/unarmoured aluminium /copper conductor cables. Fabricate the cable trays from perforated 1.6/2mm thick PVC CRCA sheet duly galvanised with expansion coupler plates duly galvanised, with bolts, washer and nuts. Knock out holes for cable connections as per approved design. The tray should comply with the specification of NEC (National Electric Codes) and NEMA (National Electric Manufacturers Association). The steel should be as per IS:226 and galvanising as per IS :2629/BS 729/ASTM 123. The rate shall also include for supporting steel , fish plates , fixing accessories , nuts bolts, supporting down rods , dash fastener, cutting the RCC etc. complete as required. (the horizontal and vertical bends, T's should be factory fabricated and the rate should include for the same) |  |  |  |  | 0
0
a | 150 mm wide x 40 mm x 1.6 mm Thickness | RM | 10 |  |  | 0 |  | 0
b | 300 mm wide x 40 mm x 1.6 mm Thickness | RM | 0 |  |  | 0 |  | 0
c | 450 mm wide x 40 mm x 2.0 mm Thickness | RM | 0 |  |  | 0 |  | 0
d | 600 mm wide x 40 mm x 2.0 mm Thickness | RM | 20 |  |  | 0 |  | 0
0
6 | Fabricating, supplying to site of installation, installation of 500 mm size of 105 mm height mesh type EZ-Electroplated Zinc ( Legrand -Cablofil make ) cable tray including threaded G.I. down rods, dash fasteners, cablofil fixing accesories etc. complete as required. Cablofil make | RM |  |  |  | 0 |  | 0
0
7 | Supporting brackets for cable trays, switch board etc. fabricated out of MS angle, channels & flats duly painted complete with necessary hardware. | KG |  |  |  | 0
0
| TOTAL CARRIED OVER TO SUMMARY |  |  |  |  | 0 |  | 0
0
F | DISTRIBUTION BOARDS |  |  |  |  | 0
0
1 | Supply,inginstalling, connecting testing and commissioning of the following double door 1/4 rows vertical type 1.6 mm thick and 1. 4 thick door sheet steel enclosed fully recessed type, TPN Miniature Circuit Breakers Distribution Boards dust proof, verm­in proof, with hinged and lockable doors complete with DP MCB's and inter-connection with copper wire , insulated copper bus bar , cable glands­/conduit entry bushes, bonding to earth and paint­ing. Also provide separate neutral busbar for each phase. Provide separate Earth Links for each phase. Use brass thimbles for connections of all wires. 1 row for single phase and 4 rows for 3 phase. Provide separate 4 way 63 A main neutral link also. The phase busbar links shall be factory pre insulated. |  |  |  |  | 0
| Note :- The IP rating of the DB should be IP 43 . |  |  |  |  | 0
| Provide DB charts in laminated sheets in all Distribution Boards |  |  |  |  | 0
a | Light & Power Distribution Board |  |  |  |  | 0
0
b | 10 Way TPN DB, each phase consisting of 8 Nos. 10/20 AMP SP MCB’s and controlled by one number 30 mA sensitivity 63 AMPS DP RCCB backed up with 1 no 63 Amps 4 pole MCB. | Nos | 10 |  |  | 0 |  | 0
0
c | 12 Way TPN DB, each phase consisting of 10 Nos. 10/20 AMP SP MCB’s and controlled by one number 30 mA sensitivity 63 AMPS DP RCCB backed up with 1 no 63 Amps 4 pole MCB. For Power DB | Nos | 6 |  |  | 0 |  | 0
0
d | 14 Way TPN DB, each phase consisting of 12 Nos. 10/20 AMP SP MCB’s and controlled by one number 30 mA sensitivity 63 AMPS DP RCCB backed up with 1 no 63 Amps 4 pole MCB. For Light DB | Nos |  |  |  | 0 |  | 0
0
e | 8 Way SPN DB, consisting of 4 Nos. 10/20 AMP SP MCB’s and controlled by one number 30 mA sensitivity 32 AMPS DP RCCB backed up with 32 Amps DP MCB. EM DB | Nos | 6 |  |  | 0 |  | 0
0
i | Fabricated Kitchen DB, consisting of 2 Nos. 40 AMP TP MCB + 2 Nos. 32 AMP SP MCB + 16 Nos 20 SP MCB and controlled by one number 100 FP MCCB and 160 Amps 4 pole copper Bus bar , inclduing ELR. The design of panel as approved by consultant | Nos |  |  |  | 0
0
2 | UPS Distribution Boards (All MCB's in UPS DB's should be D Curve) |  |  |  |  | 0
0
a | 10 Way TPN DB, each phase consisting of 8 Nos. 10/20 AMP SP MCB’s and controlled by one number 40 AMPS DP RCCB (30 mA) for each phase and 1 no. 40 amps 4 pole MCB incomer. UPS DB | Nos. | 4 |  |  | 0 |  | 0
0
b | 12 Way TPN DB, each phase consisting of 10 Nos. 10/20 AMP SP MCB’s and controlled by one number 63 AMPS DP RCCB (30 mA) for each phase and 1 no. 63 amps 4 pole MCB incomer. UPS DB | Nos. |  |  |  | 0 |  | 0
0
c | 14 Way SPN DB, consisting of 10 Nos. 10/20 AMP SP MCB’s and controlled by one number 30 mA sensitivity 63 AMPS DP RCCB backed up with 40 Amps DP MCB. For UPS DB | Nos. | 2 |  |  | 0 |  | 0
0
d | 12 Way SPN DB, consisting of 5 Nos. 20/32 AMP DP MCB’s and controlled by one number 30 mA sensitivity 63 AMPS DP RCCB for backed up with 63 Amps dP MCB. The bus bar shall be Twin bus bar For Server DB | Nos. | 2 |  |  | 0 |  | 0
0
3 | Supply, installation, testing and commissioning of sheet metal enclosed 400A ATS with inbuilt by pass + 1No 400Amp TPN MCCB ( 36 KA) With Dual KWH Meter (This shall include cable entry boxes both for incoming and outgoing cable)The enclosure shall be IP 42. | Nos. |  |  |  | 0
0
4 | Fabricated Main EM DB , consisting of 4 Nos. 32 AMP DP MCB’s and controlled by one number 30 mA sensitivity 40 AMPS DP RCCB backed up with 40 Amps DP manual changeover switch. | Nos. | 1 |  |  | 0 |  | 0
0
5 | Supply, installation, testing and commissioning of sheet metal enclosed 100A ATS with inbuilt by pass + 1No 100Amp TPN MCCB ( 25 KA) (This shall include cable entry boxes both for incoming and outgoing cable)The enclosure shall be IP 42. | Nos. |  |  |  | 0
0
6 | Supply, installation, testing and commissioning of sheet metal weather proof enclosure with 800 A TPN MCCB . This shall include cable entry boxes both for incoming and outgoing cable) | Nos. |  |  |  | 0
0
7 | Supply, installation, testing and commissioning of sheet metal weather proof enclosure with 63 A 4P MCB with RCCB (300mA). This shall include cable entry boxes both for incoming and outgoing cable) | Nos. |  |  |  | 0
0
8 | Supply, installation, testing and commissioning of sheet metal enclosure with 100A FP MCCB (25 kA). This shall include cable entry boxes both for incoming and outgoing cable) | Nos. |  |  |  | 0
0
9 | Supply, installation, testing and commissioning of sheet metal enclosure with 40/32 A 4P MCB. This shall include cable entry boxes both for incoming and outgoing cable) | Nos. |  |  |  | 0
0
10 | Supply, installation, testing and commissioning of sheet metal enclosure with 40/63 A DP MCB. This shall include cable entry boxes both for incoming and outgoing cable) For VRV Indoor units. | Nos. |  |  |  | 0
0
11 | Supply, installation, testing and commissioning of sheet metal enclosure with 80 A DP MCB. This shall include cable entry boxes both for incoming and outgoing cable) For VRV Indoor units. The enclosure shall be IP 42. | Nos. |  |  |  | 0
0
12 | Supply, installation, testing and commissioning of Automatic transfer switch with dual power input and 10 Nos. output ports of C-13 type with 25/32 Amp load and 3 Mtr. Connection cable with open end complete as required (For Racks) | Nos. |  |  |  | 0
0
| TOTAL CARRIED OVER TO SUMMARY |  |  |  |  | 0 |  | 0
0
G | SUB DISTRIBUTION PANELS |  |  |  |  | 0
0
1 | MAIN L.T. PANEL CUM LOAD MANAGEMENT PANEL |  |  |  |  | 0
0
| LT Panels: Supply & Delivery on site of Cubical type, sheet steel enclosure 2.0 mm thick CRCA for load bearing member and partition 1.6 mm thick Aluzinc (w/o painted) , powder coated (Paint Shade: Siemens Grey), free standing indoor type extendible compartmentlized type Main LT Panel / Sub Panels with vermin proof hinged lockable doors for each compartment, bus bar interconnections for incoming and outgoing including feeders earthing and painting and as per specifications. All meters shall be digital with LED display, whereever mentioned. Energy Meters shall be dual recording (grid and DG power) and have RS 485 Modbus RTU half duplex communication interface for provision of IBMS connectivity and wired accordingly. Provide 2 NO/2NC potential free contacts wires and terminal blocks in the cable alley for IBMS operation for each DG sets, Transformer and bus coupler ACB operation status, load manager output and energy meter output TB on connection to be provided. |  |  |  |  | 0
| MLTP / Capacitor panel will have only top entry & with rear access. All other panels will have top cable entry & no rear access. Shrouding of bus bar vertical as well as horizontal and all live parts is mandatory. |  |  |  |  | 0
| Under voltage relay of all incomers of Main L.T. Panel shall have interlocking with F.A. panel so that in case of fire all panel shall be switched off automaticaly except Critical supply panel. |  |  |  |  | 0
| Vendor will have to provide technical / commissioning support to installer at site. Supply as per scope given above. & Technical Specification given below describes the desired interlocks between various incoming power sources along with operating scenarios. This should be achieved through PLC Based Control System. Provide dedicated 1KVA UPS with 10 minutes backup for powering PLC within the panel. |  |  |  |  | 0
0
| LT PANELS & SUB DISTRIBUTION PANELS |  |  |  |  | 0
| Supplying, Receiving, Unloading, Unpacking, Shifting, Testing & Commissioning of the following Panels: |  |  |  |  | 0
0
Note | Provide insulated dedicated earth link in all UPS Panels |  |  |  |  | 0
| All MCCB's 250 Amps and above shall be Microprocessor based |  |  |  |  | 0
| All Light & Power panel ,UPS and A.C. Panel incomer MCCB shall have Over current, Earth fault and short circuit protection. |  |  |  |  | 0
| All Incomer MCCB's in UPS Panels shall be microprocessor based |  |  |  |  | 0
| The microprocessor based MCCBs shall have |  |  |  |  | 0
| Over Load (Phase) |  |  |  |  | 0
| Current setting Ir(Ir=XIn) OFF 0.4 to 1.0 in steps of 0.1 |  |  |  |  | 0
| Time delay , tr( Inverse) 10 sec at 6/r |  |  |  |  | 0
| Over Load (Neutral) |  |  |  |  | 0
| Current setting In (Intrl =XIr)0.5, 0.75&1.00 Intrl |  |  |  |  | 0
| Inverse 10 sec at 6 Intrl/Fixed 200ms |  |  |  |  | 0
| Short Circuit setting -2- 10 |  |  |  |  | 0
| Instantaneous- 1.5-1 |  |  |  |  | 0
| All MCB's in UPS Panels shall be D Curve |  |  |  |  | 0
| In all Electrical panels protective acrylic sheet to be provided in cable alley and feeders. |  |  |  |  | 0
| Outgoing meters shall be able to monitor all major power quality parameters Voltage , current , frequency , KVAH,KWH,Power factor and individual,harmonics, ethernet ready - IEC-625-22.2 |  |  |  |  | 0
| Incomer meter shall Support monitoring parameters —full range of 3-phase voltage, current, power and energy measurements, power factor, frequency, total harmonic distortion (THD), individual power harmonics (up to 63rd order). Accuracy standards - use four-quadrant metering and sample current/voltage simultaneously without gaps with 128 samples per cycle (zero-blind); comply with ANSI C12.20 class 0.2 and IEC 61557-12 class 0.2 for revenue meters. |  |  |  |  | 0
| Meter shall have Waveform capture shall be available for both current and voltage waveforms. Voltage sag and swell detection with waveform capture. With a resolution of 8 cycles @ 128 cycles/ sec or more. Communications - serial RS-485 Modbus and Ethernet Modbus TCP; provide two Ethernet ports to allow wiring from meter to meter as a daisy-chain; be capable of serve data over the Ethernet network accessible through a standard web browser and on the HMI (front display); the monitor shall contain default pages from the factory. |  |  |  |  | 0
| Meter Alarming capabilities - support 29 set-point driven alarms, four (4) digital alarms, (4) unary alarms, 10 Boolean alarms and five (5) custom alarms; user definable alarm events; set-point driven alarms shall be available for voltage/current parameters, input status, and end of interval status. |  |  |  |  | 0
| Solenoid Operated ATS with AC33B utilization category, source priority selection & MODBUS port along with phase sequence protection along with genset start & stop contacts. With enclosure & extended busbar arrangements for the termination of armoured cable. Along with 50KA TPN Thermal Magnetic Based MCCB at Output. (Compatible with Communication protocol). |  |  |  |  | 0
0
| Provide On / Off and trip indicating lamp on main incomer only. |  |  |  |  | 0
| All MCCB breaker shall be Schneider make unless otherwise specified |  |  |  |  | 0
| Note: The breaking capacity and trip setting of the breakers shall be finalized as per the final design . The report shall be as per Etap analysis. |  |  |  |  | 0
| All MCB's Breaking Capacity shall be enhanced to 55 KA due to cascading |  |  |  |  | 0
| Provide shut trip for fire integration in the all panels. Critical & UPS panel not required. |  |  |  |  | 0
0
a | The SDB-1 Light & power 32nd Floor shall consists of : |  |  |  |  | 0
| MAIN INCOMER |  |  |  |  | 0
| 1 No.250 A FP ATS MCCB (25KA/1 sec)( O/C, S/C,) and neutral isolation link 100% of rated current. Terminals suitable to receive 2R X 3.5c x 185 sq. mm AL cable connection on one side and Busbar connection on the other side. |  |  |  |  | 0
0
| Main BUSBAR Section |  |  |  |  | 0
| 300 amps TPN busbar chamber of suitable length with aluminium busbars. All busbars and interconnections shall be of suitable size aluminium strips current density of copper shall not be more than 0.8 Amps/ sq.mm.provide 50% capacity for neutral bus bar. |  |  |  |  | 0
0
| INDICATING PANELS |  |  |  |  | 0
| 3 nos phase indicating lamps (LED type) each backed up with MCB and switch shall be provided for each incomer. |  |  |  |  | 0
| Provide on/off indication lamp on each incomer & MCCB. |  |  |  |  | 0
| Provide Intelligent Panel Meter - Schneider multifunctional meter EM-6436 NG dual with RS485 for all incoming feeder |  |  |  |  | 0
0
| OUTGOINGS |  |  |  |  | 0
| 1 Nos. 125 A TPN MCCB (25 kA/ 1 sec) terminals to receive suitable Cable on one side and Busbar connection on the other side. |  |  |  |  | 0
| 2 Nos. 100 A TPN MCCB (25 kA/ 1 sec) terminals to receive suitable Cable on one side and Busbar connection on the other side. |  |  |  |  | 0
| 14 Nos. 63 A 4P MCB (10 kA/ 1 sec) terminals to receive suitable Cable on one side and Busbar connection on the other side. |  |  |  |  | 0
| 5 Nos. 32 A 4P MCB (10 kA/ 1 sec) terminals to receive suitable Cable on one side and Busbar connection on the other side. |  |  |  |  | 0
| 1 Nos. 40 A DP MCB (10 kA/ 1 sec) terminals to receive suitable Cable on one side and Busbar connection on the other side. |  |  |  |  | 0
| 2 Nos. 20/25 A DP MCB (10 kA/ 1 sec) terminals to receive suitable Cable on one side and Busbar connection on the other side. |  |  |  |  | 0
0
0
| The SDB Light & power as described above and specifications complete | Set | 1 |  |  | 0 |  | 0
0
b | THE UPS Output Panel shall consists of : |  |  |  |  | 0
0
| MAIN INCOMER |  |  |  |  | 0
0
| 1 No. 125 A TP+2N MCCB (36KA/1 sec)( O/C, S/C,E/F) and neutral isolation link 200% of rated current. Terminals suitable to receive 5R X 1C X 50 sq. mm XLPE Cu. Ar. cable connection on one side and Busbar connection on the other side. |  |  |  |  | 0
| BUSBAR-Section |  |  |  |  | 0
| 300 amps TP+2N busbar chamber of suitable length with Copper busbars. All busbars and interconnections shall be of suitable size copper strips current density of copper shall not be more than 1.6 Amps/ sq.mm.provide 100% capacity for neutral bus bar. |  |  |  |  | 0
| INDICATING PANELS |  |  |  |  | 0
| 3 nos phase indicating lamps (LED type) each backed up with MCB and switch shall be provided for each incomer. |  |  |  |  | 0
| Provide on/off indication lamp on each incomer and MCCB. |  |  |  |  | 0
| Provide Intelligent Panel Meter - multifunctional meter EM 6436 with RS485 for all incoming feeder |  |  |  |  | 0
| Provide Transient Voltage Surge Suppressor Rating 40kA class II along with 63 A MCCB. Including all necessary accessories. For Switching Operation on each incomer. |  |  |  |  | 0
| OUTGOINGS |  |  |  |  | 0
| 9 Nos. 63 A 4P MCB (10 kA/ 1 sec) terminals to receive suitable Cable on one side and Busbar connection on the other side. |  |  |  |  | 0
| 2 Nos. 63 A DP MCB (10 kA/ 1 sec) terminals to receive suitable Cable on one side and Busbar connection on the other side. |  |  |  |  | 0
| The UPS Output Panel (LOC:-UPS Room ) as described above and specifications complete. | Set | 1 |  |  | 0 |  | 0
0
c | THE UPS PDU-01 Panel shall consists of : |  |  |  |  | 0
0
| MAIN INCOMER |  |  |  |  | 0
0
| 1 No. 63 A TP+2N MCCB (25KA/1 sec)( O/C, S/C,E/F) and neutral isolation link 200% of rated current. Terminals suitable to receive 4C X 35 sq. mm XLPE Cu. Ar. cable connection on one side and Busbar connection on the other side. |  |  |  |  | 0
| BUSBAR-Section |  |  |  |  | 0
| 150 amps TP+2N busbar chamber of suitable length with Copper busbars. All busbars and interconnections shall be of suitable size copper strips current density of copper shall not be more than 1.6 Amps/ sq.mm.provide 100% capacity for neutral bus bar. |  |  |  |  | 0
| INDICATING PANELS |  |  |  |  | 0
| 3 nos phase indicating lamps (LED type) each backed up with MCB and switch shall be provided for each incomer. |  |  |  |  | 0
| Provide on/off indication lamp on each incomer and MCCB. |  |  |  |  | 0
| Provide Intelligent Panel Meter - multifunctional meter EM 6436 with RS485 for all incoming feeder |  |  |  |  | 0
| Provide Transient Voltage Surge Suppressor Rating 40kA class II along with 63 A MCCB. Including all necessary accessories. For Switching Operation on each incomer. |  |  |  |  | 0
| OUTGOINGS |  |  |  |  | 0
| 8 Nos. 32 A DP MCB (10 kA/ 1 sec) terminals to receive suitable Cable on one side and Busbar connection on the other side. |  |  |  |  | 0
| The UPS PDU-01&02 Panel as described above and specifications complete. | Set |  |  |  | 0 |  | 0
0
d | The Fabricated VTPN DB shall consists of : |  |  |  |  | 0
| MAIN INCOMER |  |  |  |  | 0
| 1 No 100 A FP ATS MCCB (25KA/1 sec)( O/C, S/C,) and neutral isolation link 100% of rated current. Terminals suitable to receive 4c x 70 sq. mm AL cable connection on one side and Busbar connection on the other side. Rating of the bus bar should be as per the |  |  |  |  | 0
0
| OUTGOINGS |  |  |  |  | 0
| 2 Nos. 32/40 A 4P RCBO (10 kA/ 1 sec) terminals to receive suitable Cable on one side and Busbar connection on the other side. |  |  |  |  | 0
| 2 Nos. 32/40 A 4P RCBO (10 kA/ 1 sec) terminals to receive suitable Cable on one side and Busbar connection on the other side. |  |  |  |  | 0
| 13 Nos. 20 A DP RCBO (10 kA/ 1 sec) terminals to receive suitable Cable on one side and Busbar connection on the other side. |  |  |  |  | 0
0
| The SDB Kitchen panel as described above and specifications complete | Set |  |  |  | 0 |  | 0
0
2 | Thermal scanning with Thermal Imaging camera, of all the cable and wiring joints in all the panels and MCB Distribution Boards after commissioning . | LS |  |  |  | 0
0
3 | Providing & fixing in position 1000 mm wide, Electrical Insulating Mats as per IS 15652:2006, 2mm thick, suitable up to 3.3 KV, fire retardant,no effect of acids, alkalies and transformer oils, moisture proof, high tensile strength and texture finish / cloth impression (Anti slip, marking on top). | RM | 18 |  |  | 0 |  | 0
0
4 | Supply & fixing in position approved shock treatment chart written in English, Hindi and Local language. These charts shall be framed in wooden frame & covered with clear glass. | Nos. | 1 |  |  | 0 |  | 0
0
5 | Supply & fixing in position the best quality danger notice boards of approved shape & size as reqd. by the local Electrical Inspecting Authority written in English, Hindi & local language. | Nos. | 1 |  |  | 0 |  | 0
0
6 | Supply & fixing in position the Electrical A 1 Size SLD chart in the UPS/electrical room. These charts shall be framed in wooden frame & covered with clear glass. | Nos. | 1 |  |  | 0 |  | 0
0
7 | Supplying the first aid box as approved by John Ambulance society. | Nos. | 1 |  |  | 0 |  | 0
0
0
| TOTAL CARRIED OVER TO SUMMARY |  |  |  |  | 0 |  | 0
0
H | LIGHTING SENSORS |  |  |  |  | 0
0
1 | Supply and Installation of Motion Sensors for Lighting Control in General Areas | Nos. | 96 |  |  | 0 |  | 0
| Make: Honeywell |  |  |  |  | 0
| TOTAL CARRIED OVER TO SUMMARY | [6 empty] | 0

## 7. Light Fixtures
* QUANTITIES AND SPECS TO BE UPDATED LATER AS PER THE RCP LAYOUT. CURRENT QTYS KEPT ARE ASSUMPTION BASED. | [5 empty] | 2) BUDGET SPECS
S No. | ITEM | UNIT | Qty | Supply Rate | Installation Rate | Total Rate (Rs.) | As per SNITCH Approved RC Rates | AMOUNT | Remarks
1 | Suspended LED Linear Light with electronic ballast. | Nos | 120 |  |  | 0 |  | 0 | QUOTED INSTALLATION ONLY
2 | Recessed LED Linear Light with electronic ballast. | Nos | 30 |  |  | 0 |  | 0
3 | Suspended Decorative Gloves light:Dia 350mm With electronic ballast. | Nos | 4 |  |  | 0 |  | 0
4 | Recessed & Suspended light fixture (600x600) with electronic ballast. | Nos | 20 |  |  | 0 |  | 0
5 | Downlight fixture Type -01 | Nos | 300 |  |  | 0 |  | 0
6 | Downlight fixture Type -02 | Nos | 50 |  |  | 0 |  | 0
7 | Decorative Hanging Light | Nos | 6 |  |  | 0 |  | 0
8 | Suspended Cylindrical light fixture | Nos | 150 |  |  | 0 |  | 0
9 | 360mm suspended Ring light fixture | Nos | 15 |  |  | 0 |  | 0
10 | Recessed Channel of 4 spots and linear light | Nos | 12 |  |  | 0 |  | 0
11 | Ceiling Recessed downlighter | Nos | 25 |  |  | 0 |  | 0
12 | Strip Light | Mtr | 180 |  |  | 0 |  | 0
13 | 3 Watts LED Ni Cd Battery backup up to 2 hrs emergency Exit light with Prolite Make or equivalent make. The sample shall be submitted before ordering. | Nos | 50 |  |  | 0 | 0 | 0
14 | Silver Series Digital PIR presence detection sensor of range 6.0 m Dia coverage recessed mounting at height of 2.4-3 meter to control 6A lighting load with 0.4 meter four core power cable. To be commissioned by hand held programmer with programmable features of delay time 10 Sec - 96 Hours, photocell and power up (status of luminaires when power is applied). It shall have provision to manually override luminary ON/OFF status using hand held remote control | NOS |  |  |  | 0 |  | 0
| TOTAL - SUPPLY OF LIGHTS | [5 empty] | 0 | 0

## MAKE LIST (to be updated)
PROPOSED MAKES
SR. NO. | MATERIAL | PROPOSED MANUFACTURER / SUB-CONTRACTOR / BRAND
A | INTERIOR, CIVIL & ALLIED WORKS
1 | ANTI TERMITE COMPOUND | PCI
2 | ACC BLOCKS | AEROCON
3 | WATER PROOFING COMPUND | PIDILITE
4 | CEMENT | ACC
5 | TMT BARS | REROLD
6 | SELF LEVELLING | ARDEX
7 | CERAMIC/ VITRIFIED TILES | KAJARIA/RAK
8 | SANITORY WARE | JAQUAR/TOTO
9 | CP FITTING/FIXTURES | JAQUAR
10 | DRY WALL PARTITION/CEILING | GYPROC/USG
11 | MODULAR CEILING | ARMSTRONG
12 | BAFFEL / METAL CEILING/DESIGNER CEILING | ARMSTRONG/LD2
12 | COMMERCIAL PLYWOOD | CENTURY/GREEN PLY
13 | MARINE PLYWOOD | CENTURY/GREEN PLY
14 | MDF | CENTURY/GREEN PLY
15 | PRELAM BOARD | ACTION TESSA
16 | VENEER | MERINO
17 | LAMINATES | MERINO
18 | ADHESIVE | FEVICOL SH./ARALDITE
20 | GLASS | SAINT GOBIN
21 | LACQUERED GLASS | SAINT GOBIN
22 | DEMOUNTABLE GLASS PARTITION | BAUX / BOTTOMLINE / KUBIC
23 | SCREWS (OXIDISED) | GKW
24 | DOOR CLOSERS | DORMA/GEZE
25 | HARDWARE (GLASS & FLUSH DOORS) | DORMA
26 | CABINET LOCKS/HINGES | EBCO
27 | PAINTS | ASIAN
28 | BLINDS | VISTA/HUNTER DUGLAS
29 | PVC PIPES ( CPVC / UPVC ) | ASHIRVAD
30 | ACOUSTICAL PANEL | VIVIDHA/KARIKA
31 | ALUMINIUM SKIRTING | BOTTOMLINE
32 | TRANSIT PROFILE | BOTTOMLINE
33 | SPORTS VINYL/VINYL | CLASSIC / SQUARE FOOT
34 | ALUMINIUM CORNER GUARD | BOTTOMLINE
35 | ANTI STATIC VINYL FLOORING | GERFLOOR
36 | TOILET CUBICALS | STYLAM/MERINO
37 | RAISED FLOORING TILES | UNI TILE
B | CARPET/MODULARS/CHAIRS
1 | MODULAR FURNITURE | AFC / SPACEWOOD / EQUIVALENT
2 | CHAIRS | FEATHERLITE / EQUIVALENT
3 | LOOSE FURNITURE | CUSTOMIZED
C | HVAC & ALLIED WORKS
1 | HIGH SIDE MATERIAL | TOSHIBA/CARRIER/DAIKIN
2 | COPPER PIPES AND FITTINGS | MEXFLOW/MANDEDV/TOTALLINE
3 | INLINE FAN | CARYAIRE/KRUGER/SYSTEMAIR
4 | DUCTS | ZECO/DEVDUCT/VEDHA
5 | FLEXIBLE DUCTS (INSULATED AND NON-INSULATED) | UP-TWIGA/SEVENSTAR
6 | AIR TERMINALS (SWIRL DIFFUSERS, GRILLS, DISC VALVES, NOZZLES, LOUVERS, NON-VISION DOOR GRILLS, COLLAR DAMPERS, HIT AND MISS DAMPERS, NRDS, VCDS, MVCDS, SOUND ATTENUATORS, CROSS TALK SILENCERS,SLOT DIFFUSER, BUTTERFLY DAMPERS) | AIRMASTER/SYSTEMAIR/COSMIC/CARYAIRE
7 | COMMUNICATION CABLES | LAPP/POLYCAB
8 | NITRILE RUBBER | K-FLEX/ARM FLEX
9 | THREADED ROD & SOLLOTED CHANNEL | MOONSHINE
10 | DRAIN PUMP | WIPCOOL/ASPEN
11 | DRAIN PIPE | VECTUS/ASTRAL
D | ELECTRICAL & ALLIED WORKS
CABLES & ACCESSORIES
1 | CABLES | KEI/POLYCAB
2 | CABLE LUGS/GLANDS | DOWELS/HMI
3 | CABLE TRAYS | PROFAB/CABLE TECH
WIRES & ACCESSORIES
1 | SINGLE CORE WIRES | KEI/POLYCAB
2 | THREE CORE FLEXIBLE WIRES (BLACK & WHITE) | KEI/POLYCAB
3 | CONDUIT PIPES & FITTINGS (PVC) | VIP /NATIONAL/PRECISSION
3 | CONDUIT PIPES & FITTINGS (MS) | BEC/GUPTA
4 | SWITCHES/SOCKETS | ANCHOR/LEGRAND
5 | METAL CLAD SOCKETS/IEC TYPE PLUG-SOCKETS | NEPTUNE BALLS
LIGHT FITINGS/FIXTURES
1 | LED FITTINGS | PHILPS/RIPPLE
2 | LED SPOT LIGHTS | PHILPS/RIPPLE
3 | DECORATIVE LIGHTS | CUSTOM MADE WITH PHILIPS / WIPRO FITTINGS
DB & MCB
1 | MCCB, MCB, DB, RCBO, ELCB | ABB/LEGRAND
2 | LT PANELS | CPRI APPROVED
E | FAS SYSTEM
1 | CONVENTIONAL FIRE ALARM SYSTEM | HONEYWELL/RAVEL
2 | SMOKE DETECTORS | HONEYWELL/RAVEL
3 | RESPONSE INDICATORS | HONEYWELL/RAVEL
4 | HOOTERS | HONEYWELL/RAVEL
5 | MANUALL CALL PINTS | HONEYWELL/RAVEL
6 | CABLES | POLYCAB/VARSHA
F | UPS SYSTEM
1 | UPS SYSTEM | VERTIV/APC
2 | CABLES | KEI
G | PA SYSTEM
1 | ANALOGUE PA SYSTEM | BOSCH
2 | SPEAKER | BOSCH
2 | CABLES | POLYCAB/VARSHA
H | NETWORK
1 | UTP Cable | D-Link
2 | I/O & Facepalet | D-Link
I | SIGNAGE
1 | Emergency EXIT/ FIRE EXIT Signs | Prolite,ETON,Henrich
J | EXTINGUISHER
1 | Extinguisher | EXCELLENT,SAFEX