## Summary
Project: Societe Generale_Bangalore
Subject: Summary of HVAC works
Date: 26-02-2026
Summary
SL.No | Description | Amount | Remarks
1 | HVAC Low side works | 6931014
2 | HVAC LEED & WELL | 479250
3 | LEED | 0
| Total Basic Amount | 7410264 |  | 7410264 | TRUE

## BOQ_HVAC Lowside works
Project :M/s Societe Generale Scope : HVAC Low side BOQ
SL.No | Description | Unit | Voyager (Qty) | Victor (Qty) |  | Total Qty | Rate |  | Amount |  | Total Amount | Remarks
|  |  | GF | 2F (Office) | 2F(Cafeteria) |  | Supply | Installation | Supply | Installation
A | AIR DISTRIBUTION
1 | Supply, fabrication, installation and testing of factory fabricated GSS ducts with flanges in accordance with the approved shop drawings and as per specifications.
Note: The entire ducts should be fabricated at factory and delivered to site in assembled condition. The contractors should include the transportation charges and necessary handling charges. The contractor should use only Hitech supports and full threaded rods to support the ducts as per the specification. After erection of the duct the entire duct should be tested for Duct leakage pressure test. The contractor should arrange the pressure test machine and the costing for the same to be included in the ducting price.
a) | 24 gauge galvanized sheet steel (0.63mm) (0-750mm) | Sqm | 94 | 320 | 40 | 454 | 836 | 228 | 379544 | 103512 | 483056 |  | 483056
b) | 22 gauge galvanized sheet steel (0.80mm) (751-1500mm) | Sqm | 90 | 94 | 0 | 184 | 922 | 228 | 169648 | 41952 | 211600 |  | 211600
c) | 20 gauge galvanized sheet steel (1.00mm)(1501-2100mm) | Sqm | 19 | 29 | 0 | 48 | 1007 | 228 | 48336 | 10944 | 59280 |  | 59280
[6 empty] | 0 | - | -
1.01 | Supply , fabrication, erection and commissioning of site fabricated rectangular ducts (using lock forming machines) using GI Sheet with 120 GSM in accordance with SMACNA standard The price shall include flanges, turning vanes, supports (factory fabricated, full threaded rod & slotted channel), sealant (neoprene gasket), hangers, access door etc. The joints shall be 100% leak proof and shall be tested with smoke testing. Note :- Leak test should be with Smoke leak test method and Air-balancing should be with Digital Hood method. Duct ends should be covered during construction so that it should be dust free. |  |  |  |  | 0 | - | -
a) | 24 gauge galvanized sheet steel (0.63mm) (0-750mm) | Sqm | 5 | 5 | RO | 10 | 836 | 228 | 8360 | 2280 | 10640 |  | 10640
b) | 22 gauge galvanized sheet steel (0.80mm) (751-1500mm) | Sqm | 5 | 5 | RO | 10 | 922 | 228 | 9220 | 2280 | 11500 |  | 11500
[6 empty] | 0 | - | -
1.02 | Factory made Elliptical ducting with Hitech Supports GSS Ducting.The duct should be internally insulated with 6 mm thick nitrile rubber. The ducts to be factory fabricated & two coats of spray paint as per the Architects colour specifications., Necessary bends should be made as per the drawing, two support & connecting rings should be considered for the same, costing for the same to be included in the ducting price. Note :- Leak test should be with Smoke leak test method and Air-balancing should be with Digital Hood method. Duct ends should be covered during construction so that it should be dust free. |  |  |  |  | 0 | - | -
| Please note that all elliptical duct should be delivered to the site with zinc chromate primer. |  |  |  |  | 0 | - | -
a) | 24 gauge galvanized sheet steel (0.63mm) (0-600mm) | Sqm | 290 | 20 | 0 | 310 | 1450 | 390 | 449500 | 120900 | 570400 |  | 570400
b) | 22 gauge galvanized sheet steel (0.8mm) (625-900mm) | Sqm | 300 | 10 | 0 | 310 | 1550 | 390 | 480500 | 120900 | 601400 |  | 601400
c) | 20 gauge galvanized sheet steel (0.8mm) (925-1200mm) | Sqm | 20 | 5 | 0 | 25 | 1650 | 390 | 41250 | 9750 | 51000 |  | 51000
d) | 18 gauge galvanized sheet steel (1.0 mm) (1225-1500mm) | Sqm | 30 | 5 | 0 | 35 | 1850 | 390 | 64750 | 13650 | 78400 |  | 78400
[6 empty] | 0 | - | -
1.03 | Supply & Installation of Factory fabricated Sound Attenuator of 0.8mm GSS Outer Casing & 0.8mm GSS Perforated inner baffles filled with inorganic fibre glass of Class O' Acoustic Material. Insertion loss should be approx. 18 dB to 23 dB. Min. Length should be 900 mm. | Sqm | 20 | 16 | RO | 36 | 5605 | 665 | 201780 | 23940 | 225720 |  | 225720
[6 empty] | 0 | - | -
1.04 | Factory fabricated, powder coated plenum with Double skin AHU construction of 25m thk PUF insulation of density 40kg/m3. Appropriate cut out to be made to connect the branch ducts with dampers as per approved drawing. 0.63 thk inner & outer skin. | Sqm | 25 | 25 | RO | 50 | 2850 | 380 | 142500 | 19000 | 161500 |  | 161500
[6 empty] | 0 | - | -
1.05 | Supply, fabrication, installation and testing of the flexible connections constructed out of fire resistant double canvas sleeve as per the approved shop drawings. | Sqm | 3 | 1 | RO | 4 | 1378 | 1140 | 5512 | 4560 | 10072 |  | 10072
[6 empty] | 0 | - | -
1.06 | Volume Control Damper |  |  |  |  | 0 | - | -
a) | Supply, installation and testing of GSS construction of 16G opposed blade volume control dampers within ducts to be provided with suitable links, levers and quadrants for manual control the volume of air flow.The end flanges should be of TDF. | Sqm | 4 | 8 | 1 | 13 | 6000 | 1300 | 78000 | 16900 | 94900 |  | 94900
b) | Supply & Installation of OVAL GSS Volume Control Dampers (18 G GSS)with operating handle for Supply air duct branches in accordance with the approved shop drawings and technical specifications. | Sqm | 15 | 1 | 0 | 16 | 8900 | 1300 | 142400 | 20800 | 163200 |  | 163200
[6 empty] | 0 | - | -
1.07 | Supply, installation, testing and commissioning of Motorized Fire and smoke damper with 450 mm extended sleeves for supply air ducts. Fire damper assembly should be CBRI approved Rated for 250C for 120min. Fire dampers shall be supplied with extended fire rated sleeves and Open/closed position indicator on the fire damper stem and body. | Sqm | 10 | 1 | RO | 11 | 9300 | 1500 | 102300 | 16500 | 118800 |  | 118800
[6 empty] | 0 | - | -
1.08 | Supply, installation, testing and commissioning of Spring return actuators for above mentioned Motorized fire and smoke dampers. The actuator shall be selected based on the respective fire damper size as per OEM recommendation. Actuators shall be suitable for BMS/Fire damper control panel connectivity with necessary accessories. The cost of Control cabling from fire damper panel to BMS DDC panel is included in BMS Vendor scope. Plug tops to be included in the cost.. The number of actuator shall be selected based on fire damper size as per OEM recommendation. The suitable torque shall be selected as per OEM recommendation. | Nos. | 12 | 10 | RO | 22 | 9000 | 1200 | 198000 | 26400 | 224400 |  | 224400
[6 empty] | 0 | - | -
1.09 | Supply, installation, testing and commissioning of Fire Damper control panel - The Vendor has to supply fire damper control panel to suit no of fire damper configuration in each AHU room . The number of fire dampers provided in other rooms shall be connected to the nearest fire damper panel in the AHU Room. The panel shall operate the fire dampers based on fire signal from fire panel. The panel shall give Open/ close status and panel trip status feed back to the BMS. The panel shall give 24V power supply to Actuators . The power and control panel to have manual push switch to test all fire damper manually. The power requirement & access requirement shall be coordinated with respective team by HVAC vendor. The unit shall be BMS compatible with MODBUS protocol. The Panel shall have power and control wiring and wiring from fire control panel to fire dampers. The UPS Power for control panel shall be provided by Electrical Team with 6 Amp socket within one meter distance as shown in the approved drawing. The Power cabling from nearest designated power socket with 6 Amp plug and cable should be considered by HVAC vendor. | Nos. | 2 | 1 | RO | 3 | 15960 | 1425 | 47880 | 4275 | 52155 |  | 52155
[6 empty] | 0 | - | -
1.1 | Motorized Damper(ON/OFF Type) |  |  |  |  | 0 | - | -
| The supply & Installation of the volume control damper with the outer shell constructed of 16G thick galvanized steel frame and the blade/Leaf with 16G GSS. And with flanges for connection. The Damper to be provided with necessary high torque Actuator working on 24V AC/DC. and control panel with step down transformer, indicator, provision for remote control operation & monitoring etc. Refer tender drawings for more details. |  |  |  |  | 0 | - | -
| The number of Actuator per damper is based on the number of damper required for the project as per drawing. However if the damper size exceeds 1.5sqmt, the number of actuator per damper can be selected 2 or more based on manufacturer selection and requirement for the smooth operation. |  |  |  |  | 0 | - | -
| Necessary control contactors with power and control cabling shall be considered for interlocking motorized dampers with respective indoor units. Necessary Adapters / Contactors / control panels to be considered for interlocking of MVCD's of respective units. |  |  |  |  | 0 | - | -
a | Dampers | Sqm | RO | RO | RO | 0 | - | -
b | Actuator | Nos | RO | RO | RO | 0 | - | -
[6 empty] | 0 | - | -
1.11 | SUPPLY, INSTALLATION, TESTING AND COMMISSIONING OF Fusible link type fire dampers with 450 mm extended sleeves For return , exhaust and Fresh air application.Fire damper assembly should be CBRI certified Rated for 250C for 120min, the link should be open at 74 C . Dampers shall be spring return type and have a limit switch. Fire dampers should be supplied with extended fire rated sleeves suitable for mounting across fire rated walls. The access space requirement shall be coordinated with respective teams by HVAC vendor.The sizes as shown in Approved drawing. | Sqm | 1 | 1 |  | 2 | 8265 | 1710 | 16530 | 3420 | 19950 |  | 19950
[6 empty] | 0 | - | -
1.12 | Supply,installation,testing and balancing of square type extruded aluminium powder coated diffusers for supply air required as per the approved shop drawings. Diffuser shall be with spring loaded removable core type distribution grid. |  |  |  |  | 0 | - | -
| Extruded Aluminium diffusers powder coated: |  |  |  |  | 0 | - | -
a) | 375x375 (Neck size) overall size 596 x 596 | Nos. | RO | RO | RO | 0 | - | -
b) | 300x300 (Neck size) overall size 596 x 596 | Nos. | RO | RO | RO | 0 | - | -
c) | 225x225 (Neck size) overall size 596 x 596 | Nos. | RO | RO | RO | 0 | - | -
d) | Round diffusers(315 dia neck size) with collar damper | Nos. | 1 | RO | RO | 1 | 1378 | 357 | 1378 | 357 | 1735 |  | 1735
[6 empty] | 0 | - | -
1.13 | Supply,installation,testing and balancing of square type extruded aluminium powder coated diffusers for Return air required as per the approved shop drawings. Diffuser shall be with spring loaded removable core type distribution grid. |  |  |  |  | 0 | - | -
| Extruded Aluminium diffusers powder coated: |  |  |  |  | 0 | - | -
a) | 375x375 (Neck size) overall size 596 x 596 | Nos. | RO | RO | RO | 0 | - | -
b) | 300x300 (Neck size) overall size 596 x 596 | Nos. | RO | RO | RO | 0 | - | -
c) | 225x225 (Neck size) overall size 596 x 596 | Nos. | RO | RO | RO | 0 | - | -
d) | Round diffusers(250 dia neck size) without collar damper | Nos. | RO | RO | RO | 0 | - | -
[6 empty] | 0 | - | -
1.14 | Supply,installation,testing & balancing of continuous linear fixed bar extruded aluminium powder coated return air grilles normal flow 45° / 15°/0° one way/two way deflection with all sides flanged without dampers. |  |  |  |  | 0 | - | -
a) | 100mm high | Rmt | RO | RO | RO | 0 | - | -
b) | 150mm high | Rmt | RO | RO | RO | 0 | - | -
c) | 1800x600mm linear grille for return air | Nos | RO | RO | RO | 0 | - | -
d) | linear Grille(various sizes as per drawing) | sqmt | 3 | 3 | 1.5 | 7.5 | 4589 | 1045 | 34417.5 | 7837.5 | 42255 |  | 42255
e) | 600x600 mm grille with damper | Nos | RO | RO | RO | 0 | - | -
[6 empty] | 0 | - | -
1.15 | Supply & installation of Al.Collar damper | Sqm | 1 | 2 | 2 | 5 | 4750 | 475 | 23750 | 2375 | 26125 |  | 26125
[6 empty] | 0 | - | -
1.16 | Supply,installation,testing & balancing of linear fixed bar extruded aluminium powder coated supply air grilles with 450 x 100 size with normal flow 45° / 15°/0° one way/two way deflection with all sides flanged with collar dampers. The Grille should be mounted as indicated in the layout. | Nos | RO | RO | RO | 0 | - | -
[6 empty] | 0 | - | -
1.17 | Supply,installation,testing & balancing of curved fixed bar extruded aluminium powder coated curved type supply air grilles as per drawing with normal flow 45° / 15°/0° one way/two way deflection with all sides flanged with collar dampers. The Grille should be mounted on the surface of the elliptical ducts. | Sqm | 6 | 5 | RO | 11 | 10194 | 3325 | 112134 | 36575 | 148709 |  | 148709
[6 empty] | 0 | - | -
1.18 | Supply & installation of flexible duct of following sizes with fire retardant Al.foil sheet.Metalized polyester is not acceptable. Note: Universal clamp should be provided to fix the flexible duct in the spigots and covered with tape. If the flexible duct length is beyond 1500 mm, then circular clip with chain to be provided to support the flexible duct. |  |  |  |  | 0 | - | -
a) | DIA 150 mm | Rmt | RO | RO | RO | 0 | - | -
b) | DIA 200 mm | Rmt | 7 | 9 | RO | 16 | 600 | 120 | 9600 | 1920 | 11520 |  | 11520
c) | DIA 250 mm | Rmt | RO | 62 | RO | 62 | 750 | 140 | 46500 | 8680 | 55180 |  | 55180
[6 empty] | 0 | - | -
1.19 | Supply & installation Spigot & Butterfly damper of following sizes. It should be of 22G. |  |  |  |  | 0 | - | -
a) | DIA 150 mm | Nos. | RO | RO | RO | 0 | - | -
b) | DIA 200 mm | Nos. | 7 | 9 | RO | 16 | 965 | 193 | 15440 | 3088 | 18528 |  | 18528
c) | DIA 250 mm | Nos. | RO | 62 | RO | 62 | 1240 | 248 | 76880 | 15376 | 92256 |  | 92256
d) | DIA 300 mm | Nos. | RO | RO | RO | 0 | - | -
[6 empty] | 0 | - | -
1.2 | Supply & installation of round duct of following sizes. It should be of 24G. |  |  |  |  | 0 | - | -
a) | DIA 150 mm | Rmt | RO | RO | RO | 0 | - | -
b) | DIA 200 mm | Rmt | 7 | 9 | RO | 16 | 221 | 57 | 3536 | 912 | 4448 |  | 4448
c) | DIA 250 mm | Rmt | RO | 62 | RO | 62 | 242 | 57 | 15004 | 3534 | 18538 |  | 18538
d) | DIA 300 mm | Rmt | RO | RO | RO | 0 | - | -
[6 empty] | 0 | - | -
1.21 | Supply & installation of factory fabricated Spill Air Plenum / Mixing boxes of 1200 X 100 X 350 size . Note: The mixing Box to be properly supported and should be erected as per our drawing.it has to be fabricated at factory and delivered to site. | Nos. | 7 | 71 | RO | 78 | 1650 | 440 | 128700 | 34320 | 163020 |  | 163020
[6 empty] | 0 | - | -
1.22 | Supply & installation of factory fabricated Spill Air Plenum / Mixing boxes of 1000 X 150 X 350 size . Note: The mixing Box to be properly supported and should be erected as per our drawing.it has to be fabricated at factory and delivered to site. | Nos. | RO | RO | RO | 0 | - | -
[6 empty] | 0 | - | -
1.23 | Supply & installation of factory fabricated Spill Air Plenum / Mixing boxes of 1500 X 150 X 350 size . Note: The mixing Box to be properly supported and should be erected as per our drawing.it has to be fabricated at factory and delivered to site. | Nos. | RO | RO | RO | 0 | - | -
[6 empty] | 0 | - | -
1.24 | Supply and installation of Z type speech privacy duct of 24G (as per drawing) with 10mm thk acoustic open cell nitrile rubber. Length shall be 1500mm. |  |  |  |  | 0 | - | -
a) | 250mm Wide | Nos | RO | RO | RO | 0 | - | -
b) | 300mm Wide | Nos | 7 | 7 | RO | 14 | 2375 | 475 | 33250 | 6650 | 39900 |  | 39900
c) | 350mm Wide | Nos | RO | RO | RO | 0 | - | -
d) | 400mm Wide | Nos | RO | RO | RO | 0 | - | -
e) | 450mm Wide | Nos | RO | RO | RO | 0 | - | -
[6 empty] | 0 | - | -
1.25 | Supply, installation, testing & commissioning of slot diffuser with hit & miss damper. The diffuser shall be of extruded aluminium type with powder coat finish. |  |  |  |  | 0 | - | -
a) | 2 slot with hit & Miss damper | Rmt | 10 | 10 | RO | 20 | 1300 | 260 | 26000 | 5200 | 31200 |  | 31200
b) | 2 slot without hit & miss damper | Rmt | 20 | 20 | RO | 40 | 1100 | 210 | 44000 | 8400 | 52400 |  | 52400
[6 empty] | 0 | - | -
1.26 | Air balancing for the entire office space. The vendor need to arrange the third party agency & submit the report for consultant's approval. | Nos. | 1 | 1 | 1 | 3 |  | 80750 |  | 242250 | 242250 |  | 242250
[6 empty] | 0 | - | -
1.27 | Associated civil works such as wall opening to take the duct & chw. pipes and closing of the same in proper manner. After erection of the S/A & R/A duct, the balance gaps need to sealed by using brick & mortar in all the AHU Room. The AC vendor is responsible for the same. C angle to be considered to close the wall opening above the fire dampers. | Lot | RO | RO | RO | 0 | - | -
[6 empty] | 0 | - | -
1.28 | Supply, installation, of Aluminium Louver with Bird Mesh in accordance with the approved shop drawings and specifications.The louver shall be with 45 deg deflection and shall prevent rain water entry through the louvers. | Sqm | RO | 1 | RO | 1 | 6888 | 3325 | 6888 | 3325 | 10213 |  | 10213
[6 empty] | 0 | - | -
1.29 | AHU filter covering cloth (cora) during commissioning stage | Nos. | 2 | 1 | RO | 3 | 4275 | 475 | 12825 | 1425 | 14250 |  | 14250
[6 empty] | 0 | - | -
1.3 | Disc valves 150 dia | Nos | RO | RO | RO | 0 | - | -
[6 empty] | 0 | - | -
1.31 | Supply & installation of 150 dia rigid flexible duct | Rmt | RO | RO | RO | 0 | - | -
[6 empty] | 0 | - | -
1.32 | Supply & installation of 150 dia butterfly damper | Nos | RO | RO | RO | 0 | - | -
[6 empty] | 0 | - | -
C | INSULATION |  |  |  |  | 0 | - | -
1 | supply, installation, testing and commissioning of Acoustic insulation for GI Supply air ducts and return air ducts. Acoustic material shall be 15 mm thick open cell elastomeric foam class 1 The density shall be 140 kg.m3 with thermal conductivity of 0.05 W/ m Deg K.Material shall have antibacterial properties The insulation shall be as per technical specification and drawings etc, All joints to be sealed with anti condensation tapes. | Sqm | 55 | 65 | 40 | 160 | 900 | 150 | 144000 | 24000 | 168000 |  | 168000
[6 empty] | 0 | - | -
2 | Thermal insulation of ducts using 9 mm thick cold insulation using closed cell Nitrile rubber (class "O") insulation without aluminium foil in sections stuck to the inside of the duct & fixtures using manufacturer approved cold adhesive on both surface of the duct and inner face of the insulation. | Sqm | 30 | 385 | 0 | 415 | 310 | 110 | 128650 | 45650 | 174300 |  | 174300
[6 empty] | 0 | - | -
3 | Supply and installation of Under deck insulation with Expanded polystyrene of 13mm thick & 40-60 kg/cum density in sheet form. with fire retardant adhesive and joints sealed in accordance with the approved shop drawings and technical specifications. Quoted price shall be inclusive of adhesive, etc. | Sqm | RO | RO | RO | 0 | - | -
[6 empty] | 0 | - | -
4 | CABINET TYPE INLINE FANS |  |  |  |  | 0 | - | -
5 | The supply, installation, testing and commissioning of cabinet type fan, 20 mm ESP with all accessories like fan, motor, flanges, non-canvass type fire retardant flexible connections, etc., The impeller shall be of forward type. The motor should be of IP 21, class 'F' insulation suitable for operating at 1Ph, 230V, 50hz power supply. |  |  |  |  | 0 | - | -
a) | 300 cfm with 20mm static for Cafe Fresh air | Nos | RO | RO | RO | 0 | - | -
b) | 1200 cfm with 20mm static for Cafe General exhaust | Nos | RO | RO | RO | 0 | - | -
[6 empty] | 0 | - | -
6 | DRY SCRUBBER comprising of Prefilter, electrostatic precipitator module, Adsorbed Module along with System controls all housed in a unit as indicated in specifications. The Electrostatic section shall be made of 16 Gauge galvanized sheet, high bake epoxy powder coated, washable type Aluminum mesh pre filters, spiked ionizers to create high voltage DC field, aluminum collector plates which should be alternatively charged positive and negative with large collecting area, to work as magnet for charged smoke and oil particles. Particle efficiency of 90-95% as per ASHRAE test method. Collector cell should be of permanent type and incorporate facility for easy removal for cleaning. The system should be fitted with appropriate overload protection and safety interlock. No ionizing wires are acceptable. Operating Voltage – 220V, 50 Hz Single Phase for dry scrubber, Ionizing Voltage – < 13 KVDC. Collector Cell Voltage – < 7 KVDC. From electrical DB to unit - Power/communication cables, GI Perforated cable tray, glands, body earthing with end terminations are part of the BOQ. capacity should be considered as below. |  |  |  |  | 0 | - | -
a) | 2500 cfm | Nos | RO | RO | RO | 0 | - | -
b) | 2000 cfm | Nos | RO | RO | RO | 0 | - | -
[6 empty] | 0 | - | -
7 | Supply, installation, testing and commissioning of 200 CFM Duct Inline fan (explosion proof) for battery exhaust system with H2 sensor & it should be with 25mm static pressure with timer for the battery room. Fan will run at predetermined speed based on the timer setting & also based on the H2 concentration. The necessary starter panel to be considered in the costing. | Nos | RO | RO | RO | 0 | - | -
[6 empty] | 0 | - | -
8 | ELECTRICAL WORKS |  |  |  |  | 0 | - | -
| Supply & installation of cabling works |  |  |  |  | 0 | - | -
a) | 4 C X 10 Sqmm Cu. Cable | Rmt | RO | RO | RO | 0 | - | -
b) | 4 C X 6 Sqmm Cu. Cable | Rmt | RO | RO | RO | 0 | - | -
c) | 3 C X 4 Sqmm Cu. Cable | Rmt | RO | RO | RO | 0 | - | -
d) | 2 C X 1.5 Sqmm Cu. Cable | Rmt | RO | RO | 50 | 50 | 108 | 25 | 5400 | 1250 | 6650 |  | 6650
e) | Earthing 25 X 6 GI flat | Rmt | RO | RO | RO | 0 | - | -
f) | 8SWG GI | Rmt | RO | RO | RO | 0 | - | -
g) | 25mm MS Conduits | Rmt | RO | RO | RO | 0 | - | -
h) | Cable Trays 150 mm wide | Rmt | RO | RO | RO | 0 | - | -
[6 empty] | 0 | - | -
9 | Supply & installation of starter panel with auto manual selector switch & it should be with potential free contact for FA & BMS integration |  |  |  |  | 0 | - | -
a) | 5 HP | Nos | RO | RO | RO | 0 | - | -
b) | 2 HP | Nos | RO | RO | RO | 0 | - | -
c) | 0.5 HP | Nos | RO | RO | 1 | 1 | 20900 | 1425 | 20900 | 1425 | 22325 |  | 22325
[6 empty] | 0 | - | -
D | REFURBICATION WORKS |  |  |  |  | 0 | - | -
1 | Removal, storing existing duct refurbed area as per the design requirement | Sqm | RO | RO | 50 | 50 |  | 475 |  | 23750 | 23750 |  | 23750
[6 empty] | 0 | - | -
2 | Removal, storing & reinstallation of the existing ductwork in the refurbed area as per the design requirement | Sqm | RO | RO | RO | 0 | - | -
[6 empty] | 0 | - | -
3 | Removal, storing & reinstallation of the existing air terminals along with spillair box, butterfly damper in the refurbed area as per the design requirement | Lot | RO | RO | RO | 0 | - | -
| SUB TOTAL FOR HVAC LOWSIDE WORKS | [5 empty] | - | - | 3475262.5 | 1040262.5 | 4515525
[6 empty] | 0 | - | -
A | CHILLED WATER WORKS |  |  |  |  | 0 | - | -
1 | Supply, Installation, Testing & Commissioning of blow through Chilled water Fan coil Units of following capacity. Fan Coil unit with Fan, Aluminium filter, 3- speed motor,3 row deep cooling Coil, ball valve with strainer for inlet & without strainer at outlet, flexible connection, airvent, with auxiliary extended insulated stainless steel sandwiched drain pan, FCU inclusive of Digital type thermostat which will be compatible to hardwired BMS along with on/off /trip/speed control,ball valve with strainer for inlet, without strainer at outlet & 2 way modulating type PIBCV (0 to 10 VDC & 4 to 20 mA) with control cabling including conduits & all accessories etc.(All FCU airflow should be selected at medium speed). Computerized fan selection to be approved by consultants before procurement in terms of Outlet Velocity, efficiency and noise level. Quoted price shall be inclusive of 19mm thick Nitrile rubber insulation for Valve package. Cassette unit shall be inbuilt controller to integrate with BMS compatibility. |  |  |  |  | 0 | - | -
a | Chilled water FCU - 1200 CFM/3TR | Nos | RO | RO | RO | 0 | - | -
[6 empty] | 0 | - | -
2 | Supply & Installation of MS class ‘C’ pipes for chilled water pipe to required lengths and installed with all welded joints, providing and fixing in position with the necessary fittings like elbows, tees and reducers, Supports (Hitech support). Quoted price shall be including the Nitrile rubber insulation as indicated below |  |  |  |  | 0 | - | -
a) | 80 mm dia | Rmt | RO | RO | RO | 0 | - | -
b) | 65 mm dia | Rmt | RO | RO | RO | 0 | - | -
c) | 50 mm dia | Rmt | RO | RO | RO | 0 | - | -
d) | 40 mm dia | Rmt | RO | RO | RO | 0 | - | -
e) | 32 mm dia | Rmt | RO | RO | RO | 0 | - | -
f) | 25 mm dia | Rmt | RO | RO | RO | 0 | - | -
[6 empty] | 0 | - | -
3 | Supply & Installation of 'CLASS-O' Elastomeric nitrile rubber insulation of preformed pipe section & Insulation to be covered with 24G Aluminium Cladding. Quoted price shall be inclusive of Adhesive, Nitrile rubber tapes, Aluminium Cladding etc The thermal conductivity should not exceed 0.025 w/m k. |  |  |  |  | 0 | - | -
a) | 80 mm dia with 25mm thick insulation | Rmt | RO | RO | RO | 0 | - | -
b) | 65 mm dia with 25mm thick insulation | Rmt | RO | RO | RO | 0 | - | -
c) | 50 mm dia with 25mm thick insulation | Rmt | RO | RO | RO | 0 | - | -
d) | 40 mm dia with 25mm thick insulation | Rmt | RO | RO | RO | 0 | - | -
e) | 32 mm dia with 25mm thick insulation | Rmt | RO | RO | RO | 0 | - | -
f) | 25 mm dia with 19mm thick insulation | Rmt | RO | RO | RO | 0 | - | -
[6 empty] | 0 | - | -
4 | Supply & Installation of Butterfly valves with matching flanges. The valves should have feasibility of changing the inner lining if worn out and the handles should have lockable facility.The valves shall hold the water without the leakage. Valves to have long neck to facilitate thermal insulation of valves.shall be insulated to the same thickness as the pipe to which they are connected. |  |  |  |  | 0 | - | -
a) | 80 mm dia | Nos | RO | RO | RO | 0 | - | -
b) | 65 mm dia | Nos | RO | RO | RO | 0 | - | -
c) | 50 mm dia | Nos | RO | RO | RO | 0 | - | -
d) | 40 mm dia - Ball Valve | Nos | RO | RO | RO | 0 | - | -
e) | 25 mm dia - Ball Valve | Nos | RO | RO | RO | 0 | - | -
[6 empty] | 0 | - | - | 0 | 0 | 0
| SUBTOTAL CHILLED WATER WORKS | [5 empty] | - | -
[7 empty] | - | -
A | VARIABLE REFRIGERANT VOLUME SYSTEM |  |  |  |  | 0 | - | -
[6 empty] | 0 | - | - | 0 | 0 | 0
| Supply, Installation, Testing & Commissioning of inverter based compressor with Variable refrigerant system connectable to multiple indoor units. Outdoor unit shall be factory assembled weather proof casing constructed from heavy gauge mild steel panels. The unit shall be completely factory wired and tested with necessary controls. The compressor shall be highly efficient scroll type and one compressor shall be capable of inverter controller. The aluminum fins shall be covered with anti-corrosion resin. Unit shall be equipped with oil recovery system to ensure stable operation with long refrigerant piping. The scope shall include the supply of the necessary power and control cable, the required ODU stand with rubber padding. |  |  |  |  | 0 | - | - | 0 | 0 | 0
1 | OUTDOOR UNITS |  |  |  |  | 0 | - | -
| Supply, Installation, Testing & Commissioning of inverter based compressor with Variable refrigerant system connectable to Air Handling units. Outdoor unit shall be factory assembled weather proof casing constructed from heavy gauge mild steel panels. The unit shall be completely factory wired and tested with necessary controls. The compressor shall be highly efficient scroll type and one compressor shall be capable of inverter controller. The aluminum fins shall be covered with anti-corrosion resin. Unit shall be equipped with oil recovery system to ensure stable operation with long refrigerant piping. The unit shall be compatible for BMS operation- Necessary relay card /soft integrator to be provided. The necessary covel piece with painting shall be provided by the contractor for the ODUs. |  |  |  |  | 0 | - | -
a) | 6HP - Outdoor units | Nos | 2 | RO | RO | 2 | 128250 | 5700 | 256500 | 11400 | 267900 |  | 267900
[6 empty] | 0 | - | -
2 | Indoor Units |  |  |  |  | 0 | - | -
| Supply, Installation, Testing & Commissioning of Indoor Units shall be either Ceiling mounted duct able as specified. The indoor unit shall have independent electronic control valve to control the refrigerant flow rate respond to variations of the air-conditioning load of the room. The fan shall be aerodynamically designed turbo multiplied type. Statically and dynamically balanced to ensure lowest noise. The cooling coil shall be made of seamless copper tube. The tube shall be hydraulically or mechanically expanded and tested for 21 Kg/cm2. Indoor units shall have a wireless remote control. With including Refnet joints and cordless/corded remote controller for all indoors. |  |  |  |  | 0 | - | -
| Indoor Unit(IDU): Cooling Only : All the units should be supplied with Cordless remote control. The following Indoor unit capacities are required for each Floor. Double layer Canvas connection for each csu unit shall be a part of scope. |  |  |  |  | 0 | - | -
a) | 4.5TR /1624 CFM Ceiling mounted duct type unit | Nos | 2 | RO | RO | 2 | 47500 | 3800 | 95000 | 7600 | 102600 |  | 102600
[6 empty] | 0 | - | -
B | INSTALLATION, TESTING & COMMISSIONING OF VRF WORKS |  |  |  |  | 0 | - | -
| Supply, Installation of copper piping with necessary fittings imported fittings, Y-joints and headers etc.(This includes the pressure testing and refrigerant charge and electrical & Control cable between IDU&ODU and MCB(provided by others) to ODU etc.). The vendor shall quote as a lump sum value as per the approved drawing for the above works. In Case any changes in the layout after approval, then the following unit rates shall be applicable. |  |  |  |  | 0 | - | -
1 | Refrigerant Piping |  |  |  |  | 0 | - | -
| Interconnecting copper refrigerant pipe work duly insulated with elastomeric nitrile rubber type tubular insulation between indoor & outdoor units as per specifications . All piping inside the room shall be properly supported with hanger and all external piping shall run in covered cable tray. The cost should include for cable tray also. |  |  |  |  | 0 | - | -
a) | 41.3mm OD (insulation =19mm thick) | Rmt | RO | RO | RO | 0 | - | -
b) | 38.1mm OD (insulation =19mm thick) | Rmt | RO | RO | RO | 0 | - | -
c) | 34.9mm OD (insulation =19mm thick) | Rmt | RO | RO | RO | 0 | - | -
d) | 31.8mm OD (insulation =19mm thick) | Rmt | RO | RO | RO | 0 | - | -
e) | 28.6mm OD (insulation =19mm thick) | Rmt | RO | RO | RO | 0 | - | -
f) | 25.4mm OD (insulation =19mm thick) | Rmt | RO | RO | RO | 0 | - | -
g) | 22.2mm OD (insulation =19mm thick) | Rmt | RO | RO | RO | 0 | - | -
h) | 19.1mm OD (insulation =13mm thick) | Rmt | RO | RO | RO | 0 | - | -
i) | 15.9mm OD (insulation =13mm thick) | Rmt | 160 | 0 | 0 | 160 | 930 | 190 | 148800 | 30400 | 179200 |  | 179200
j) | 12.7mm OD (insulation =13mm thick) | Rmt | RO | RO | RO | 0 | - | -
k) | 9.5mm OD (insulation =13mm thick) | Rmt | 160 | 0 | 0 | 160 | 700 | 210 | 112000 | 33600 | 145600 |  | 145600
l) | 6.4mm OD (insulation =13mm thick) | Rmt | RO | RO | RO | 0 | - | -
[6 empty] | 0 | - | -
2 | Transmission & Control Wiring |  |  |  |  | 0 | - | -
a) | Providing & fixing control cum trans-mission wiring in Perforated Cable tray supported from the slab in the ceiling slab and in terrace supported in totality from the floor (between indoor and outdoor unit.) |  |  |  |  | 0 | - | -
| (2 core x 1.5 Sq. mm cu.cable ) | Rmt | 160 | 0 | 0 | 160 | 108 | 25 | 17280 | 4000 | 21280 |  | 21280
b) | Control cabling for corded Remotes thru PVC Conduit | Rmt | RO | RO | RO | 0 | - | -
| (2 Core x 1.0 sqm) | Rmt | RO | RO | RO | 0 | - | -
[6 empty] | 0 | - | -
3 | Installation, testing, commissioning of Imported Equipment including topping up of Refrigerant R-410A | Kg | 8 | RO | RO | 8 | 950 | 333 | 7600 | 2664 | 10264 |  | 10264
[6 empty] | 0 | - | -
4 | AUTO SEQUENTIAL CONTROL PANEL | No. | 1 | RO | RO | 1 | 19000 | 2375 | 19000 | 2375 | 21375 |  | 21375
| Supply & installation of Auto sequential control panel for the UPS Room VRV AC units. The panel should have the following features. |  |  |  |  | 0 | - | -
| 1. A/C units shall be able to restart automatically after power failure/interruption. 2. Automatic fault changeover 3. Sequential changeover of operating units every 12 hours. 4. Normally two duty and one standby units. If high temp reached, both units shall be in operation to cool down the room. 5.Should generate an alarm if the unit trips or the room temperature goes beyond the set point |  |  |  |  | 0 | - | -
[6 empty] | 0 | - | -
6 | Supply, installation testing and Commissioning of Cable trays for Refrigerant Pipes. Pre galvanized for indoor conditioned space and Hot dip galvanized for outdoor conditions with cover. |  |  |  |  | 0 | - | -
a) | 100x75mm (perforated type cable tray) | Rmt | RO | RO | RO | 0 | - | -
b) | 100x75mm (Ladder type cable tray) | Rmt | RO | RO | RO | 0 | - | -
c) | 150x75mm (perforated type cable tray) | Rmt | 10 | RO | RO | 10 | 447 | 100 | 4470 | 1000 | 5470 |  | 5470
d) | 150x75mm (Ladder type cable tray) | Rmt | RO | RO | RO | 0 | - | -
e) | 300x75mm with cover | Rmt | 65 | 0 | 0 | 65 | 900 | 90 | 58500 | 5850 | 64350 |  | 64350
f) | 300x75mm (Perforated type cable tray) | Rmt | 20 | 0 | 0 | 20 | 50 | 90 | 1000 | 1800 | 2800 |  | 2800
[6 empty] | 0 | - | -
7 | Supply & installation of rigid CPVC drain piping insulated with 6 mm thick closed cell elastomeric Nitrile rubber. The condensate drain pipe shall be with Pipe-in Pipe-out system. |  |  |  |  | 0 | - | -
a) | 25mm Dia | Rmt | RO | RO | RO | 0 | - | -
b) | 32mm Dia | Rmt | 25 | RO | RO | 25 | 190 | 48 | 4750 | 1200 | 5950 |  | 5950
c) | 40mm Dia | Rmt | RO | RO | RO | 0 | - | -
d) | 50mm Dia | Rmt | RO | RO | RO | 0 | - | -
[6 empty] | 0 | - | -
8 | Plain cable tray for laying of Drain pipes in ceiling level with supports at 1m interval. |  |  |  |  | 0 | - | -
a) | 300x75mm | Rmt | RO | RO | RO | 0 | - | -
b) | 100x75mm | Rmt | 25 | RO | RO | 25 | 390 | 86 | 9750 | 2150 | 11900 |  | 11900
[6 empty] | 0 | - | -
9 | Electrical Works for VRF System |  |  |  |  | 0 | - | -
a) | Suitable size power cable from Isolator to the ODUs' | Rmt | 10 | RO | RO | 10 | 796 | 29 | 7960 | 290 | 8250 |  | 8250
[6 empty] | 0 | - | -
10 | Condensate drain pump with 2L net capacity. The necessary supporting arrangements to be considered for ceiling suspended type pump installation | No. | 2 | RO | RO | 2 | 4750 | 475 | 9500 | 950 | 10450 |  | 10450
[6 empty] | 0 | - | - | 0 | 0 | 0
| SUB TOTAL FOR VRF UNIT WORKS | [5 empty] | - | - | 752110 | 105279 | 857389
[6 empty] | 0 | - | -
A | VARIABLE AIR VOLUME BOXES (Honeywell make) |  |  |  |  | 0 | - | -
[6 empty] | 0 | - | - | 0 | 0 | 0
1 | Supply, installation, testing and commissioning of Pressure Independent VAV Boxes with digital thermostat. The co2 sensors & occupancy sensor signal cabling will be taken through the VAV controller and the VAVs should have the provision to accept the signal for air qty, modulation. The contractors should include the transportation charges and necessary handling charges. The contractor should use only with hitech threaded rod supports with required accessories to support the ducts as per the specification |  |  |  |  | 0 | - | -
| Note: The VAV Boxes should be factory calibrated and it should be instruct at factory by PMC or consultant. |  |  |  |  | 0 | - | -
| The color of the thermostat shall be confirmed based on the Architect approval. |  |  |  |  | 0 | - | -
| Size of the VAV Boxes is as under :- VAV Box need to be selected 20% extra CFM in compared to the designed CFM |  |  |  |  | 0 | - | -
1.1 | Digital Thermostat with Temperature & Occupancy sensor |  |  |  |  | 0 | - | -
[6 empty] | 0 | - | -
a | Size 6" Vav Box : 60 - 500 CFM VAV BOX | Nos | 9 | 10 | RO | 19 | 20900 | 2375 | 397100 | 45125 | 442225 |  | 442225
[6 empty] | 0 | - | -
b | Size 8" Vav Box : 105 - 900 CFM VAV BOX | Nos | 5 | 10 | 1 | 16 | 21375 | 2375 | 342000 | 38000 | 380000 |  | 380000
[6 empty] | 0 | - | -
c | Size 10" Vav Box : 165 - 1400 CFM VAV BOX | Nos | 3 | 5 | RO | 8 | 21850 | 2375 | 174800 | 19000 | 193800 |  | 193800
[6 empty] | 0 | - | -
d | Size 12" Vav Box : 240 - 2000 CFM VAV BOX | Nos | 5 | 1 | 1 | 7 | 22800 | 2375 | 159600 | 16625 | 176225 |  | 176225
[6 empty] | 0 | - | -
e | Size 14" Vav Box : 320 - 3000 CFM VAV BOX | Nos | RO | RO | RO | 0 | - | -
[6 empty] | 0 | - | -
f | Size 16" Vav Box : 400 - 5000 CFM VAV BOX | Nos | 1 | RO | RO | 1 | 24225 | 2375 | 24225 | 2375 | 26600 |  | 26600
[6 empty] | 0 | - | -
1.2 | Supply & installation of 1 " dia .PVC conduits complete with all fittings and accessories | RM | 330 | 390 | 30 | 750 | 50 | 15 | 37500 | 11250 | 48750 |  | 48750
[6 empty] | 0 | - | -
1.3 | Supply & installation of PVC Cu Conductor Control Cabling |  |  |  |  | 0 | - | -
a) | 4 C X 1.5 Sqm. | Rmt | 330 | 390 | 30 | 750 | 175 | 35 | 131250 | 26250 | 157500 |  | 157500
b) | 2 C X 1.5 Sqm. | Rmt | RO | RO | RO | 0 | - | -
c) | CAT 6 cable for bus communication | Rmt | RO | RO | RO | 0 | - | -
[6 empty] | 0 | - | -
1.4 | Supply & installation of Powder coated perforated cable trays with Top Cover (Necessary support items should be part of the costing) U-clams to be used for cable trays support. [Color to match with interior requirement] Before procuring vendor to obtain sample approval for the product from Client. |  |  |  |  | 0 | - | -
a) | 50 mm wide | Rmt | RO | RO | RO | 0 | - | -
[6 empty] | 0 | - | -
1.5 | Supply & installation of VAV Bacnet controller/ Modbus card with wall mountable metallic enclosure for BMS integration. | Nos | 1 | 1 | RO | 2 | 61750 | 4750 | 123500 | 9500 | 133000 |  | 133000
[6 empty] | 0 |  |  | 0 | 0 | 0 |  | 0
1.6 | Removal, re-installation, testing commissioning of existing VAVs' as per the design requirement. | Nos | RO | RO | RO | 0 |  |  | 0 | 0 | 0 |  | 0
[6 empty] | 0 |  |  | 0 | 0 | 0
| SUB TOTAL FOR VAV WORKS | [7 empty] | 1389975 | 168125 | 1558100
[11 empty] | 6931014 |  | 6931014

## BOQ_HVAC LEED & WELL
Project :M/s Societe Generale Scope : LEED & WELL BOQ
S. No. | Description | Unit | Voyager (Qty) | Victor (Qty) | Total Qty | Rate |  | Amount |  | Total Amount | Remarks
|  |  | Ground | Level-02 |  | Supply | Installation | Supply | Installation
1 | IAQ TEST :
| Indoor air quality test to be conducted at 6 locations in the floor space before & 6 locations after occupancy. (Please note that vendor has to repeat the IAQ test till it achieves the acceptance level), Flush out activities for the office area before IAQ Test. Required Exhaust fans including supply, installation and dismantle after the Flush out activities to be considered . The below Following tests to be conducted for IAQ & IAQ Testing as per LEED v4. The IAQ testing lab needs to be carried out with the NABL-certified team. | Lot | 1 | 1 | 2 |  | 30000 | 0 | 60000 | 60000 |  | 60000
| a) RESPIRABLE PARTICULATE MATTER (RSPM) b) CARBON MONOXIDE c) CARBON DIOXIDE d) OXIDES OF SULPHUR as SO2 e) OXIDES OF NITROGEN as NO2 f) OXYGEN as O2 g) TOTAL VOLATILE ORGANIC COMPOUND h) YEAST & MOULD COUNT i) FORMALDEHYDE j) AMMONIA (NH3) k) PM 10 l) PM 2.5 m) Ozone n) Acetaldehyde o)Benzene p) Hexane q) Naphthalene r) Phenol s) Styrene t)Tetrachloroethylene u) Toluene v) vinyl acetate w) Dichlorobenzene x) Xylenes total | [6 empty] | 0 | 0 | 0 |  | 0
[8 empty] | 0 | 0 | 0 |  | 0
2 | Floor Flushing | [6 empty] | 0 | 0 | 0 |  | 0
| Peripheral windows should be kept open for air escaping .All Lift lobby & staircase doors should kept open for circulation.Along with above Heavy duty floor stand exhaust fans should be kept in same floor balcony areas & near to openable windows & air flushing should be done. | Lot | 1 | 1 | 2 |  | 65000 | 0 | 130000 | 130000 |  | 130000
2.01 | Renting for below fans for floor flush out incase if floor flush is taking time & running the fans for 24-48 hours to meet the air gases within the threshold value.Required cable & terminations should be consider as part of HVAC vendor scope .Fan capacities are mentioned below . | Lot | 1 | 1 | 2 |  | 25000 | 0 | 50000 | 50000 |  | 50000
[8 empty] | 0 | 0 | 0 |  | 0
3 | Air Quality Monitor | [6 empty] | 0 | 0 | 0 |  | 0
| Supply of IAQ Monitor to measure the levels of PM 2.5, TVOCs, CO2, Temperature, Humidity on a real time basis. The IAQ Monitor shall be RS485 enabled and should be capable of getting connected with Wi-Fi. The Monitor is with touchscreen LED display and should be capable of sending the indoor air quality information on display. The Monitor should indicate the quality of air through changing the colours as per the NAAQS standards. | RO | 3 | 2 | 5 | 46200 | 1650 | 231000 | 8250 | 239250 |  | 239250
[8 empty] | 0 | 0 | 0 |  | 0
4 | Central Air Cleaner for AHU | [6 empty] | 0 | 0 | 0 |  | 0
[8 empty] | 0 | 0 | 0 |  | 0
| Supply of SEMI -HYBRID HEPA class ( polarisation based ) central air purification system using Filterless Magnetic Air Purification Process of different capacities inside AHU to improve the air quality by removing microbial, pollution inside the air. The air purification system must be IS 17570:2021 : ISO 16890:2016 certified in accordance to ASHRAE 52.2 2017 with valid test data by ASHRAE validated lab having in USA only. It should be a monobloc-structured unit specifically designed for integration in the Return Air path of units of all sizes, to centrally capture and kill germs. It shall be in grids of sizes 610x370x150mm (1000 CFM), and 610x680x150 mm (2000 CFM) to cover the full capacity (CFM) of the units. The central air cleaner unit should have no consumable parts and the minimum life of central air cleaner unit should be more than 10 years. The central air cleaner shall be capable of removing particulates as small as 0.01 microns including particulate matter PM 2.5 & PM 1.0, allergens, pollen, bacteria, pathogens and various VOC. It must be a monobolic-structured unit specifically designed for integration in return air path of air delivery systems to provide a single indoor air quality (IAQ) solution meeting global safety and performance standards set forth by ISHRAE, GRIHA, IGBC, CDC , ASHRAE & CPCB Notification No B-29016/20/90/PCI-L Manufacturer must comply with DIPP guidelines for public procurement policy notification No REGD No. DL-33004/99 dated 21 July 2006 & Micro and Small Enterprises (MSEs) Order, 2012 inline with make in India initiative. For ease of supply and spares the OEM must have manufacturing facilities in India/Delhi NCR and support MAKE In India initiative. The OEM must strictly follow DIPP guidelines, Green Pro for more than 50 % Indian components and OEM registered under MSME will be given preference. Supplier must have experience of more than six years 'executing projects with the same technology products and have successful installation in CPWD /PWD hospitals/governments project. List of project need to be submitted for approval. | [6 empty] | 0 | 0 | 0 |  | 0
| The below global certificate/ report is a must to ensure the performance, safety and reliability of the Air Purification being proposed • The central air cleaner must be designed to trap and kill microbes with high efficiency duly tested on E. coli (ATCC 15597), H1N1, as per ASTM E2149 with no less than 99% killing in less than 15 minutes. • The unit shall include activated granular carbon filtration that together eliminate harmful gases. • The central air cleaner must be tested as per FDA GLP Regulations (40 CFR Part 160) for corona virus inactivation capability of over 99% in presence of FDA inspector in global labs. • The unit shall be UL 2998 (that does not produces ozone, ozone generation shall be less than 50 ppb from an International Lab) & Intertek ETL, UL 867, CSA C22 No. 187, and CE certified for safety and quality and with EMC (Electromagnetic compatibility), LVD (Low Voltage directive) and RoHS compliant for complete modules. • The system shall be ANSI/ASHRAE 52.2 2017 tested with at least a MERV 15 rating and an ISO 16890 ePM 1.0 90%. • Each central air cleaner modules should be UL certified and not components or individual parts. The central air cleaner must be listed and certified by a US OSHA set standards duly implemented through NRTL accredited labs such as Intertek, Underwriters Limited, etc. to ensure safety and compliance with no consumable media filter. • The central air cleaner performance must be tested from a ASHRAE compliant from an International Lab third-party testing laboratory to confirm CME (Composite Minimum Efficiency) meeting following criteria: Particle Size CME 0.3 to 0.4 μm 90% • The failure to submittal the certifications along with the submittal shall lead to rejection of the product. • For safety & security no arching, popping noise should occur during dust test. Also there should be no residual charge to avoid any shock risks. • The system should have a UL certified inbuilt pneumatic sensor allowing it to work as a controller (optional). It must automatically detect airflow and the capability to interface with the building management system. If the HVAC system is turned ON and the airflow is detected, then the output power should be available to the system, otherwise the system shall automatically turn off for the protection of service personnel. APPROVED MAKES : Trane/Dr Air / Magneto | [6 empty] | 0 | 0 | 0 |  | 0
[8 empty] | 0 | 0 | 0 |  | 0
4.01 | AHU CAPACITY - 15000 CFM (MAX) | No. | RO | RO | 0 | 575000 | 25000 | 0 | 0 | 0 |  | 0
[8 empty] | 0 | 0 | 0 |  | 0
5 | Airflow Measuring Station | [6 empty] | 0 | 0 | 0 |  | 0
5.1 | The AMCA certified AMS airflow measuring station with the high performance control damper. The complete assembly is utilized to provide effective set point monitoring and control. Custom-designed extruded sensing blades which capture the static and total pressure data from the air stream, a Class 1A leakage rated control damper, aluminum airflow straightener, and factory piped and mounted pressure transducer. The AMS shall bee BMS compatible. Velocity Rane: 300 FPM to 5000 FPM, accuracy with not more than 3%deviation. | RO | RO | RO | 0 |  |  | 0 | 0 | 0 |  | 0
[8 empty] | 0 | 0 | 0 |  | 0
5 | USB type desk mount portable type fan with 3 speed fan along with 150cm long cord for power | RO | 0 | 0 | 0 | 1500 | 250 | 0 | 0 | 0 |  | 0
| Total | [6 empty] | 231000 | 248250 | 479250 |  | 479250

## BOQ_LEED
Project |  | M/s Societe Generale
Sl. No | Code | Description | Location | Unit | Quantity | Rate | AMOUNT | Remarks
LEED and WELL points
|  | Terms and conditions for LEED v4 PLATINUM as below: 1. Clients to have renewable energy use and has to be reflected and accounted as wheeled energy in electricity bills. 2. REC purchases to be analyzed if any. Note:- LEED Certification is only for the New fit out area not for refurb areas | [6 empty] | 0
0
1 |  | LEED REGISTRATION |  | Ls | 1 |  | 0 |  | 0
|  | Carrying out LEED (Leadership in Energy and Environmental Design) registration for the project under the appropriate LEED rating system (e.g., LEED ID+C, LEED NC, or LEED O+M), including all coordination, documentation, and administrative formalities required for official registration with the U.S. Green Building Council (USGBC) or Green Business Certification Inc. (GBCI). |  |  |  |  | 0 |  | 0
|  | Preparing and submitting the required documentation for LEED project registration with USGBC/GBCI. Payment of applicable registration fees to USGBC/GBCI on behalf of the client (to be reimbursed as per actuals if applicable). Coordination with the design, construction, and sustainability teams to gather necessary information for registration. Uploading project information on the LEED Online platform and creating the project account. Providing support in selecting the appropriate LEED rating system based on project type and scope. Maintaining communication with USGBC/GBCI for acknowledgment, updates, and verification of registration status. Submitting registration confirmation and official receipt for client records. Inclusions: Administrative, consultancy, and coordination charges for LEED registration. All documentation support for initial LEED project setup on LEED Online. Liaison with project stakeholders for registration completion. |  |  |  |  | 0 |  | 0
[7 empty] | 0 |  | 0
2 |  | WELL (HSR) |  | Ls | 1 |  | 0 |  | 0
|  | WELL ( HSR ) related to Indoor air quality for new fitout (GF- Voayger ,2F (Full Floor)- Right top quadrant) |  |  |  |  | 0 |  | 0
[7 empty] | 0 |  | 0
2.01 |  | LEED & WELL CONSULTANT |  | Ls | 1 |  | 0 |  | 0
|  | Engaging a qualified and USGBC-accredited LEED Consultant to provide complete consultancy services for achieving LEED Certification for the project under the applicable rating system (LEED ID+C, LEED NC, or LEED O+M). The consultant shall guide the project team from registration to certification, ensuring compliance with all required LEED prerequisites and credits. |  |  |  |  | 0 |  | 0
|  | Total Amount Of LEED & WELL |  |  |  |  | 0 |  | 0

## Make List
ANNEXURE -4
PROPOSED MAKE OF MATERIALS
S.No. | Item | Make | SG Preferred Make
PROPOSED MAKES FOR CIVIL & INTERIOR WORKS
PROPOSED MAKES FOR MEP
1 | Electrical Panels | VV Systems
2 | LT Cables | Polycab
3 | Copper Wires | Polycab
4 | Switches & Sockets | Honeywell MK-Eva
5 | Power Cube | CJ Infra
6 | MCB / ELCB / MCCB | Schneider
7 | Distribution System | Schneider
8 | Industrial Socket | Neptune- BALS
9 | PVC Conduits | VIP/Precision/Universal | VIP
10 | Batteries | Exide / Quanta
11 | Inverter | Socomec
12 | Light Fixtures | Revix
13 | Decorative Light Fixtures | Revix
14 | LMS | Lutron / Zencontrol / Helver
15 | GI Ducts | Ductofab / GP Spira / Dev duct | GP Spira
16 | GI Sheets | Jindal / Tata
17 | Diffusers | Airmaster / Systemair / Synchro | Airmaster
18 | Grills | Airmaster / Systemair / Synchro | Airmaster
19 | Thermal Insulation (Nitrile rubber) | K-Flex / Armaflex / A-Flex
20 | Acoustic Insulation (Nitrile rubber) | K-Flex / Armaflex / A-Flex
21 | Acoustic Insulation (Fiberglass) | UP Twiga
22 | VCD and Fire Dampers | Airmaster / Systemair / Synchro | Airmaster
23 | Mixing Box | Airmaster / Systemair / Synchro | Airmaster
24 | Butterfly Damper | Airmaster / Systemair / Synchro | Airmaster
25 | Flexible Ducts | UP Twiga / Seven Star
26 | Collar Damper | Airmaster / Systemair | Airmaster
27 | Dx. units & VRF units | Bluestar / Daikin | Bluestar
28 | Refrigerant Pipes | Total line / Rajco / Nippon
29 | Inline Fans | Caryaire / Kruger / Systemair | Caryaire
30 | Plumbing Fixtures & Accessories | Hindware / Jaquar / Euronics
31 | Sink and Tap | Nirali / Futura
32 | PVC Pipes | Astral pipes / Supreme / Finolex
33 | PHE Valves | Zoloto / Leader | Zoloto
34 | GI - Pipe | Jindal ( Hissar ) / TATA
35 | Sprinkler | Tyco / New age / HD | Tyco
36 | Flexible Drops | Tyco / New age / HD | Tyco-Braided
37 | Fire Extinguishers | Safex / Excellent/ Eversafe | Safex
38 | Fire Signages | Prolite / Agnis / Agni
39 | Fire Alarm Panel | Honeywell Notifier
40 | Smoke Detectors / heat Detectors | Honeywell Notifier
41 | Cables/Wires | Polycab / Ravicab / Varsha /Calliplast | Polycab
42 | MS Conduits | Bharat / BEC | Bharat
43 | PA Speakers | Honeywell
44 | Amplifier | Honeywell
45 | Microphone | Honeywell
46 | Cables/Wires | Polycab / KEI / Bonton | Polycab
47 | Rodent Repellent System | Maser / C-System / Varna
48 | WLD System | Maser / C-System / Varna
49 | CCTV | Honeywell
50 | NVR | Honeywell
51 | Access Control | Tyco (iStar Ultra)
52 | Turnstile | P-Gate, Turnstile-KABA | P-Gate--Boon Edam(Local Supply)
53 | Cables & Conduits | Cables - Amp / D-link / Finolex Conduit - Precision / VIP national / BEC
52 | VAV | Honeywell
54 | BMS | Honeywell Trend
55 | Chilled Water FCU | Edgetech / Carrier / Zeco
56 | Chilled Water pipes | Jindal / Tata
57 | Auto Sequential Panel | Aircon Controls / Thittanix
Note: Final Make Selection shall be Adrianse prerogative