## Master Summary
Category | Amount (in INR)
C&I | 0
HVAC | 0
MV | 0
LV | 0
Sub - Total | 0
GST @ 18% | 0
Labor Cess @ 1% | 0
Grand Total | 0

## C&I BOQ
C&I BOQ FOR CINEPOLIS
PROJECT NAME & CITY - K MALL, JODHPUR |  | ID - Sand ID
Notes: 1. Unless otherwise specified in the item description all Plywood for furniture, carpentry & associated works shall be Powder Free, Termite & Borer Resistant, BWP Grade Marine Plywood conforming to IS:710:1976 standards and list of approved makes. 2. All flooring to be protected with 3mm thk MDF of size 8' x 4' of with tape on joints not leaving any surface exposed. No extra item to be considered for protection of all flooring area. In case of any wear and tear this has to be redone. Flooring should be protected at all times. 3. Contractor to submit detailed rate analysis of all items once order confirmed. 4. All wooden and ply surfaces whose finishes have not been prescribed are to be painted in anti corrosive paint black Japan along with anti-termite treatment. 5. For items supplied by Cinepolis - The contractor shall be provided with 10% extra quantity of the material than needed as per the quantity area. Any material required above it shall be provided to the contractor at his own cost. The contractor has to make his own queries regarding the same before finalizing the contract. 6. Quality Assessment / Quality Check System: The Contractor shall allow for providing and implementing a QA/QC system to meet international standards and to the approval of Cinepolis. 7. Works at all heights / depths or floor levels and constrained locations should be considered in the item rates, it includes necessary framing and MS scaffolding required to execute all items as per BOQ. 8. Any addition in quantities from BOQ needs to be certified by Cinepolis before execution and maximum six weeks after site mobilization. 9. Measurements for billing shall be made for finished dimensions as per actual execution specified for the work and not as per quantities mentioned in the BOQ. 10. Supply of well seasoned timber, free from knots, cracks and other defects must be considered in item rate. 11. Submission of shop drawings wherever required should be considered within 5-7 days for approval from Cinépolis. Once the shop drawings is approved, it will be considered that site conditions were verified by GC. 12. Contractor should submit all the material samples (to be supplied by him) for approval from Cinepolis before procurement and maximum two weeks after site mobilization. 13. Vendor should submit all RFI's for any queries regarding the design within maximum two weeks from RFP being floated. 14. All screws visible on final finished surface must be with duco paint matching to the surface. 15. Protection for flooring (with MDF sheet), wall finishes, chairs etc. must be considered at all time. No extra item to be considered for protection. In case of any wear and tear this has to be redone without any additional cost. 16. For all the dismantling activities, contractor must consider disposal of unserviceable material and cleaning up site. 17. Rates for all items in this BOQ must be quoted with reference to relevant tender drawings. 18. General lighting to be considered in all areas in all times without any additional cost. 19. For any request of Specification change, GC to consider 10-15 days for approval from Cinepolis. 20. Carting away debris at area designated by Cinepolis site team and cleaning up site to be considered. 21. All areas which are to be retained must be protected at all times without any additional cost.
S. No. | ITEM DESCRIPTION | UNIT | QUANTITY | RATE | AMOUNT
1 | DISMANTLING WORKS
1.01 | Dismantling of masonry including interior finishes on walls Dismantling of existing brickwork/ block work (all thickness) inclusive of dado/ wall/ and cement plaster, wall panelling, decorative element, LED screens, Poster cases, signages, door with frames, etc. till the structural member. This also includes protection of all retained elements (adjoining surfaces, base structure and MEP services), carting away debris, cleaning up site and termination of MEP services as applicable, etc. complete. Refer drawing. | Sqm | 10 |  | 0
MEASUREMENT METHOD : Shall be measured along the surface area (one side).
1.02 | Dismantling of existing wall tile Dismantling of existing wall tile till the structural member or masonry wall as applicable, including the removal of base mortar etc. This also includes protection of all retained elements (adjoining surfaces, base structure and MEP services), carting away debris, cleaning up site and termination of MEP services as applicable, etc. complete. Refer drawing. | Sqm | RO | 0 | 0
MEASUREMENT METHOD : Shall be measured along the surface area.
1.03 | Dismantling of False Ceiling Dismantling of existing lobby false ceiling and ceiling sections till the structural member including light fixtures, speakers, beam detectors, fire sprinklers, grills, diffuser, cassette AC, etc. This also includes protection of all retained elements (adjoining surfaces, base structure and MEP services), carting away debris, cleaning up site and termination of MEP services as applicable, etc. complete. Refer drawing. | Sqm | RO | 0 | 0
MEASUREMENT METHOD : Shall be measured along the surface area in plan.
1.04 | Dismantling of existing tile flooring Dismantling of existing tile flooring and skirting without damaging the structural slab or the PCC underlay. This also includes protection of all retained elements (adjoining surfaces, base structure and MEP services), carting away debris, cleaning up site and termination of MEP services as applicable, etc. complete. Refer drawing. | Sqm | RO | 0 | 0
MEASUREMENT METHOD : Shall be measured along the surface area in plan
2 | CIVIL WORKS
2.01 | 115mm thick Brickwork Providing and laying 115mm thick partition wall with well burnt good quality of first class designation 75 in cement mortar 1:4 (1cement: 4 coarse sand) including providing 2 Nos of 6mm dia MS round bars at every IV th course, including curing rubbing the surface, racking out joints at all levels/ height, including chicken mesh at the junction of RCC & masonry, trowelling, finishing smooth. This item also includes 12 - 15 mm thick plaster 1:4:2 (1cement : 4 fine sand : 2 coarse sand) on both sides in etc. complete. Refer drawings. | Sqm | RO | 0 | 0
MEASUREMENT METHOD : Shall be measured along the surface area (one side).
2.02 | 230mm thick Brickwork Providing and laying 230mm thick brick wall with well burnt good quality, class designation 75 in cement mortar 1:4 (1cement : 4 coarse sand) including, curing, rubbing the surface, racking out the joints at all levels/ height, including chicken mesh at the junction of RCC & masonry, trowelling, finishing smooth. This item also includes 12 - 15 mm thick plaster 1:4:2 (1cement : 4 fine sand : 2 coarse sand) on both sides in etc. complete. Refer drawings. | cum | 5 |  | 0
MEASUREMENT METHOD : Shall be measured the along the volume (combined with wall thickness).
2.03 | 200mm thick AAC Block Providing and laying 200mm thk AAC blocks with cement mortar 1:4 (1cement:4 coarse sand) including RCC lintel with necessary reinforcement at every 1.0mtr level. including, curing, rubbing the surface, racking out the joints at all levels/ height, including chicken mesh at the junction of RCC & masonry, trowelling, finishing smooth. The plaster shall be adequately cured. This item also includes 12 - 15 mm thick plaster 1:4:2 (1cement : 4 fine sand : 2 coarse sand) on both sides, etc. complete. Refer drawings. | cum | RO | 0 | 0
MEASUREMENT METHOD : Shall be measured the along the volume (combined with wall thickness).
2.04 | Cement Plaster Providing & applying 12-15 mm thick Plaster in plum, line and level to internal walls, columns etc at all levels/ height, in cement sand mortar 1:4 using screened sand, including scaffolding, stagging, curing, trowelling, finishing smooth, etc. complete. Refer drawings. | Sqm | 20 |  | 0
MEASUREMENT METHOD : Shall be measured along the surface area.
2.05 | Lintel for opening Providing and laying in position Reinforced cement concrete work in lintels, including the cost of centring, shuttering, finishing and reinforcement with M25 grade concrete and 12mm dia steel bar. Size of lintel should be 150mm high and width should be as per wall thickness and length should be the width of opening and 150mm bearing on both sides. The item includes laying of lintel in existing blockwork as well, etc. complete. Refer drawings. | cum | 1 |  | 0
MEASUREMENT METHOD : Shall be measured the volume (combined with RCC thickness).
2.06 | Screeding (20 to 50mm thick) Providing and laying M10 PCC floor screeding of general level to lay floor tiles/stones above with an approximate thickness of 20mm to 50mm using cement concrete 1:3:6 (1cement : 3coarse sand : 6 graded stone,down gauge), including tamped, spaded , trowelled and top finished neat. Top surface should be finished neat and smooth and laid to water levels or proper slopes as directed, curing, etc. complete. Refer drawings. | Sqm | 840 |  | 0
MEASUREMENT METHOD : Shall be measured along the surface area in plan
2.07 | Screeding (50 to 75mm thick) Providing and laying M10 PCC floor screeding of general level to lay floor tiles/stones above with an approximate thickness of 50mm to 75 mm using cement concrete 1:3:6 (1cement : 3coarse sand : 6 graded stone,down gauge), including tamped, spaded , trowelled and top finished neat. Top surface should be finished neat and smooth and laid to water levels or proper slopes as directed, curing etc, complete. Refer drawings. | Sqm |  |  | 0
MEASUREMENT METHOD : Shall be measured along the surface area in plan
2.08 | Waterproofing Providing and laying in situ 25mm thick (average) seven course water proofing treatment with APP (Atactic poly-propylene) modified Polymeric membranes over roof consisting of first coat of bitumen primer @ 0.40 Kg per sqm, 2nd, 4th & 6th courses of bonding material @ 1.20 Kg/sqm, which shall consist of blown type bitumen of grade 85/25 conforming to IS : 702, 3rd and 5th layers of roofing membrane APP modified Polymeric membrane 1.5 mm thick of 2.25 Kg/sqm weight consisting of five layers prefabricated with centre core as 20 micron HMHDPE film sandwiched on both sides with polymeric mix and the polymeric mix is protected on both side with 20 micron HMHDPE film. 7th, the top most layer shall be finished with cement mortar 1:3 (1cement : 3 fine sand) mixed with 2% integral water proofing compound by weight of cement over a 12 mm layer of cement mortar 1:3 (1 cement : 3 fine sand) and finished neat, etc. complete. Refer drawings. | Sqm | 321.3 |  | 0
MEASUREMENT METHOD : Shall be measured along the surface area.
2.09 | Cement based levelling compound Providing and laying of cement based levelling compound Ardex CL 11 with primer T-51 in two coats of 2mm as per ardex specification. Rate to include for all necessary tools & tackles, labour etc all complete. Refer drawings. | Sqm | 20 |  | 0
Brand: Ardex Code: CL 11 with primer T-51
MEASUREMENT METHOD : Shall be measured along the surface area in plan.
3 | FLOORING WORKS
3.01 | Vitrified Tile Flooring Providing and fixing vitrified tiles over 20 mm thick bed of cement mortar 1:4 (1 cement : 4 coarse sand) and jointing with grey cement slurry @3.3kg per sqm including pointing in white cement mixed with pigment of matching shade to tile. Tile joints to be finished in white cement mixed with pigment of matching shade of tile. Tile to be layed as per pattern/ design and multiple start points as shown in the drawing. In case of any damage to tiles due to other construction activities or removal of protection; contractor must replace the affected tiles at his own cost. Rate to include cutting, wastage, cost of all materials and all necessary activities, etc. complete. Refer drawings.
3.01.01 | Database Code: C010827 Brand: AGL Model: Tropic Brown (Double glazed tile) Finish: Glossy Size :600 x 600mm Thickness: 8.5 mm | Sqm | 99 |  | 0
3.01.02 | Database Code: C000103 / C2030.20/G/0208 Brand: Somany Model: FB Dusky S&P Crema Colour: Matt Finish: anti- skid Size : 600x600mm Thickness: 10mm | Sqm | 117.6 |  | 0
3.01.03 | Database Code: C010778 Brand: Orient Bells Model: CN Armani Grey LT Color : Dark Grey Finish: Glossy Size : 600 X 1200mm Thickness: 10mm | Sqm | RO | 0 | 0
3.01.04 | Database Code: C000236 Brand: Kajaria Model: Toronto blanco Finish: Glossy Size: 300 x 450mm Thickness: 10mm | Sqm | 4 |  | 0
3.01.05 | Database Code: C000138 Brand: Kajaria Model: Kajaria pvt K6306 Finish: Glossy Size : 600 X 600mm | Sqm | 93.45 |  | 0
3.01.06 | Database Code: TBD08 Brand: Johnson Model: Light Grey Polish Colour: Light Grey Finish: Glossy Size : 600x600mm & 600x1200mm Thickness: TBC | Sqm | 10.5 |  | 0
3.01.07 | Database Code: C007483 Brand: AGL Model: Volga White Mastro Ruby (Double glazed Tile) Finish: Glossy Size : 600 x 600mm Thickness: 8.5 mm | Sqm | 276.7 |  | 0
3.01.08 | New Criteria Brand _ Kajaria Model _ Apollo White Size _ 600x1200mm Finish _ Matt Material _ Vitrified | Sqm | 0 |  | 0
3.01.09 | Providing & Fixing water jet cut Porcelain Brown Floor Tiles of 98 mm wide strips in Flooring 20mm thick bed of cement mortar 1:4 (1 cement : 4 coarse sand) and jointing with grey cement slurry @3.3kg per sqm including pointing in white cement mixed with pigment of matching shade to tile. Tile joints to be finished in white cement mixed with pigment of matching shade of tile. Tile to be layed as per pattern/ design and multiple start points as shown in the drawing. In case of any damage to tiles due to other construction activities or removal of protection; contractor must replace the affected tiles at his own cost. Rate to include cutting, wastage, cost of all materials and all necessary activities, etc. complete. ( including around brass strip TBC) Database Code: C010827 Brand: AGL Model: Tropic Brown (Double glazed tile) Finish: Glossy Size :600 x 600mm Thickness: 8.5 mm | Rmt | 6.3 |  | 0
SKIRTING WORKS
Providing and laying skirting over adequate thickness of cement mortar 1:4 (1 cement: 4 coarse sand) mix. Rates to include for surface cleaning, cutting, etc. Joints to be finished with approved pigmented shade added to match the approved tile shade. Rate to include cutting, wastage, cost of all materials, adhesives and all necessary activities, etc. complete. Refer drawings
3.01.10 | Database Code: C000139 Brand: Kajaria Model: Kajaria pvt K6306 Finish: Glossy Size : 100 X 600mm | Rmt | 98.7 |  | 0
3.01.11 | Brand: AGL Model: Tropic Brown (Double glazed tile) Finish: Glossy Size :600 x 600mm Thickness: 8.5 mm DB Code:- SK04 | Rmt | 47.25 |  | 0
3.01.12 | Database Code: C007474 Brand: Somany Model: Chroma Bianco Colour: Ivory Finish: Matt Size : 600x600mm Thickness: TBC | Sqm | RO | 0 | 0
3.01.13 | Database Code: C008976 Brand: RAK Ceramic Model: Statuario Classic Finish: Marble Finish Size : 100 x 1200mm Thickness: TBC | Rmt | 0 |  | 0
3.01.14 | Database Code: C007483 Brand: AGL Model: Volga White Mastro Ruby (Double glazed Tile) Finish: Glossy Size : 600 x 600mm Thickness: 8.5 mm | Rmt | 130.85 |  | 0
3.01.15 | New Criteria Brand _ Kajaria Model _ Apollo White Size _ 100x1200mm Finish _ Matt Material _ Vitrified | Rmt | 0 |  | 0
MEASUREMENT METHOD : Shall be measured as per the running length along which it has been installed
Vinyl Tile flooring
Providing and Laying PVC Non-Skid tile flooring laid on even base, dust & oil free with appropriate adhesive 2MM thk. Heavy duty. as shown in drawings and as directed by architect .etc. Complete. The finishing should be done neat and free of bubbles and as per the standards of the manufacturers specification. The rate shall include all cutting and wastage, cost of all materials, adhesives etc. complete. Before laying, the existing flooring should be made free from dust and undulations.
3.01.14 | Database Code: C000136 Brand: ARMSTRONG Model: EXCELON IMPERIAL PEWTER CLASSIC 51908T011 Colour: Grey PVC Floor Size : 300 x 300mm Thickness: TBC | Sqm | 29.4 |  | 0
Vinyl skirting
Providing and fixing of 100mm high Skirting over existing cement plaster made in curve at the joint with floor The vinyl skirting is to be laid in continuity with the floor fixed with adhesive as per manufacturers instructions and specifications
3.01.15 | Database Code: C000137 Brand: CUSTOM MADE BRAND ARMSTRONG Model: PEWTER CLASSIC Colour: Gray Size : 100 x 300mm Thickness: TBC | Rmt | 38.85 |  | 0
3.02 | BOH Grey Kota Stone flooring (C000134) Providing & laying of grey color kota stone to flooring, tread, riser etc in plumb, line and level in approved pattern on 20mm thick cement mortar 1:4 (1 cement: 4 coarse sand) bed. Joints to be finished with white cement and pigmented shade added to match the approved stone shade. Stone to be layed as per pattern / design and multiple start points as shown in the drawing. Rate to include for surface cleaning & preparation, cutting, mirror polishing. In case of any damage to the stone due to other construction activities or removal of protection; contractor must replace the affected stone at his own cost. Contractor to ensure that the kota stone installed is from one lot and there is no colour and shade variation. Rate to include cutting, wastage, cost of all materials and all necessary activities, etc. complete. Refer drawings. Base Rate:- Rs. 65/- Per Sqft
| Brand : Customized Model : Grey Kota Stone Size : 550 x 550 X 18mm | Sqm | 244.65 |  | 0
MEASUREMENT METHOD : Shall be measured along the surface plan area.
3.03 | BOH Kota stone skirting (C000135) Providing and laying kota stone skirting over adequate thickness of cement mortar 1:4 (1 cement: 4 coarse sand) mix. Rates to include for surface cleaning, cutting, chamfering edges of kota stone, grinding, mirror polishing. Joints to be finished with white cement with pigmented shade added to match the approved stone shade. Rate to include cutting, wastage, cost of all materials, adhesives and all necessary activities, etc. complete. Refer drawings
| Brand : As approved Model : Grey Kota stone Thickness: 18mm Height : 100mm BD Code:- (C000135) | Rmt | 237.3 |  | 0
MEASUREMENT METHOD : Shall be measured as per the running length along which it has been installed
MEASUREMENT METHOD : Shall be measured along the surface plan area.
3.04 | Audi PVC flooring (C007498) Installation of PVC non skid flooring (provided by Cinepolis) in rolls laid on an even base with the help of 2-3mm thick suitable adhesive. Before laying of tile on adhesive, ensure the substrata is clean & free from impurities like dust, dirt, oil, debris, grease, curing agents, loose plaster etc. PVC roll to be layer in length along the Audi width with overlap on existing chamfered edges as shown in the drawing. In case of any damage to installed PVC flooring due to other construction activities or removal of protection; contractor must replace the affected flooring at his own cost. The finishing should be done neat, free of bubbles and as per the standards from the manufacturer. The rate shall include all cutting, wastage, cost of all materials, adhesives etc. complete. Only PVC roll to be provided by Cinépolis, rest all items to be considered in quoted rates by contractor. | Sqm | 658.35 |  | 0
MEASUREMENT METHOD : Shall be measured along surface area. Will not include any overlaps or wastages.
3.05 | Carpet flooring (C000194) Installation of floor carpet (provided by Cinepolis) in rolls laid on an even base with the help of 2-3mm thick suitable adhesive. Before laying of tile on adhesive, ensure the substrata is clean & free from impurities like dust, dirt, oil, debris, grease, curing agents, loose plaster etc. Carpet to be layer with the pattern along the Audi width with the corners neatly and firmly fixed so as to avoid any peeling off. The edge of the carpet hitting the wall is to be trimmed and all loose threads are to be sewed so that they do not come out loose. The finishing should be done neat, free of bubbles and as per the standards from the manufacturer. In case of any damage to installed carpet due to other construction activities or removal of protection; contractor must replace the affected flooring at his own cost. The rate shall include all cutting, wastage, cost of all materials, adhesives, etc. complete. Only carpet roll to be provided by Cinépolis, rest all items to be considered in quoted rates by contractor. | Sqm | 884.1 |  | 0
MEASUREMENT METHOD : Shall be measured along surface area. Will not include any overlaps or wastages.
3.06 | Transition profile between Mall & Cinepolis flooring Providing and fixing of transition profile at the junction of Mall and Cinema Flooring change with a solid brass profile of size 6.3mm x 6.3mm flushed with flooring level in plum, line and level with the help of suitable adhesive. Before fixing the profile, ensure the substrata is clean & free from impurities like dust, dirt, oil, debris, grease, curing agents, loose plaster etc. The rate shall include all cutting, wastage, cost of all materials, adhesives, etc. complete. Refer drawings.
| Brand: Customised Brass Shape: Square Bar Finish: Mill Finish Size : 6.3 X 6.3mm Database Code:- C010421 | Rmt | 68.25 |  | 0
MEASUREMENT METHOD : Shall be measured as per the running length along which it has been installed
3.07 | Z' Transition Profile Providing & fixing Anodized Aluminium 'Z' shape profile of size 25 X 25mm, between carpet & external tile in plum, line and level fixed with Bostik adhesive. Before fixing the profile, ensure the substrata is clean & free from impurities like dust, dirt, oil, debris, grease, curing agents, loose plaster. The rate shall include all cutting, wastage, cost of all materials, adhesives, etc. complete. Refer drawings.
| Brand: Wall line Color : Black Size : 25 X 25mm Database Code:- C008185 | Rmt | 17.85 |  | 0
MEASUREMENT METHOD : Shall be measured as per the running length along which it has been installed
3.08 | Brass profile around 100mm Tile Providing and fixing of transition profile around the 100mm tile strips with a solid brass profile of size 6.3mm x 6.3mm flushed with flooring level in plum, line and level with the help of suitable adhesive. Before fixing the profile, ensure the substrata is clean & free from impurities like dust, dirt, oil, debris, grease, curing agents, loose plaster etc. The rate shall include all cutting, wastage, cost of all materials, adhesives, etc. complete. Refer drawings. 'Brand: Customised Brass Shape: Square Bar Finish: Mill Finish Size : 6.3 X 6.3mm Database Code:- C010421 | Rmt | 142 |  | 0
3.09 | Expansion joint
3.09.01 | Supply and installation of factory-extruded dual-durometer Santoprene expansion joint seal system, suitable for floor-to-floor, and corner applications. The seal shall be designed to accommodate horizontal and vertical movement of ±13mm and shall be factory-extruded in widths (variable as per site requirement). The profile shall include soft and rigid Santoprene durometers for optimal flexibility and secure retention within the system. Seals to be supplied in specified colours including upon requested by cinepolis . Retainers shall be in mill-finish aluminium and installed recessed into the substrate. Installation shall be in accordance with manufacturer’s recommendations, ensuring secure fitment and watertight performance. Fire-rated option to comply with UL 2079 or ASTM E-119 standards. Floor Expansion joint, as per detail FL-01. MODEL:101 SERIES RECESSED MOUNT Database Code:- C009210 Finish- Mill finish aluminium |  |  |  | 0
3.09.01a | As item 3.09 Floor-to-Floor expansion joint | Rmt | RO | 0 | 0
4 | DADO WORKS
4.01 | Dado over masonry wall Providing and fixing vitrified tile work in dado over 12mm thick bed of cement mortar 1:3 (1 cement : 3 coarse sand) and jointed with grey cement slurry @3.3 kg/sqm including pointing in white cement mixed with pigment of matching shade complete. Tile to be layed as per pattern/ design as shown in the drawing. In case of any damage to the tile due to other construction activities or removal of protection, contractor must replace the affected tiles at his own cost. The rate shall include all cutting, wastage, cost of all materials, etc. complete. Refer drawings.
4.01.01 | Database Code: C010187 Brand: Italmarmi Somany Model: Modellato Series Colour: Felce Finish: Glossy Size : 75 x 300mm / 100 x 300mm Thickness: TBC | Sqm | 24.15 |  | 0
4.01.02 | Database Code: C010779 Brand: Nitco Model: CP white- (Carara Gold) Colour: Finish: Glossy Size : 300 x 600mm Thickness: 10mm | Sqm | RO | 0 | 0
4.01.03 | Database Code: C007499 Brand: Kajaria Model: Toronto blanco Colour: Beige Finish: Glossy Size : 300 x 450mm Thickness: 10mm | Sqm | 200.55 |  | 0
4.01.04 | Database Code: TBD08 Brand: Johnson Model: Light Grey Polish Colour: Light Grey Finish: Glossy Size : 600x600mm & 600x1200mm Thickness: TBC | Sqm | 13.65 |  | 0
MEASUREMENT METHOD : Shall be measured along the surface area.
4.01.05 | Brand: Johnson Model: Super White (Full body) Finish: Glossy Size : 800 x 2400mm Thickness: 15mm Brand: Walline or similar Model: U shaped SS 304 Colour: Gold coated Size: 12mm x 12mm | Sqm | 338.1 |  | 0
4.03 | Corner Guard.
4.03.01 | Providing & Fixing SS Gold Mirror Tile connector profile of size 10mm x 10mm in plum line and level corner guards in all Toilet wall as mentioned in drawing and as directed by Engineer in charge, including all cutting, wastage, hardware, adhesives etc. complete. Brand : Walline Model:- 10 MM X 10 MM TIT TC1010 WALLINE DB Code:- C005684 | Rmt | RO | 0 | 0
4.03.02 | Providing & Fixing Transition aluminium flat profile size 20mm in plum line and level in all change in finishes of wall from skirting level to 2.1 m. level (or at lintel lvl from skirting lvl) as mentioned in drawing and as directed by Engineer in charge, including all cutting, wastage, hardware, adhesives etc. complete. Brand : Walline Colour : Black DB Code:- PR01 | Rmt | 2.1 |  | 0
4.03.03 | Providing & Fixing Anodized aluminium corner profile size 12mm x 12mm x 2100mm in plum line and level corner guards in all change in finishes of wall from skirting level to 2.1 m. level (or at lintel lvl from skirting lvl) as mentioned in drawing and as directed by Engineer in charge, including all cutting, wastage, hardware, adhesives etc. complete. Brand : Walline Colour : Black DB Code:- C000127 | Rmt | 30.45 |  | 0
4.03.04 | Corner Guard (BOH Area ) Providing & Fixing aluminium corner guard size 12mm x 12mm x 2100mm in plum line and level corner guards in all back areas from skirting level to 2100mm level (or at lintel lvl from skirting lvl) of aluminium before paint coat, paint is done above the guard after fixing the guard (need to be flushed with putty level). Refer drawings. | Rmt | 28.35 |  | 0
MEASUREMENT METHOD : Shall be measured as per the running length along which it has been installed
5 | CEILING WORKS
5.01 | Gypsum Ceiling supported on RCC slab (C000081) Providing & fixing Suspended Ceiling Sheet Block with hidden suspension & G.I. Frame work, clamps, accessories, Screws etc. It includes all clamps, necessary hardware and members for fixing the framing to RCC structures (complete hardware) including necessary vertical and curve fascia at drops, offsets, grooves, chamfering, moulding, coffer for lights, making coves, cutouts and providing extra supports for joints of boards, light fittings, grills, diffusers, speakers, smoke detectors, sprinklers, applying appropriate sections for creating trap doors etc. Gypsum board must be installed in staggered pattern and all joints should be filled and finished with jointing compound, jointing tapes and ready to receive plastic paint finish, etc. complete. Refer drawings.
| Gypsum board: Gyproc/ Armstrong/ Boral/sheetrock Hardware : Gyproc/ Armstrong Board thickness : 12.7mm | Sqm | 263.55 |  | 0
MEASUREMENT METHOD : Shall be measured along the surface area in plan area. the coves, drops and other vertical facia will be included in the plan measurement.
5.01a | Gypsum Ceiling supported on RCC slab (C000081) FIRELINE SHEETROCK 15.9MM Providing & fixing Suspended Ceiling Sheet Block with hidden suspension & G.I. Frame work, clamps, accessories, Screws etc. It includes all clamps, necessary hardware and members for fixing the framing to RCC structures (complete hardware) including necessary vertical and curve fascia at drops, offsets, grooves, chamfering, moulding, coffer for lights, making coves, cutouts and providing extra supports for joints of boards, light fittings, grills, diffusers, speakers, smoke detectors, sprinklers, applying appropriate sections for creating trap doors etc. Gypsum board must be installed in staggered pattern and all joints should be filled and finished with jointing compound, jointing tapes and ready to receive plastic paint finish, etc. complete. Refer drawings.
| Gypsum board: Gyproc/ Armstrong/ Boral/sheetrock Hardware : Gyproc/ Armstrong Board thickness : 15.9mm | Sqm | 106.05 |  | 0
MEASUREMENT METHOD : Shall be measured along the surface area in plan area. the coves, drops and other vertical facia will be included in the plan measurement.
5.02 | Laminate Ceiling on RCC Structure (C007486) Providing and fixing false ceiling with right angled OR curved corner as per drawing, including frame work in GI and hangers at appropriate distance as per manufacturers recommendation. It includes all clamps and necessary material for hanging the ceiling from RCC structures (complete hardware) including necessary vertical fascia at drops, offsets, grooves, chamfering, moulding, coffer for lights, making coves, cutouts and providing extra supports for joints of boards, light fittings, grills, diffusers, speakers, smoke detectors, sprinklers, applying appropriate sections for creating trap doors etc. The frame work should be finished with 12mm thick ply (BWR grade) and factory pasted 1mm thick laminate over 4mm thick MDF. The factory pasted laminate and MDF should be fixed to ply with help of suitable adhesive. Laminate joints to have 2mm wide grooves at equidistance as per drawing and the grooves to be filled in matching paint, etc. complete. Refer drawing.
| Brand: Merino Model: Magas Walnut Bronze Design No. : 10866 | Sqm | 98.7 |  | 0
MEASUREMENT METHOD : Shall be measured along the surface plan area. the coves, drops and other vertical facia upto 300mm will be included in the plan measurement.
5.03 | Grid ceiling (Acoustic Board) (C000199) Fixing of Grid ceiling edge tiles on necessary GI frame supported to existing soffit. Vendor to also include the vertical hanging system i.e. GI wire system and connectors etc. complete as per drawing & specification. Refer drawing.
| Brand : Armstrong / Ecophone Material : Black Acoustical Tile (OPTRA BLACK) Size : 600 x 1200 x 24 mm | Sqm | 1067.85 |  | 0
MEASUREMENT METHOD : Shall be measured along the surface plan area. drops and other vertical facia will be included in the plan measurement.
5.04 | 15mm Double Board Acoustic Gypsum Ceiling supported on RCC slab Providing and fixing Gyproc® SoundBloc Board or equivalent in 2 layers consists of installing an aerated, higher-density gypsum core board —complying with IS 2095 Part 1:2023 and EN 520:2004 —onto a rigid hidden suspension & G.I. Frame work with MS support at every 1.2 mtr to support ceiling, clamps, accessories, Screws etc. It includes all clamps, necessary hardware and members for fixing the framing to RCC structures (complete hardware) including necessary vertical and curve fascia at drops, offsets, grooves, chamfering, moulding, light fittings, grills, diffusers, speakers, smoke detectors, sprinklers, applying appropriate sections for creating trap doors etc..Gypsum board must be installed in staggered pattern and all joints should be filled and finished with jointing compound, jointing tapes and ready to receive plastic paint finish, etc. complete. The supporting GI and MS structure must be engineered to sustain the board’s high flexural strength—exceeding 550 N for 12.5 mm or 650 N for 15 mm thicknesses —while ensuring the system is not exposed to temperatures exceeding 49°C or high-humidity environments that could lead to mold growth. All components, including the MS primary supports and GI secondary framing, must be installed in accordance with Saint-Gobain's design criteria or manufacturing standards to maintain the assembly's Class 1 surface spread of flame rating and acoustic performance. Gypsum board: Gyproc/ Armstrong/ Boral/sheetrock Hardware : Gyproc/ Armstrong Board thickness : 15mm ( Double Board) | Sqm | 100.8 |  | 0
Brand : Gyproc® SoundBloc Board Material : Gyproc® SoundBloc Board Size : TBC
MEASUREMENT METHOD : Shall be measured along the surface plan area. drops and other vertical facia will be included in the plan measurement.
6 | CARPENTRY WORK
6.01 | Glass Wool Insulation (wall behind screen) (BG1) Providing and fixing acoustical treatment from UP twiga make with 50mm thick resin bonded fiberglass wool and RP tissue (black glass tissue), density 20kg/cum, 1200x600mm board, 0.037w/ mk thermal conductivity, 0.9 NRC, 1.35 R-value (thermal resistance) on the existing masonry wall with plastic screw and washer with cap finish @ 600mm c/c in proper plumb, level, line etc. complete. Refer drawings. | Sqm | 413.7 |  | 0
MAKE: UP Twiga Material : Resin bonded fiberglass wool Product code : TI-1250 Thickness : 50mm
MEASUREMENT METHOD : Shall be measured along the surface area, only flat surface area to be measured
6.02 | Glass Wool Insulation above false ceiling (upto roof bottom) Rear and side walls . Providing and fixing acoustical treatment from UP twiga make with 50mm thick resin bonded fiberglass wool of density 20kg/cum, 1200x600mm board, 0.037w/ mk thermal conductivity, 0.9 NRC, 1.35 R-value (thermal resistance) on the existing masonry wall with plastic screw with cap finish @ 600mm c/c in proper plumb, level, line etc. complete. Refer drawings.
| MAKE: UP Twiga Material : Resin bonded fiberglass wool Product code : TI-1250 Thickness : 50mm | Sqm | 100 |  | 0
MEASUREMENT METHOD : Shall be measured along the surface area, only flat surface area to be measured
6.03 | Audi fabric panelling (Rear and side walls) Audi fabric panelling as per drawings and specification as below : a) Bottom runner - Providing & fixing 18mm thick fire retardant ply boxing of size 100mm x 100mm (open box) with provision of stapling of fabric on fire retardant ply at approximately 1500mm from floor with the facia of 18mm thick MDF to be chamfered or moulded and the box to be painted in three coats of enamel paint (Apcolite Premium Satin enamel Paint color_Dried Spices 8749, Matt Finish, Brand- Asian Paint) with base primer. The boxing is to be fixed on wall with the help of triangular wedge shaped cuts of 40mm thick fire retardant ply and placed at a distance of 600mm c/c or as suggested by Cinépolis site incharge to provide adequate support and fine fabric fixing quality. b) Top Runner - Providing & fixing 18mm thick fire retardant ply boxing of size 100mm x 100mm (open box) with provision of stapling of fabric on fire retardant ply at false ceiling level with facia of 18mm thick MDF to be chamfered or moulded and the box to be painted in three coats of enamel paint (Apcolite Premium Satin enamel Paint color_Dried Spices 8749, Matt Finish, Brand- Asian Paint) with base primer .The boxing is to be fixed on wall with the help of triangular wedge shaped cuts of 40mm thick fire retardant ply and placed at a distance of 600mm c/c or as suggested by Cinépolis site incharge to provide adequate support and fine fabric fixing quality. c) Fiberglass wool - Providing and fixing acoustical treatment from UP twiga make with 50mm thick resin bonded fiberglass wool of density 20kg/cum, 1200x600mm board, 0.037w/ mk thermal conductivity, 0.9 NRC, 1.35 R-value (thermal resistance) on the existing masonry wall with plastic screw with cap finish @ 600mm c/c in proper plumb, level, line etc. complete. d) Brown Fabric (C000077) - Fixing of Brown decorative fabric as approved by Cinepolis on acoustically treated wall. The fabric to be fixed with gripper at 1300mm for rear walls and 600mm for side walls spacing. Only fabric supplied will be paid as per installed surface area in separate item. | Sqm | 352.275 |  | 0
MEASUREMENT METHOD : Shall be measured along the surface area, only flat surface area to be measured
| Audi fabric panelling (Rear and side walls) Audi fabric panelling as per drawings and specification as below : a) Bottom runner - Providing & fixing 18mm thick fire retardant ply boxing of size 100mm x 100mm (open box) with provision of stapling of fabric on fire retardant ply at approximately 1500mm from floor with the facia of 18mm thick MDF to be chamfered or moulded and the box to be painted in three coats of enamel paint (Apcolite Premium Satin enamel Paint color_Dried Spices 8749, Matt Finish, Brand- Asian Paint) with base primer. The boxing is to be fixed on wall with the help of triangular wedge shaped cuts of 40mm thick fire retardant ply and placed at a distance of 600mm c/c or as suggested by Cinépolis site incharge to provide adequate support and fine fabric fixing quality. b) Top Runner - Providing & fixing 18mm thick fire retardant ply boxing of size 100mm x 100mm (open box) with provision of stapling of fabric on fire retardant ply at false ceiling level with facia of 18mm thick MDF to be chamfered or moulded and the box to be painted in three coats of enamel paint (Apcolite Premium Satin enamel Paint color_Dried Spices 8749, Matt Finish, Brand- Asian Paint) with base primer .The boxing is to be fixed on wall with the help of triangular wedge shaped cuts of 40mm thick fire retardant ply and placed at a distance of 600mm c/c or as suggested by Cinépolis site incharge to provide adequate support and fine fabric fixing quality. c) Fiberglass wool - Providing and fixing acoustical treatment from UP twiga make with 50mm thick resin bonded fiberglass wool of density 20kg/cum, 1200x600mm board, 0.037w/ mk thermal conductivity, 0.9 NRC, 1.35 R-value (thermal resistance) on the existing masonry wall with plastic screw with cap finish @ 600mm c/c in proper plumb, level, line etc. complete.. e) Black matt fabric (C000196) - Fixing of Black matt fabric (provided by Cinepolis) on acoustically treated wall. The fabric to be fixed with gripper at 1300mm for rear walls and 600mm for side walls spacing. The job shall includes led light at every 4'. Only fabric will be supplied by Cinepolis. Rate to include all necessary hardware of approved quality, tools & tackles accessories, labour etc all complete. Only fabric will be supplied by Cinepolis, rest to be provided and fixed by the contractor. Refer drawings. | Sqm | 352.275 |  | 0
MEASUREMENT METHOD : Shall be measured along the surface area, only flat surface area to be measured
6.04 | Wall Carpet (BC01) Laying only of Roll stamped Carpet (provided by Cinepolis) up to a height of approximately 1500mm (up to bottom runner) and on Tunnel side walls. With the corners neatly and firmly fixed so as to avoid any peeling off. Rate to include for the labour, necessary accessories, approved quality of hardware/adhesive as per manufacturers exclusive of the carpet . The edge of the carpet hitting the floor is to be trimmed and all loose threads are to be sewed so that they do not come loose, etc. complete as per drawings. Only carpet roll to be provided by Cinépolis, rest all items to be considered in rates. Refer drawings. | Sqm | 655.2 |  | 0
MEASUREMENT METHOD : Shall be measured along the surface area, only flat surface area to be measured.
6.05 | Acrylic Coping above parapet Providing and Fixing 12mm thick acrylic solid surface pasted over 12mm thick fire retardant ply screwed to existing masonry wall in proper plumb, line and level with suitable adhesive overlapping on carpet laid on the parapet wall. Width of coping should be approximately 300mm wide and total 30mm high beading on both sides. Rate to include all the necessary accessories, tools & tackles, labour etc. complete. Refer drawings. | Rmt | RO | 0 | 0
Brand : Staron Lotte Model : Iris Thickness : 12mm
MEASUREMENT METHOD : Shall be measured as per the running length along which it has been installed
6.06 | Ply Box Panelling Providing and fixing of 18mm thick fire retardant ply base with required framework in made of 1.6mm thick of 50X25mm Aluminium over existing masonry for fixing speakers, maintenance lights, decorative lights, beam detector, transmitter, emergency lights, etc. complete as required. Refer drawings.
6.06.01 | size : 300 x 300 mm for maintenance light emergency light, Fire Beam Detectors transmitter. | NO's | 56 |  | 0
6.06.02 | size : 200 x 200 mm for evacuation arrow signage. | NO's | 16 |  | 0
6.06.03 | size : 600 x 600 mm for speakers | NO's | 72 |  | 0
6.06.04 | size : 1100 x 400 mm for Decorative light | NO's | 40 |  | 0
MEASUREMENT METHOD : Shall be measured as per installed numbers.
6.07 | Aluminium anodized corner guard Providing and fixing black aluminium anodized corner guard of size 12x 12 x 1mm to the horizontal junction of gypsum ceiling with parapet wall in access tunnel. The fixing is to be done with clear glue adhesive. Rate to include all the necessary accessories, tools & tackles, labour etc. complete. Refer drawings. Brand: Wall line | Rmt | 9.45 |  | 0
MEASUREMENT METHOD : Shall be measured as per the running length along which it has been installed
6.08 | Acoustical Sealant Providing and fixing of Acoustical sealant on the junction of Audi walls and structural roof as per drawings. The opening/joint surface should be cleaned of loose debris, dirt, oil, grease, moisture and frost free. The finishing should be done neat and as per the standards of the manufacturers specification. Rate to include all the necessary accessories, tools & tackles, labour etc. complete. Refer drawings. | Rmt | RO | 0 | 0
Brand: Hilti Model: FLEXIBLE FIRESTOP SEALANT CP 606
MEASUREMENT METHOD : Shall be measured as per the running length along which it has been installed
6.09 | Transition Profile Fixing PVC Transition Profile (provided by Cinepolis) between carpet & PVC Flooring in plum, line and level, etc complete. Rate to include all the necessary accessories, tools & tackles, labour etc. complete as per drawings. Only transition profile to be provided by Cinépolis, rest all items to be considered in rates. Refer drawings. | Rmt | 168 |  | 0
MEASUREMENT METHOD : Shall be measured as per the running length along which it has been installed
6.1 | Laminate Panelling with Partition & SS skirting (C007475) Providing and fixing laminate panelling with varies thickness as mentioned below with right angled OR curved corner as per drawing grid framing (600 x 600mm) in made of 1.6mm thick of 50mm x 25mm Aluminium frame vertical members and 50mmx 25mm Aluminium horizontal frame members as per detail including basework in 12mm thick commercial ply screwed over framework including hardware and accessories. Panelling shall be finished with 1mm thick Merino Laminate pasted over 4mm thick MDF factory pasted in proper plumb, level and line with suitable adhesives as per manufacturers recommendations, plywood edge thickness of cove to be finished with 1mm thick laminate. To include provision for mounting of poster case, signage, niche for TV (Niche shall be painted in Black), additional support for TV mount, Cove Light, etc. The skirting should be flushed with level of laminate panelling. Grains and joints of laminate should be aligned (as per drawing) etc, complete. Refer drawings. Note:- Required MS supports will be paid in separate other item respectively. ( If required )
Brand: Merino Model: Magas Walnut Bronze Design No. : 10866
MEASUREMENT METHOD : Shall be measured along the surface area.
6.10.1 | As per Item 6.11, but for upto 50mm thick Laminate Panelling on Blockwork/RCC surface. | Sqm | 30.45 |  | 0
6.10.2 | As per above Item 6.11, but for 50-150mm thick Laminate Panelling with necessary support from Floor, Ceiling & Wall. | Sqm | 39.9 |  | 0
6.10.3 | As per above Item 6.11, but for Box Partition more then 150mm thick Laminate Panelling with necessary support from Floor & Ceiling as required on site/as mentioned on drawing. | Sqm | 36.75 |  | 0
6.11 | Lacquered Glass Panelling with aluminium skirting (C000119) Providing and fixing tempered glass facade 100mm thick with grid framing (600 x 600mm) in made of 1.6mm thick of 50mm x 25mm Aluminium frame vertical members and 50mmx 25mm Aluminium horizontal frame members as per detail including basework in 12mm thick MDF nailed over existing framework including hardware and accessories. This is finished with 6mm thick tempered glass lacquer plainstrong black with silicon glue over the MDF base in a way that no pasting material is visible through the glass. The glass to have appropriate holes for the mounting of signage, LED screens. The glass joints are to be filled with enamel paint of matching shade. The sides of niches to be finished in Asian Paints Black Raven Song 8253. The skirting should be flushed with level of lacquered glass panelling etc, complete. Refer drawings.
| Brand : AIS Glass/ ASAHI Model : Tempered & Lacquered Colour : Plainstrong Black Thickness : 6mm | Sqm | 52.8 |  | 0
MEASUREMENT METHOD : Shall be measured along the surface area.
6.11.a | MIRROR PANEL (M01) Providing and fixing in position 6mm thick Mirror as per detail in drawing to 12mm thick ply shall be fixed to frame with rawl plug and screw. The job shall include fixing provision for LED light strip, mirror edge polishing, rounding, hardwood framing, powder coated black aluminium section around the mirror, fittings etc. complete as shown in drawing. | Sqm | 7.35 |  | 0
Brand for mirror : Saint Gobain Thickness : 6mm
6.12 | Inclined Laminate Ceiling with MS framework (for concession menu board & Cinépolis signage ) Providing and fixing false ceiling supported by MS frame work of size 50mm x 50mm x 5mm with grid of 600mmx1200mm, including all clamps and necessary members and hardware for fixing the frames to Structural slab (complete hardware). All MS members should consider welding, buffing, painting with 2 coats of anti-corrosive paint etc. The frame work should be finished with 12mm thick ply (BWR grade) and factory pasted 1mm thick laminate over 4mm thick MDF. The factory pasted laminate and MDF should be fixed to ply with help of suitable adhesive. The item includes mounting of LED screens, signages etc. Laminate joints to have 2mm wide grooves at equidistance as per drawing and the grooves to be filled in matching paint, etc. complete. Refer drawing.
| Brand : Merino Laminate Model : Magas Walnut Bronze Design No : 10866 | Sqm | 10.5 |  | 0
MEASUREMENT METHOD : Shall be measured along the surface area.
6.13 | Full Height Mirror to Dressing area Providing and fixing 6mm thick extra clear 1st quality lead backed mirrors in plum, line and level supported 19mm thick BWP ply on Aluminium frame with silicon sealers. Frame to be fixed on the wall with 30mm galvanized screw. This includes 'U' shape profile around the mirrors fixed with suitable adessive and provision for LED strip lights on the periphery of mirror frame work etc. complete. Refer drawings.
| Brand for mirror : Saint Gobain Thickness : 6mm Brand for edge profile : Walline Code : TIT U 1225 Finish : Gold Size : 12x 25mm | Sqm | 2.1 |  | 0
MEASUREMENT METHOD : Shall be measured along the surface area.
6.14 | Wash Basin Counter works Providing and fixing Wash Basin counter with top 650mm deep and 350mm height front apron of 12mm thick acrylic solid surface pasted on 18mm thick BWP Ply fixed over MS Base made out of 50x 50mm thick Box sections, L- angles, Fixed with necessary hardware, welded, finished with 2 coats of anti corrosive paint in proper plumb, level and line etc. complete. Refer drawings.
6.14.1 | Brand : Dupont Model : Natural Gray Thickness : 12mm DB Code: TBD12 | Sqm | RO | 0 | 0
6.14.2 | Brand : TBC Model : Black Galaxy Granite Thickness : 18mm Finish : Per-Polished DB Code: CT-03 | Sqm | 4.2 |  | 0
MEASUREMENT METHOD : Shall be measured along the surface area in plan
6.15 | Stainless steel Skirting (SK03) Providing and fixing modular SS Skirting of 100mm Height flushed suitable adhesive on base of 6mm thick BWR grade ply fixed on frame continuing from the laminate panelling. Including al necessary activities, tools, accessories, etc, complete. Refer drawing.
| Brand : Brand Jindal Finish : Grey Brushed Code : SK03 Height : 100mm | Rmt | 18.9 |  | 0
MEASUREMENT METHOD : Shall be measured as per the running length along which it has been installed
6.16 | Aluminium channel Providing and fixing Aluminium square brushed finish 8 x 8mm or 12 x 12mm over laminate panelling at junctions and grooves as per design etc. complete. Refer drawings.
| Brand : Wall line | Rmt | RO | 0 | 0
MEASUREMENT METHOD : Shall be measured as per the running length along which it has been installed
7 | PARTITION WORKS
7.01 | Gypsum Partition (gypsum board only one side) Providing and fixing of 50mm x 30mm G.I. stud framing with vertical made of 50mm single section at 600mm c/c with horizontal bracing at regular intervals 600mm c/c in staggered fashion including floor and ceiling channels horizontal metal noggins as per drawing or as per manufacturer specification/drawings for dry wall partition (upto bottom of slab) and all as per the drawings and specifications. The cost includes labour, materials, wastages, lead, lifts, hardware, any additional bracings required as per site. The cost shall also includes additional channel supports required to GI stud due to existing service ducts. The G.I. frame shall be covered with 12mm thick Gypsum board (one side) of approved make and necessary cutting for electrical conduits & electrical fittings, lighting. The job shall include provision for mounting of poster case, signage, niche for TV (Niche shall be painted in Black), additional support for TV mount, Cove Light, etc. The gypsum panelling must be finished with jointing compound, tapes and ready to receive plastic paint finish, etc, complete. Refer drawing. Note:- Required MS supports will be paid in separate other item respectively.
Gypsum board: Gyproc/ Armstrong/ Boral Hardware : Gyproc/ Armstrong Board thickness : 12.7mm
MEASUREMENT METHOD : Shall be measured along the surface area (one side).
7.01.01 | As per above Item 7.04, but for 50-150mm thick Gypsum partition with necessary support from Floor, Ceiling & Wall. | Sqm | 58.8 |  | 0
7.01.02 | As per above Item 7.04, but for Box Partition more then 150mm thick Gypsum Partition with necessary support from Floor, Ceiling & Wall. as required on site/as mentioned on drawing. | Sqm | 5.25 |  | 0
7.01a | 12mm Bison board Partition ( board only one side) Providing and fixing of 50mm x 30mm G.I. stud framing with vertical made of 50mm single section at 600mm c/c with horizontal bracing at regular intervals 600mm c/c in staggered fashion including floor and ceiling channels horizontal metal noggins as per drawing or as per manufacturer specification/drawings for dry wall partition (upto bottom of slab) and all as per the drawings and specifications. The cost includes labour, materials, wastages, lead, lifts, hardware, any additional bracings required as per site. The cost shall also includes additional channel supports required to GI stud due to existing service ducts. The G.I. frame shall be covered with 12mm thick Bison board (one side) of approved make and necessary cutting for electrical conduits & electrical fittings, lighting. The Cement Sheet panelling must be finished with jointing compound, tapes and ready to receive plastic paint finish, etc, complete. Refer drawing.
MEASUREMENT METHOD : Shall be measured along the surface area (one side).
7.01a.01 | Same as Item 7.04a, For partition thickness upto 150mm size | Sqm | 12.6 |  | 0
7.01a.02 | Same as Item 7.04a, For Box partition thickness more then 150 to as required on site/as mentioned on drawing | Sqm | 0 |  | 0
7.01b | 12mm Bison board Partition ( board both side) Providing and fixing of 50mm x 30mm G.I. stud framing with vertical made of 50mm single section at 600mm c/c with horizontal bracing at regular intervals 600mm c/c in staggered fashion including floor and ceiling channels horizontal metal noggins as per drawing or as per manufacturer specification/drawings for dry wall partition (upto bottom of slab) and all as per the drawings and specifications. The cost includes labour, materials, wastages, lead, lifts, hardware, any additional bracings required as per site. The cost shall also includes additional channel supports required to GI stud due to existing service ducts. The G.I. frame shall be covered with 12mm thick Bison board (one side) of approved make and necessary cutting for electrical conduits & electrical fittings, lighting. The Cement Sheet panelling must be finished with jointing compound, tapes and ready to receive plastic paint finish, etc, complete. Refer drawing.
MEASUREMENT METHOD : Shall be measured along the surface area (two side).
7.01b.01 | Same as Item 7.04a, For partition thickness upto 50mm size including door as required at site ( door accessories will be paid in separate item) | Sqm | 7.35 |  | 0
7.01b.01.1 | Exter over for door ( size - 625 x 2200mm high) including the lock, hinge, stopper, paint etc as required. | NO's | 2 |  | 0
7.01c | M.S FRAME WORK Steel work in built up tubular round, square or rectangular hollow tubes etc. including cutting, hoisting, fixing and finished with coat of red oxide primer and 2 or more coat of enamel paint including all lead and lift etc. as per architectural drawings and direction of EIC. | Kg | 750 |  | 0
7.02 | Temporary Store Providing and fixing temporary ply partition with 50mm x 30mm G.I. stud framing with vertical made of 50mm single section at 600mm c/c and horizontal bracing at 600mm c/c. These frames are fixed to the floor and soffit at 600mm centres with necessary hardware, finished with 12mm thick ply on both sides, including necessary cutting for electrical fittings. It also includes door shutter made in 12mm thk. ply with M.S. hold fasts/fasteners on all three side and all necessary hardware (hinges, handle) etc. complete. Refer drawings. | Sqm | 50 |  | 0
MEASUREMENT METHOD : Shall be measured along the surface area (one side).
8 | METAL WORK- RAMP, RAILING AND HANDRAIL
8.01 | MS Handrail Providing and Fixing MS handrail along parapet wall with circular handrail dia 38mm hollow pipe with supporting MS brackets @ 800mm c/c of 12mm thickness. The brackets must be fixed on wall with a 150mm high base of 12mm thick fire retardant ply covered with 12mm thick acrylic solid surface including turning at all edges, properly fixed in plumb, line and level . MS handrail is to be smooth with enamel paint including base preparation with putty, primer, proper grinding etc. Rate to include for all the necessary accessories, tools & tackles, labour, etc. complete. Refer drawings.
| Brand : Asian Paints Colour : Dried Spices 8749 Brand :Staron Lotte Finish : Matt Apcolite Premium Satin enamel Paint | Rmt | 69.52 |  | 0
MEASUREMENT METHOD : Shall be measured as per the running length along which it has been installed
8.02 | MS railing of 300mm Supplying and fixing of MS railing of 300mm in height in plumb, line and level with handrail of 38mm dia, vertical balusters of 38mm dia @ distance of approx. 900 mm c/c with horizontal bars of 25mm dia welded to give a neat look. Railing is to be smooth with enamel paint finish including base preparation with putty, primer, proper grinding etc. including cutting, hoisting, fixing in smooth at welded joints and joints have to be position as per detailed drawings etc. complete. Refer drawings. | Rmt | 38.85 |  | 0
MEASUREMENT METHOD : Shall be measured as per the running length along which it has been installed
8.03 | MS railing of 900mm Supplying and fixing of MS railing of 900mm in height in plumb, line and level with handrail of 38mm dia, vertical balusters of 38mm dia @ distance of approx. 900 mm c/c with horizontal bars of 25mm dia welded to give a neat look. Railing is to be smooth with enamel paint finish including base preparation with putty, primer, proper grinding etc. including cutting, hoisting, fixing in smooth at welded joints and joints have to be position as per detailed drawings etc. complete. Refer drawings. | Rmt | 71.4 |  | 0
MEASUREMENT METHOD : Shall be measured as per the running length along which it has been installed
8.04 | SS railing of 1000mm with Glass Supplying and fixing of stainless steel (Grade 304) railing with glass of 900mm in height in plumb, line and level with handrail of 38mm dia, vertical balusters of 25mm dia @ distance of approx. 900mm c/c (or actual division as per site conditions) welded to give a neat look. railings smooth & buffed finish at welding joints and joints have to be with gas welding etc, fitted with four nos. solid glass connectors for holding the infill glass of 12mm thick toughened and laminated, glass connector to be fitted with balustrade with the help of S.S srew overall mounted on S.S solid base plate 100x8mm with the help of dash fasteners. including cutting, hoisting, fixing in smooth & buffed finish at welding joints and joints have to be position as per detailed drawings etc. complete. Refer drawings. | Rmt | RO | 0 | 0
Brand for Glass : Saint Gobain Thickness : 12mm thick Toughened and Laminated
MEASUREMENT METHOD : Shall be measured as per the running length along which it has been installed
9 | PAINTING & POLISHING WORK
9.01 | Emulsion paint (water base) on Gypsum ceiling Providing and applying three coats of acrylic emulsion paint brand asian paint quality Semi-Matt or as approved on internal ceiling surfaces and wherever required at all level to give an an even and uniform shade, after thoroughly sand papering existing surfaces to remove dust, dirt etc. and repairing dents, cracks, holes with POP to achieve level surface and applied over a coat of primer and putty "Altek" or "Wall care" or approved equivalent as per manufacturer specification fully to give a smooth and an even surface including thoroughly brushing the surface free from water / mortar dropping and other foreign matter and sand papered smooth, complete as per directions by Cinepolis in-charge. Refer drawing.
9.01.01 | Brand : Asian paints Code : L104 Cotton Wool Finish : Matt Colour : White DB Code:- C008505 | Sqm | 0 |  | 0
9.01.02 | Brand : Asian paints Code : Grey Matter 8304 Finish : Stain Finish Colour : Grey DB Code:- C000142 | Sqm | 142.8 |  | 0
9.01.03 | Brand : Asian paints Code : Kesar Milk 7962 Finish : Matt Colour : Cream Paint DB Code:- C000144 | Sqm | RO | 0 | 0
9.01.04 | Brand : Asian paints Code : Royal Aspira- Raven Song 8253 Finish : Matt Colour : Black DB Code:- C007487 | Sqm | RO | 0 | 0
9.01.05 | Brand : Asian paints Code : Model 8760 English Castle Colour : Grey Finish : Oil Base DB Code:- C007472 | Sqm | 1654.8 |  | 0
MEASUREMENT METHOD : Shall be measured along the surface plan area. the coves, drops and other vertical recesses will be included in the plan measurement.
9.02 | Emulsion paint on Wall Providing and applying three coats of acrylic emulsion paint brand asian paint quality Semi-Matt or as approved on wall and wherever required at all level to give an even and uniform shade, after thoroughly sand papering existing surfaces to remove dust, dirt etc. and repairing dents, cracks, holes with POP to achieve level surface and applied over a coat of primer and putty "Altek" or "Wall care" or approved equivalent as per manufacturer specification fully to give a smooth and an even surface including thoroughly brushing the surface free from water / mortar dropping and other foreign matter and sand papered smooth, complete as per directions by Cinepolis in-charge. Refer drawing.
9.02.01 | Brand : Asian paints Code : Apcolite Premium Semi-Gloss Enamel Colour : Grey Matter 8304 Finish : Satin Finish, Oil Base BD Code:- C000143 | Sqm | 669.9 |  | 0
9.02.02 | Brand : Asian paints Code : Apcolite Premium Semi-Gloss Enamel Kesar Milk 7962 Finish : Matt, Oil Base Colour : Cream Paint DB Code:- C000144 | Sqm | 232.05 |  | 0
9.02.03 | Brand : Asian paints Code : L104 Cotton Wool Finish : Matt, Oil Base Colour : White DB Code:- C007473 | Sqm | 23.1 |  | 0
9.02.04 | Brand : Asian paints Code : Model 8760 English Castle Colour : Grey Finish : Oil Base DB Code:- C007472 | Sqm | 318.15 |  | 0
MEASUREMENT METHOD : Shall be measured along the surface area.
9.03 | Water base paint on ceiling inside Audi Providing and applying three coats of Acrylic paint shade brand,asian paint quality Semi-Mate or as approved on internal ceiling surfaces and wherever required at all level to give an even and uniform shade, after thoroughly sand papering existing surfaces to remove dust, dirt etc. and repairing dents, cracks, holes with POP to achieve level surface and applied over a coat of primer and putty "Altek" or "Wall care" or approved equivalent as per manufacturer specification fully to give a smooth and an even surface including thoroughly brushing the surface free from water / mortar dropping and other foreign matter and sand papered smooth, complete per drawings and as directed by the Project Manager. Refer drawings.
| Brand : Asian Paints Code : Raven Song 8253 Finish : Matt | Sqm | 206.85 |  | 0
MEASUREMENT METHOD : Shall be measured along the surface area.
9.04 | Water base paint on True Slab Providing and applying three coats of Acrylic paint shade brand,asian paint quality Semi-Mate or as approved on internal ceiling surfaces and wherever required at all level to give an even and uniform shade, after thoroughly sand papering existing surfaces to remove dust, dirt etc. and repairing dents, cracks, holes with POP to achieve level surface and applied over a coat of primer and putty "Altek" or "Wall care" or approved equivalent as per manufacturer specification fully to give a smooth and an even surface including thoroughly brushing the surface free from water / mortar dropping and other foreign matter and sand papered smooth, complete per drawings and as directed by the Project Manager. Refer drawings.
| Brand : Asian paints Code : 8304 Grey matter Finish : Water base | Sqm | 131.25 |  | 0
MEASUREMENT METHOD : Shall be measured along the surface area.
9.05 | Door Frame paint, oil base enamel paint (All size of frame as required) Providing and applying three coats of acrylic oil base enamel paint on door frame brand Asian paint quality Semi-Matt or as approved on wall and wherever required matching with door laminate at all level to give an even and uniform shade, after thoroughly sand papering existing surfaces to remove dust, dirt etc. and repairing dents, cracks, holes with POP to achieve level surface and applied over a coat of primer and putty "Altek" or "Wall care" or approved equivalent as per manufacturer specification fully to give a smooth and an even surface including thoroughly brushing the surface free from water / mortar dropping and other foreign matter and sand papered smooth, complete as per directions by Cinepolis in-charge. | Rmt | 85.05 |  | 0
MEASUREMENT METHOD : Shall be measured along the length
9.06 | Plaster of paris punning Providing and applying plaster of paris punning of average thickness 3-5 mm (or appropriate thickness as per site), of approved brand and manufacturer, over the plastered wall surface to prepare the surface even and smooth complete. This is to be done in complete plumb, line and level, etc. complete. Refer drawings. | Sqm | 50 |  | 0
MEASUREMENT METHOD : Shall be measured along the surface area.
10 | MISCELLENEOUS WORKS
10.01 | Modular Trap door Providing & fixing modular trap door in proper lintel and level, trap door in ceiling for any equipment coming above the ceiling as per services consultant requirements. The surface to be neatly finished with paint as per the color of ceiling. Rate also to include for the provision and fixing of GI/ Aluminium frame of make all as directed by the Site in charge. Refer drawings.
Brand : USG Boral/ Knoff/ Saint Gobain
10.01.01 | Size 1 - 600 X 750mm | NO's | 2 |  | 0
10.01.02 | Size 2 - 900 X 900mm | NO's | 2 |  | 0
10.01.03 | Size 3 - 1200 X 1500mm | NO's | 2 |  | 0
10.01.04 | Size 4 - 300 X 300mm | NO's | 2 |  | 0
10.01.05 | Size 5 - 600 X 600mm | NO's | 2 |  | 0
MEASUREMENT METHOD : Shall be measured as per installed numbers.
10.02 | Curtain for Ladies frisking Providing and fixing of curtain for ladies frisking booth with rod, hooks and all required accessories. Curtain should be made out of black fabric (provided by Cinepolis). Only fabric to be provided by Cinépolis, rest all items to be considered in rates, etc. complete. Refer drawings. | Sqm | 5 |  | 0
MEASUREMENT METHOD : Shall be measured along the surface area.
10.03 | Providing and fixing of frame less 12mm laminated toughened glass | Sqm | RO | 0 | 0
10.03a | Providing and fixing of frosted film on glass as per design - make 3M | Sqm | 27.3 |  | 0
10.04 | MS Stand for CO2 cylinders in Concession Back area Providing & Fixing the stand of size 300 x 300mm made out of vertical & horizontal Supports out of MS box sections of size 1"x1", MS pipes for holding the CO2 cylinders with a height of 1200mm and locking arrangement. The stand should be created for a set of 2 cylinders (10kg each). All MS sections are to be welded of stand as per design drawings. Bottom of stand to be covered with 8mm thick MS chequered plate. Also includes 2 coats of Anti-corrosive Paint and 2 coats of Black Enamel Paint, finished with necessary cutting & buffing. Including necessary hardware etc and complete. Refer drawings. | NO's | 5 |  | 0
10.05 | Installation of Accessories Installation of all the accessories as required with proper screwing with necessary extra supports, etc. complete. Refer drawings.
10.05.01 | DFMD | NO's | 1 |  | 0
10.05.02 | Loose furniture | NO's | 25 |  | 0
10.05.03 | Usher Module | NO's | 2 |  | 0
10.05.04 | M-Ticket scanner | NO's | 4 |  | 0
10.05.05 | LED screen | NO's | 6 |  | 0
10.05.06 | Postercase | NO's | 9 |  | 0
10.05.07 | Audi number signage | NO's | 0 |  | 0
10.05.08 | WC | NO's | 0 |  | 0
10.05.09 | Urinal | NO's | RO | 0 | 0
10.05.10 | Urinal Partition Size:- DB Code:- C010136 | NO's | RO | 0 | 0
10.05.11 | Washbasin | NO's | RO | 0 | 0
10.05.12 | Hand dryer | NO's | RO | 0 | 0
10.05.13 | Diaper changing station | NO's | RO | 0 | 0
10.05.14 | Tissue dispenser | NO's | RO | 0 | 0
10.05.15 | Soap dispenser | NO's | RO | 0 | 0
10.05.16 | Toilet Cubical partition | NO's | RO | 0 | 0
10.05.17 | Grab Bars | NO's | RO | 0 | 0
10.05.18 |  | NO's | 0 |  | 0
MEASUREMENT METHOD : Shall be measured as per installed numbers.
| TOTAL COST OF C&I WORKS |  |  |  | 0

## HVAC Summary
SUMMARY OF COSTS FOR HVAC WORKS FOR CINEPOLIS AT K MALL-JODHPUR
Sr.No. | Description | Unit | Amount
1 | TOTAL FOR AIR DISTRIBUTION SYSTEM | Rs. | 0
2 | TOTAL FOR INSULATION | Rs. | 0
| TOTAL | Rs. | 0

## HVAC BOQ
SCHEDULE OF QUANTITIES FOR LOW SIDE HVAC WORKS FOR CINEPOLIS AT K MALL,JODHPUR
SR. NO. | DESCRIPTION | Area 1 Qty | Area 2 Qty | Area 3 | Total Qty | UNIT | Rate Supply | Rate Install | Total Rate | AMOUNT (Rs)
[B] | AIR DISTRIBUTIONS SYSTEM
1 | GSS SHEET METAL DUCT: FACTORY FABRICATED
Supply, Fabrication, Installation and Testing of GSS metal ducts as per IS-277 (120 GSM both sides, LFQ & confirming to Class VIII) for GS Sheets and IS-655 for fabrication of following thicknesses including necessary G.I. hangers / supports, volume control duct dampers, accessories, vanes, 3mm neoprene rubber gasket etc. complete as per specifications in accordance with the approved shop drawings. (Ducts to be sent in Prefabricated form at the jobsite. Site work will include assembly, installation and suit to site pieces and collars/droppers.)
No slip joints shall be allowed. Flanges shall be MS angle flnges / Rolamate with fire retardant gasket 5mm thk. All ducts shall be with rigid supports as per technical specifications.
a) GI sheet ducts with reinforcement/Strengthening
b) Air tight joints
c) Accessories such as splitter damper, guide vane etc.
d) Hangers and supports
e) 2 coats of black paint for sa ducts after insulation
a | 24 gauge (0.63mm) |  | 510 |  |  | sqm |  |  | 0 | 0
b | 22 gauge (0.8mm) |  | 1950 |  |  | sqm |  |  | 0 | 0
c | 20 gauge (1.0mm) |  | 110 |  |  | sqm |  |  | 0 | 0
1.2 | Supply, Fixing & welding works required additional for duct support in MS frame work duly painted with 2 or more coat of enamal paint, as required complete in all respect (for Theatres) |  | RO |  |  | Kg |  |  | 0
2 | FLEXIBLE DUCTS (for Projection Exhaust)
Supply, Installation, Testing and Commissioning of insulated flexible ducts. The insulated flexible duct shall have inner core made of double lamination of metalized polyster film permenantly bonded to a coated spring stel wire helix. Fibreglass insulation of minimum 14 kg.cu.m. density having a R-value 4.2oF-Ft2-hr/btu and 25 mm thk shall be wrapped over the inner core and covered with stronger outer jacket cum vapor barrier made of fibreglass reinforced metalized polyester film laminate. The insulated flexible duct should be fire retardant type.
The insulated flexible duct should be fire retardant type. Limit Flexible Duct to not more than 3 Ft Length
a | Insulated Flexible ducts of 200 mm dia |  | 0 |  |  | RMT |  |  | 0 | 0
b | Insulated Flexible ducts of 300 mm dia |  | 0 |  |  | RMT |  |  | 0 | 0
2.1 | FLEXIBLE CONNECTION:
| Supply, fabrication & installation of double canvass (fire retardant) flexible connection as per drawings & specifications. [for Fans & AHUs] |  | 25 |  |  | sqm |  |  | 0 | 0
3 | VOLUME CONTROL DAMPER:
| Supply, Installation and adjusting of GSS Volume Control Damper within ducts complete with suitable links, levers. Blades should be double skinned aerofoil construction and opposed blades should be at 50mm pitch centres. The blades should be mounted in nylon bushes operated by an interior wheel gear system. Manual quadrant control with position indicator to be provided to enable adjust volume of air as required. |  | 15 |  |  | sqm |  |  | 0 | 0
3.1 | Back Draft Dampers
| Supply, installation, testing and commissioning of 16 G GSS Back draft dampers models shall be designed to allow exhaust airflow but prevent airflow in the reverse direction & shall be of counterweight type & normally in shut-off position. |  | 15 |  |  | sqm |  |  | 0 | 0
4 | FIRE AND SMOKE DAMPERS:
4.1 | Fire & Smoke Dampers with Fusible Link
Fire and Smoke Dampers (FSD) shall be installed in supply air duct when they pass through AHU room walls as shown in the drawings and as per specfications.The Fire Dampers shall be operated with atleast 90 minutes fire rating as per UL 555S - Class II for fire and smoke management rated for 90 min. & tested at CBRI Roorkee, India.
Fusible Link should be rated for 72oC. Each FSD shall be of multi leaf type, low leakage and shall be tested in the factory and will be certified by the manufacturer in form of the test certificate.
Each FSD shall be supplied with matching sleeve (factory supply) and set of retaining angles for installation on wall / slab as indicated on drawings.
| (To be installed in Supply air duct tapping to projection room-site measured) |  | 0 |  |  | sqm |  |  | 0
4.2 | Fire & Smoke Dampers with same specifications as above item 4.1 but suitable for motorised operation. (Motorised fire and smoke damper FSD is to be installed in SA & RA for all Cinema & Lobby AHU's) |  | 20 |  |  | sqm |  |  | 0 | 0
4.3 | Motorised Actuator
The Actuator shall be direct coupled spring return type and motorised.
| The Actuator shall be in line with the Technical Specifications and shall be maintenance free direct coupled spring return type suitable to work on 24 V electric supply. The torque rating of the actuator shall exceed at least by 15% over torque required to open / close the damper. Shall have manual over ride facility. The selection of actuator size shall be the responsibility of the manufacturer. Power on indicating lamps with 230 V / 24 V transformer,damper close & open indication, reset push button, push button for manual running of actuator for periodic inspection, auxiliary contacts 24V & 230 V, contact points to receive signal from smoke detector / fire alarm panel etc. should be provided. |  | 20 |  |  | nos |  |  | 0 | 0
5 | GRILLS & DIFFUSERS
(All Grill & Diffuser Samples Shall be Approved by Services Consultants & Architects prior to procurement)
5.1 | For Theatres (All Grills / Diffusers should be Black Mat Finish)
6.1.1 | Supply Air Ceiling Distributor
Distributor to have extruded aluminium outer core and a separate 4-way fixed deflection L bar central core. The central core should have a separate opposed blade volume control damper. Balance area should allow free flow of air through the outer cores. G.I Black painted plenum shall be mounted above the damper with a circular neck to accept insulated flexible duct. The finish to be powder coated-matt- black [out to out size - to match modular gridwork - 24" x 24"]
(The Ceiling Distributors shall be as per samples from approved vendors)
a | neck collar size - 450 mm dia. |  | 0 |  |  | Nos |  |  | 0
b | neck collar size - 400 mm dia. |  | 0 |  |  | Nos |  |  | 0
c | neck collar size - 375 mm dia. |  | 0 |  |  | Nos |  |  | 0 | 0
d | neck collar size - 300 mm dia. |  | 0 |  |  | Nos |  |  | 0 | 0
6.1.2 | Supply / Return Air Grill Assembly
Supply / Return Air Grill Assembly comprises of :
Extruded aluminium construction, powder coated. 15o one/two way fixed deflection with 4 side flanges (removable type) as required and as shown in the drawings.
Supply / Return Air Collar with Flanged joint on one side and sealed with Grill on other side. SA Collar should be manufactured in 22G GSS sheet & factory assembled with Supply Air Grill of straght / L shaped construction.
a | 600 x 200 |  | 0 |  |  | Nos |  |  | 0 | 0
b | 750 x 200 |  | 0 |  |  | Nos |  |  | 0 | 0
c | 900 x 200 |  | 0 |  |  | Nos |  |  | 0 | 0
d | 400 x 150 |  | 20 |  |  | Nos |  |  | 0 | 0
e | 750 x 150 |  | 4 |  |  | Nos |  |  | 0 | 0
f | Assorted Size |  | 11 |  |  | sqm |  |  | 0 | 0
6.1.3 | Supply / Return Air L-bar Grill
Extruded aluminium powder coated construction with 4 side end flanges Grill as required. Extruded aluminium construction, powder coated. 15o one/two way fixed deflection with 4 side flanges as required and as shown in the drawings.
a | 12" wide |  | 45 |  |  | RMT |  |  | 0 | 0
a | 8" wide |  | 0 |  |  | RMT |  |  | 0 | 0
b | 6" wide |  | 0 |  |  | RMT |  |  | 0
c | Assorted Size |  | 4 |  |  | sqm |  |  | 0 | 0
6.1.4 | Aluminium Box type collar low leakge damper with special arrangement for volume control for above (Black Matt Powder Coated finish) |  | 30 |  |  | sqm |  |  | 0 | 0
6.2 | For Lobby, Projection and Common Areas
6.2.1 | Supply / Return Air L-bar Continous Grill
Extruded aluminium construction, powder coated. 15o one way fixed deflection with end flanges as required and as shown in the drawings.
a | 10" wide |  | 0 |  |  | RMT |  |  | 0
b | 8" wide |  | 0 |  |  | RMT |  |  | 0 | 0
c | 6" wide |  | 120 |  |  | RMT |  |  | 0 | 0
d | Assorted Size |  | 0 |  |  | sqm |  |  | 0 | 0
6.2.2 | Supply / Return Air L-bar Continous Grill - Curved
In extruded aluminium construction, powder coated. 15o one way/2 way fixed deflection with end flanges as required and as shown in the drawings. The Grill shall be in curved form to match the FC.
a | 10" wide |  | 0 |  |  | RMT |  |  | 0
b | 8" wide |  | 0 |  |  | RMT |  |  | 0 | 0
c | 6" wide |  | 0 |  |  | RMT |  |  | 0 | 0
d | Assorted Size |  | 0 |  |  | sqm |  |  | 0 | 0
6.2.3 | Air Ceiling Distributor (Supply )
Supply, Installation of Air Distributor to have extruded aluminium outer core and a separate 4-way central core. Balance area should allow free flow of air through the outer cores. [out to out size - to match modular gridwork - 24" x 24"]
(The Ceiling Distributors shall be as per samples from approved vendors)
Factory fitted aluminium Box type collar low leakge damper with special arrangement for volume control for above (Black Matt Powder Coated finish) to be included.
a | neck collar size - 450 mm dia. |  | 0 |  |  | Nos
b | neck collar size - 400 mm dia. |  | 0 |  |  | Nos
c | neck collar size - 350 mm dia. |  | 0 |  |  | Nos
d | neck collar size - 300 mm dia. |  | 0 |  |  | Nos |  |  | 0 | 0
6.2.3 | Air Ceiling Distributor (Return)
Supply, Installation of Air Distributor to have extruded aluminium outer core and a separate 4-way central core. Balance area should allow free flow of air through the outer cores. [out to out size - to match modular gridwork - 24" x 24"]
(The Ceiling Distributors shall be as per samples from approved vendors)
a | neck collar size - 450 mm dia. |  | 0 |  |  | Nos
b | neck collar size - 400 mm dia. |  | 0 |  |  | Nos
c | neck collar size - 350 mm dia. |  | 0 |  |  | Nos
d | neck collar size - 300 mm dia. |  | 0 |  |  | Nos |  |  | 0 | 0
6.2.4 | Jet Diffusers
The supply air terminal should be in Al powder coated construction with easily removable i-ball type adjustable air distribution. Volume control damper to be of opposed blade, nylon geared with aerofoil blades & black matt powder coated.
a | Diffuser Size 18" Dia |  | 0 |  |  | Nos |  |  | 0
b | Diffuser Size 15" Dia |  | 0 |  |  | Nos |  |  | 0
6.2.5 | The supply air terminal should be in Al powder coated construction with easily removable i-ball type adjustable air distribution. Volume control damper to be of opposed blade, nylon geared with aerofoil blades & black matt powder coated.
a | JET NOZZLES (I-BALL TYPE) (450 MM DIA) |  | 0 |  |  | Nos
b | JET NOZZLES (I-BALL TYPE) (400 MM DIA) |  | 40 |  |  | Nos |  |  | 0 | 0
6.2.6 | Disc Valves For Toilet Exhaust System
Supply, installation and adjusting of disc valves suitable for exhausting toilet foul air ,comprising of an adjustable centre cone and coupling sleeve made of Aluminum sheet duly epoxy painted with approved color. The disc valve shall be fitted with a galvanised steel installation frame and the sleeve shall incorporate a foam-rubber gasket for airtight sealing. The centre cone should be adjustable for balancing and with a locking arrangement to maintain the desired flow rate.
a | 100 mm dia |  | 0 |  |  | Nos |  |  | 0
b | 150 mm dia |  | 30 |  |  | Nos |  |  | 0 | 0
c | 225 mm dia |  | 0 |  |  | Nos |  |  | 0
6.2.7 | Supply, installation and adjusting of Non Vision transfer grilles in extruded aluminium comprising of a non vision door grille on one side and complete with sliding frame on the opposing side. The assemble shall be suitable for the door thickness as per site conditions. The color shall match the interior requirements.
a | 300 x200 |  | 3 |  |  | No. |  |  | 0 | 0
b | 450 x200 |  | 3 |  |  | No. |  |  | 0 | 0
c | 450 x300 |  | 3 |  |  | No. |  |  | 0 | 0
d | 700 x300 |  | 0 |  |  | No. |  |  | 0 | 0
e | 800 x 450 |  | 1 |  |  | No. |  |  | 0 | 0
f | 800 x 700 |  | 1 |  |  | No. |  |  | 0 | 0
6.2.8 | Aluminium Box type collar low leakge damper with special arrangement for volume control for above (Black Matt Powder Coated finish) |  | 6 |  |  | sqm |  |  | 0 | 0
7 | DUCT SOUND ATTENUATORS:
| Supply & Installation of Sound Attenuators -1500 mm long duct silencers at Cinema AHU Outlets as shown in the drawings. (For Audi's only to be considered as crosssectional area) |  | 0 |  |  | sqm |  |  | 0 | 0
8 | TIMER CONTROLLER
| Supply, Installation, Testing & Commissioning of Timer panel for operating Fans as per required schedule. This item shall include necessary relay, Contactor, timer, required accessories etc to operate Attic ventilation fans shall be operational for required time period at predetermined time interval & these should be user settable. This panel shall be installed near the fan panel. Power & Control cabling as required shall be lumpsum & to be included under this item. |  | 0 |  |  | Nos. |  |  | 0
| TOTAL FOR "B" AIR DISTRIBUTION SYSTEM | [8 empty] | 0
[C] | DUCT INSULATION
1 | ACOUSTIC LINING (DUCTS):
Supply, installation & testing of acoustic lining within supply and return air ducts as per specifications. All ducts shown cross hatched on the approved shop drawings shall be provided with acoustic lining of thermal insulation as per the specifications, Fibre glass insulation with 48 kg/cu.m. density with RP tissue and 24 G perforated Alum. Sheet as per Technical Specifications. (First 5 RMT of SA / RA Duct coming out of plenum box shall be internally insulated with acoustic insulation.)
1.1 | 12 mm thick acoustic lining (for Other areas) |  | 80 |  |  | sqm |  |  | 0 | 0
1.2 | 25 mm thick acoustic lining (for Theatres) |  | 375 |  |  | sqm |  |  | 0 | 0
2 | THERMAL INSULATION
Supply, installation & testing of external thermal insulation on ducts as per the specifications & approved shop drawings, Fibre glass insulation with 24 kg/sq.m. density with factory backed Alum. Foil of 0.09 mm thickness. Aluminium foil to be painted with black enemal paint.
2.1 | 25 mm thick Insulation |  | 2060 |  |  | sqm |  |  | 0 | 0
3 | THERMAL INSULATION FOR EXPOSED DUCT
Supply, fabrication & Installation of FM Global approved thermal insulation on GI ducts complete with Closed Cell Foam with factory backed Galss cloth with minimum density of 40 Kg/m3 with minimum R Value 4.1/inch & thermal conductivity -0.035 w/mok confirming to Class 'O' & the inner side stuck to the outer facia of the GI ducts with recommended / Proprietory Synthetic adhesive bonding (SR998 or equivalent) & installed as per manufacturers recommendation. The insulation joints shall be sealed with 3" wide Black Tape.
2.1 | 9 mm thick Insulation |  | 0 |  |  | sqm |  |  | 0 | 0
2.2 | 13 mm thick Insulation |  | 0 |  |  | sqm |  |  | 0 | 0
2.3 | 16 mm thick Insulation |  | 0 |  |  | sqm |  |  | 0 | 0
2.4 | 19 mm thick Insulation |  | 0 |  |  | sqm |  |  | 0 | 0
2.5 | 25 mm thick Insulation |  | RO |  |  | sqm |  |  | 0
| TOTAL FOR "C" INSULATION | [8 empty] | 0

## MV Summary
SECTION | Description | Amount
RENOVATION
A | WIRING SYSTEM (POINT WIRING) | 0
B | L.V.CABLES & WIRES | 0
C | LT PANELS AND DISTRIBUTION BOARDS | 0
D | EARTHING SYSTEM | 0
E | INSTALLATION OF LIGHT FIXTURES. | 0
F | COMMUNICATION DATA AND VOICE | 0
G | AUDI SPEAKER SYSTEM WIRING | 0
H | TEMPORARY WORK | 0
| Total | 0

## Wiring System
PROJECT: MULTIPLEX FOR CINEPOLIS INDIA PVT. LTD
4 SCREEN MULTIPLEX AT K. MALL JODHPUR
BILL OF QUANTITIES FOR ELECTRICAL WORKS
SR. | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
A | WIRING SYSTEM (POINT WIRING)
The following light points are done with 2R x 2.5Sqmm+ 1x1.5Sqmm FRLS wires. The cost to include - PVC LHSFT conduits, inspection bends, junction boxes with cover plates, FRLS wires, wire connectors, angle holders, flexible pipe etc inclusive of all accessories, as required for final installation of light fixtures.
1.01 | Primary light point (Local control) - One light point controlled by one single way 6 A switch - length upto 8.00 mtrs. | No's | 30 | 0 | 0
1.02 | Secondary Light point - One light point controlled by one single way 6 A switch looped from above and subsequnet loops - length upto 5.00 mtrs without switch. | No's | 20 | 0 | 0
1.03 | Primary Light point (DB Controlled) One light point controlled by MCB directly from DB - length upto 30.00 mtrs. | No's | 40 | 0 | 0
1.04 | Secondary Light Point One light point controlled by MCB directly from DB - looped from above and subsequent loops - length upto 5.0 mtrs. | No's | 180 | 0 | 0
2 | POWER POINTS
The following power points are done with 2R x 2.5 sq.mm + 1x1.5 Sqmm FRLS Wires. The cost to include PVC LHSFT conduits, inspection bends, junction boxes, with cover plates, FRLS wires, MS switch boxes (surface mounted/concealed), switch plates (of colours white/grey/black), switches (of colours white/grey/black) and sockets (of colours white/grey/black) as per drawings and instructions of the site incharge.
2.1 | Primary Power Point - One 6 A x 5 pin 230 volt socket outlet point controlled by one 6 A switch located on switch board length upto 10.0 mtrs. | No's | 35 | 0 | 0
2.2 | Secondary Power point One 6 A x 5 pin 230 volt socket outlet point controlled by one 6 A switch located on switch board length upto 5.0 mtrs. | No's | 75 | 0 | 0
2.3 | Two 6 A x 5 pin 230 volt socket outlet point controlled by Two 6 A switch located on switch board length upto 10.0 mtrs. | No's | RO | 0
3 | The following power points are done with 2R x 4.0 sq.mm + 1x2.5 Sqmm FRLS Wires. The cost to include PVC LHSFT conduits, inspection bends, junction boxes, with cover plates, FRLS wires, MS switch boxes (surface mounted/concealed), switch plates (of colours white/grey/black), switches 6/16A (of colours white/grey/black) and sockets 6/16A (of colours white/grey/black) as per drawings and instructions of the site incharge.
3.01 | Primary Power point One 6/16 A x 5 pin 230 volt socket outlet point controlled by one 16 A switch located on switch board length upto 10.0 mtrs. | No's | 55 | 0 | 0
3.02 | Secondary Power point One 6/16 A x 5 pin 230 volt socket outlet point controlled by one 16 A switch located on switch board length upto 5.0 mtrs. | No's | 110 | 0 | 0
3.03 | Two 16 A x 5 pin 230 volt socket outlet point controlled by Two 16 A switch located on switch board - primary - length upto 15.0 mtrs. | No's | 20 | 0 | 0
3.04 | Three 16 A x 5 pin 230 volt socket outlet point controlled by Two 16 A switch located on switch board - primary - length upto 15.0 mtrs. | No's | RO | 0
3.05 | Four 16 A x 5 pin 230 volt socket outlet point controlled by Two 16 A switch located on switch board - primary - length upto 15.0 mtrs. | No's | RO | 0
3.06 | Supply & Installation of 16A, 3 pin, Industrial plug top & socket (Male/Female) PVC couplers, Single Phase with 1 Neutral & 1 Earth, & 16A IP-44 weatherproof connectors (Kitchen area) | No's | 18 | 0 | 0
4 | CIRCUIT WIRNG - MAINS & SUB MAINS
Providing and drawings mains of the following sizes of Cu. FRLS PVC insulated flexible wires with ISI and FIA approval for 650 V / 1100 V with all necessary accessories in existing/prelaid conduits and raceways.
4.01 | 2x16Sqmm +1x6Sqmm | mtr | 0 | 0 | 0
4.02 | 2x10Sqmm +1x6Sqmm | mtr | 0 | 0 | 0
4.03 | 2x6Sqmm + 1x4Sqmm | mtr | 180 | 0 | 0
4.04 | 2x4Sqmm + 1x2.5Sqmm | mtr | 550 | 0 | 0
4.05 | 2x2.5Sq.mm + 1x1.5 Sq.mm | mtr | 600 | 0 | 0
4.06 | 4x6Sqmm + 2x4Sqmm | mtr | 90 | 0 | 0
4.07 | 4x4Sqmm + 2x2.5Sqmm | mtr | 90 | 0 | 0
5 | Supply and Installation of Conduits with juntion boxes, bends, elbows and coupler's including metal back box for data and telephone point etc., with saddle base's, saddle's etc. fixed on the surface/concealed inside the masonry walls and surface mounted on ceiling soffits, laid over false framing etc. ( For data, voice and speaker cable)
5.01 | 32mm dia, 2 mm thick PVC LHSFT conduit | mtr | 0 | 0 | 0
5.02 | 25mm dia, 2 mm thick PVC LHSFT conduit | mtr | 3500 | 0 | 0
5.03 | 19mm dia, 2 mm thick PVC LHSFT conduit | mtr | 5500 | 0 | 0
| Total cost of Section 'A' Point wiring |  |  |  | 0

## Cables & Wires
PROJECT: MULTIPLEX FOR CINEPOLIS INDIA PVT. LTD
4 SCREEN MULTIPLEX AT K. MALL JODHPUR
BILL OF QUANTITIES FOR ELECTRICAL WORKS
SR. | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
B | L.V.CABLES & WIRES
1 | Providing, laying, testing and commissioning of 1100V grade PVC insulated PVC sheathed steel wire/ tape armoured aluminium conductor cable for mains and sub mains as per specifications and drawings. The cables shall be laid in concrete trenches or buried directly underground or on cable trays. The concrete trenches will be measured separate. The cost of the cable trays or ladders, excavation and back filling of trenches will be measured separate. the unit cost of the cable shall include clamps, fasteners etc. as required for proper installation.
ALUMINIUM ARMOURED CABLE
1.01 | 3.5C x 240 Sqmm A2XFY | mtr's | 40 | 0 | 0
1.02 | 3.5C x 150 Sqmm A2XFY | mtr's | RO | 0
1.03 | 3.5C x 95 Sqmm A2XFY | mtr's | 65 | 0 | 0
1.04 | 3.5C x 70 Sqmm A2XFY | mtr's | 35 | 0 | 0
1.05 | 3.5C x 50Sqmm A2XFY | mtr's | RO | 0
1.06 | 3.5C x 35Sqmm A2XFY | mtr's | RO | 0
0
1.07 | 4C x 25Sqmm A2XFY | mtr's | 190 | 0 | 0
1.08 | 4C x 16Sqmm A2XFY | mtr's | 614 | 0 | 0
COPPER ARMOURED CABLE
1.09 | 4C x 16 Sqmm 2XWY Cable | mtr's | RO | 0
1.1 | 4C x 10 Sqmm 2XWY Cable | mtr's | RO | 0
1.11 | 4C x 6 Sqmm 2XWY Cable | mtr's | 35 | 0 | 0
1.12 | 4C x 4 Sqmm 2XWY Cable | mtr's | 595 | 0 | 0
1.13 | 4C x 2.5 Sqmm 2XWY Cable | mtr's | 150 | 0 | 0
1.14 | 3C x 6 Sqmm 2XWY Cable | mtr's | 18 | 0 | 0
1.15 | 3C x 4 Sqmm 2XWY Cable | mtr's | 180 | 0 | 0
1.16 | 3C x 2.5 Sqmm 2XWY Cable | mtr's | RO | 0
1.17 | 1C x 50 Sqmm YY Cable | mtr's | 60 | 0 | 0
1.18 | 1C x 6 Sqmm YY Cable | mtr's | 160 | 0 | 0
1.19 | PRIMARY POINT 2C X 4 Sq. mm - LED DRIVER | mtr's | 550 | 0 | 0
1.2 | SECONDARY POINT 2C X 2.5 Sq. mm - LED DRIVER | mtr's | 450 | 0 | 0
2 | Supply & Installing cable terminations for the below cables including Double compression suitable glands and lugs(crimping type), PVC taping as required and all accessories complete. (For aluminium cable, Aluminium Glands & lugs to be used. For copper cables, glands & lugs will be copper) ( The rate shall include gland earthing also.)
| ALUMINIUM ARMOURED CABLE |  |  |  | 0
2.01 | 3.5C x 240 Sqmm A2XFY | Nos | 4 | 0 | 0
2.02 | 3.5C x 150 Sqmm A2XFY | Nos | 8 | 0 | 0
2.03 | 3.5C x 95 Sqmm A2XFY | Nos | 2 | 0 | 0
2.04 | 3.5C x 70 Sqmm A2XFY | Nos | RO | 0
2.05 | 3.5C x 50Sqmm A2XFY | Nos | 2 | 0 | 0
2.06 | 3.5C x 35Sqmm A2XFY | Nos | 2 | 0 | 0
2.07 | 4C x 25Sqmm A2XFY | Nos | RO | 0
2.08 | 4C x 16Sqmm A2XFY | Nos | 44 | 0 | 0
COPPER ARMOURED CABLE
2.09 | 4C x 16 Sqmm 2XWY Cable | Nos | RO | 0
2.1 | 4C x 10 Sqmm 2XWY Cable | Nos | 20 | 0 | 0
2.11 | 4C x 6 Sqmm 2XWY Cable | Nos | 2 | 0 | 0
2.12 | 4C x 4 Sqmm 2XWY Cable | Nos | RO | 0
2.13 | 4C x 2.5 Sqmm 2XWY Cable | Nos | RO | 0
2.14 | 3C x 6 Sqmm 2XWY Cable | Nos | RO | 0
2.15 | 3C x 4 Sqmm 2XWY Cable | Nos | 32 | 0 | 0
2.16 | 3C x 2.5 Sqmm 2XWY Cable | Nos | 30 | 0 | 0
2.17 | 1C x 50 Sqmm YY Cable | Nos | 16 | 0 | 0
2.18 | 1C x 6 Sqmm YY Cable | Nos | 36 | 0 | 0
2.19 | PRIMARY POINT 2C X 4 Sq. mm - LED DRIVER | Nos | 60 | 0 | 0
2.2 | SECONDARY POINT 2C X 2.5 Sq. mm - LED DRIVER | Nos | 70 | 0 | 0
2.21 | Providing & laying of 2mm thick and 50mm in height ladder type GI cable tray of the following sizes . ( The rate shall include all accessories required for wall mounting, floor run, ceiling hung etc. with all neccessary MS/GI supports, RCC fastners, MS/GI bolts - nuts - washers etc., cost of MS supports is included )
LADDER GI CABLE TRAY
2.31 | 600X100 mm | mtr's | 50 | 0 | 0
2.41 | 400X 50mm | mtr's | 0 | 0 | 0
2.51 | 300X40 mm | mtr's | 75 | 0 | 0
2.61 | 150X40 mm | mtr's | 50 | 0 | 0
4 | Supply & Installation of floor mounted GI Race way (2.0/1.6mm thick) with cover's |  | 0
4.1 | 300 x 50mm, 2.0 mm thick | mtr's | 0 | 0 | 0
4.2 | 200 x 50mm , 1.6mm thick | mtr's | 0 | 0 | 0
4.3 | 150 x 50mm, 1.6mm thick | mtr's | 150 | 0 | 0
4.4 | 100 x 50mm, 1.6mm thick | mtr's | 75 | 0 | 0
4.5 | 50 x 50mm, 1.6mm thick | mtr's | 20 | 0 | 0
5 | Supply & Installation of wall/ceiling mounted GI Race way junction boxes with top openable cover's
5.1 | 325 X 325 X 75 mm | No's | 2 | 0 | 0
5.2 | 225 X 225 X 75 mm | No's | 0 | 0 | 0
5.3 | 175 X 175 X 75 mm | No's | 14 | 0 | 0
5.4 | 125 X 125 X 75 mm | No's | 22 | 0 | 0
6 | Supply and laying of MS angle ( MS sections of all types and sizes with welding and all types of fasyened arrangements etc. ) as per site manager's aproval | Kg's | 750 | 0 | 0
| Total cost of Section 'B' L.V. Cables & Wires |  |  |  | 0

## LT Panels and DB
PROJECT: MULTIPLEX FOR CINEPOLIS INDIA PVT. LTD
4 SCREEN MULTIPLEX AT K. MALL JODHPUR
BILL OF QUANTITIES FOR ELECTRICAL WORKS
SR. | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
C | LT PANELS AND DISTRIBUTION BOARDS
Supply, installation, testing and commissioning of M.V.Distribution Boards suitable for 415V, 3 ph, 4 wire, 50Hz distribution system. The panel shall be free standing, floor mounting, sheet metal enclosed, flush front with aluminium busbars, separate earth bus shall be provided throughout the length of the panel. The incoming and the outgoing feeder breakers, switch fuse units, change over switches, indicating lamps, meters etc. shall be accommodated in a modular multi tier arrangement. A minimum of 400mm clearance shall be given from the floor level to the bottom most termination point. The painting shall be done in conformity with IS code. Adequate size cable alley shall be provided all round the panel and at the back for easy bending and terminations. The outgoing feeders inside the panel shall be connected through solid busbars. Flexible cable links are not acceptable. Busbars shall be provided with PVC heat shrinkable sleeves or heat resistant insulated paint. The panels shall be suitable for cable entry from top. The copper earth strip of minimum 25mm x 3mm shall run throught out the length of the top / bottom of the panel ( All MCCB'c are Thermal magnetic released MCCB'S), All the MCCB,s should have rotary handle ( RHOM))
General Notes:
a | The construction of the panel shall comply to latest standards of IEC 61439.
b | The Panel shall be fully as per the requirement of Electrical Inspectorate/ CEIG authorities.
c | Auxilliary contactor to be provided along with auto-manual switch .
d | All doors to have double rubber gasket with shutter assembly & door seating frame.
e | Any panel if more than 2.5 mts width should be made in parts each part not exceeding 2.5mts
f | All UPS outgoing panels shall have neutral busbars double the size of phase.
g | Breaker terminal connections from the dropper bus shall be through only Al/Cu. bus to be used.
h | The Bus bars and connectors should have extruded insulation
i | Base frame shall be with each panel. The size will be equal to each section.
j | Bi-metallic tape / washers to be used where ever copper & Aluminium are joined.
k | Auto-Manual switch shall be provided for all motorised breakers.
l | All the DB's should be installed with suitable cable end boxes or suitable frames.
m | Specification proposed only for Tender purpose. The contractor has to submit final BOM for our approval as per SLD.
n | Contractor should refer drawings and site conditions before quoting the panels.
o | Panel Vendor should submit actual BOM as per SLD. All the panels shall be as per SLD only.
p | IP-54 for indoor type and IP-65 for outdoor type
q | Prior ordering any items contractor has to take approval from Cinepolis Site/Project incharge.
1.1 | MAIN DISTRIBUTION PANEL-MDB ( Refer SLD 1 ) Indoor | SET | 1 | 0 | 0
Incommer -1 / Incommer - 2
1000A TPN 50 kA ACB microprocessor based O/L, S/C and E/F release-2 Set
Breaker ON / OFF / TRIP indicating lamps with suitable rating control SP MCB - 2 Set
RYB phase indicating lamps with suitable rating control SP MCB - 2 Set
CT 1000/5A 15 VA, CL.1- 3 Nos+ 1 No. 1000/5A CT for RTPFC panel (Provision)
MFM with RS-485 port- 2 Set (parameters V, I, Hz, KWH, PF, KW, KVAR, max. demand KW)
Incomer 1 & 2 to be interlocked electromechanically.
Outgoing
630A FP MCCB, 25kA Thermal magnetic based O/L, S/C release- 1 Set with CT & KWH meter
160A FP MCCB, 25kA thermal magnetic based O/L, S/C release- 3 Set with CT & KWH meter
125A FP MCCB, 25kA thermal magnetic based O/L, S/C release- 1Set with CT & KWH meter
63A FP MCB, 10kA-10 Nos with KWH meter
40A FP MCB, 10kA-4 Nos with KWH meter
1.4 | UPS OUTPUT PANEL (60KVA) ( Refer SLD 2) Indoor type | SET | 1 | 0 | 0
Incomer:-
160A FP Changeover switch- 1Set
160A FP MCCB,25kA thermal magnetic based O/L, S/C release - 1Set
Metering & Protection:-
Breaker ON / OFF / TRIP indicating lamps with suitable rating control SP MCB - 1Set
RYB phase indicating lamps with suitable rating control SP MCB - 2 Set
Digital Protection MCB, VSS, Voltmeter-2 Set
CT 160/5A 15 VA, CL.1- 1 Set
Busbar:-
160A TP+2N AL busbar (25KA) insulated with colour coded heat shrinkable sleeves. Current density 0.8A/ Sqmm.
Outgoing:-
63A FP MCB 10kA- 6 Nos
1.5 | PDB CONCESSION ( Refer SLD 8) Indoor type | SET | 1 | 0 | 0
Incomer:-
160A FP MCCB,25kA thermal magnetic based O/L, S/C release - 1Set
63A 100 mA DP RCCB-3 Nos
63A 100 mA FP RCCB-1 Nos
Metering & Protection:-
Breaker ON / OFF / TRIP indicating lamps with suitable rating control SP MCB - 1Set
RYB phase indicating lamps with suitable rating control SP MCB -1 Set
Digital VAF Meter
CT 160/5A 15 VA, CL.1- 1 Set
Busbar:-
160A TP+2N AL busbar (25KA) insulated with colour coded heat shrinkable sleeves. Current density 0.8A/ Sqmm.
Outgoing:-
10-32A SP MCB - 30 Nos
63A FP MCB 10kA- 4 Nos
1.6 | HVAC panel-1 ( Refer SLD 6 ) indoor | SET | 1 | 0 | 0
Incomer:-
630A FP MCCB,35kA thermal magnetic based O/L, S/C, E/F release - 1Set
Metering & Protection:- (each incomer)
Breaker ON / OFF / TRIP indicating lamps with suitable rating control SP MCB - 1Set
RYB phase indicating lamps with suitable rating control SP MCB - 1Set
MFM with RS-485 port- 1Set (parameters V, I, Hz, KWH, PF, KW, KVAR)
CT 600/5A 15 VA, CL.1- 3 Nos
Busbar:-
600A TPN Al busbar (35KA) insulated with colour coded heat shrinkable sleeves. Current density 0.8A/ Sqmm.
Outgoing:-
100A FP MCCB-6 Nos
10-32A FP MCB - 15 Nos
40-63A FP MCB - 3 Nos
1.9 | Smoke exhaust panel ( Refer SLD 7 ) Outdoor | SET | 1 | 0 | 0
Incomer:-
160A FP MCCB,25kA thermal magnetic based O/L, S/C, E/F release - 1Set
Metering & Protection:-
Breaker ON / OFF / TRIP indicating lamps with suitable rating control SP MCB - 1Set
RYB phase indicating lamps with suitable rating control SP MCB - 2 Set
MFM with RS-485 port- 1 Set (parameters V, I, Hz, KWH, PF, KW, KVAR)
CT 160/5A 15 VA, CL.1- 3 Nos
Busbar:-
160A TPN Al busbar (25KA) insulated with colour coded heat shrinkable sleeves. Current density 0.8A/ Sqmm.
10-32A FP MCB 10kA- 15Nos
| TOTAL OF LT FABRICATED PANELS |  |  |  | 0
2 | LT DISTRIBUTION BOARDS
Supply, installation, testing and commissioning of the following Distribution Boards made of 18 gauge powder coated MS sheet steel, Cu busbar, wall mounted/fully recessed in wall, indoor industrial type, with dust proof, hinged and lockable doors, double door design, complete with inter connecting wires from incomer MCB to each RCCB along with earthing terminal. The top and bottom of the box shall have adequate number of knockouts suitable to receive the conduits and cables. All MCB to be 10kA. All MCBs are C curve except UPS DBs. IP-43. Refer SLD.
2.1 | LPDB AUDI 1,2,3,4 (Refer SLD 11,12,13,14) | SET | 4 | 0 | 0
12 WAY TPN DB
Incomer:-
63A FP MCB, 10kA- 1No
Sub-incomer:-
40A DP RCCB, 100mA- 3Nos
Outgoing: -
6-25A SP MCB, 10kA- 30 Nos
2.2 | AUDI projection DB ( Refer SLD 2.2 to 2.4 ) | SET | 4 | 0 | 0
Flexi DB 4R X 14 M
Incomer:-
63A FP MCB, 10kA- 1Nos
Sub-incomer:-
40A DP RCCB, 100mA- 3Nos
Outgoing: -
10-32A DP MCB, 10kA- 12 Nos
32A FP MCB, 10kA- 2 Nos
2.3 | AUDI EM UPS O/P DB (Refer SLD 3) | SET | 6 | 0 | 0
12 Way SPN DB
Incomer:-
40A DP MCB, 10kA- 1No
Outgoing: -
32A DP MCB, 10kA 5 Nos
2.4 | EM-DB AUDI 1/2/3/4 (Refer SLD 3.1 to 3.4) | SET | 4 | 0 | 0
12 Way SPN DB
Incomer:-
25A DP RCBO, 30kA- 1No
Outgoing: -
10-16A SP MCB, 10kA - 8 Nos
2.5 | UPS 3 IT O/P DB ( Refer SLD 4) | SET | 1 | 0 | 0
12 Way SPN DB
Incomer:-
63A DP MCB- 1No
Outgoing: -
10-16A SP MCB, 10kA - 4 Nos
2.6 | IT UPS DB-1 ( Refer SLD 4.1) | SET | 1 | 0 | 0
12 Way SPN DB
Incomer:-
16A DP MCB- 1No
Outgoing: -
10-16A SP MCB, 10kA - 4 Nos
2.7 | IT UPS DB-2 ( Refer SLD 4.2) | SET | 1 | 0 | 0
12 Way SPN DB
Incomer:-
16A DP MCB- 1No
Outgoing: -
10-16A SP MCB, 10kA - 8 Nos
2.8 | LOBBY INVERTER O/P DB ( Refer SLD 5) | SET | 1 | 0 | 0
12 way SPN DB
Incomer:-
40A DP MCB, 10kA- 1No
Outgoing: -
32A DP MCB, 10kA- 5 Nos
2.9 | EM LDB 1, 2 ( Refer SLD 5.1 to 5.2) | SET | 2 | 0 | 0
12 way SPN DB
Incomer:-
32A DP RCCB, 30mA- 1No
Outgoing: -
10-16A SP MCB, 10kA- 6Nos
2.1 | AUDI EQUIPMENT DB ( Refer SLD 7.11, 7.12) | SET | 2 | 0 | 0
4 Row 36 Way Flexy DB
Incomer:-
200A FP MCCB - 1Nos
Outgoing: -
40A FP MCB, 10kA- 9 Nos
2.11 | PDB WARE HOUSE | SET | 1 | 0 | 0
8 WAY TPN DB
Incomer:-
63A FP MCB, 10kA- 1Nos
Sub-incomer:-
40A DP RCCB, 100mA- 3Nos
Outgoing: -
16-25A SP MCB, 10kA- 12Nos
2.12 | LDB-1 LOBBY /LD-2 Admin (Refer SLD 15 & 16) | SET | 2 | 0 | 0
12 WAY TPN DB
Incomer:-
63A FP MCB, 10kA- 1Nos
Sub-incomer:-
40A DP RCCB, 30mA- 3Nos
Outgoing: -
6-16A SP MCB, 10kA- 30Nos
2.13 | PDB 1 LOBBY / Signage poster DB (Refer SLD 17 & 18) | SET | 2 | 0 | 0
8 WAY TPN DB
Incomer:-
63A FP MCB, 10kA- 1Nos
Sub-incomer:-
40A DP RCCB, 100mA- 3Nos
Outgoing: -
16-25A SP MCB, 10kA- 18Nos
2.14 | Supply & installation 1-phase, 3 pin Metal clad socket and plug top controlled by 16-25A, DP MCB in a metallic enclosure | No's | 8 | 0 | 0
2.15 | Supply & installation 1-phase, 20-25A 3 pin Metal clad socket and plug top controlled by 20-25A, DP MCB in a polycarbonate enclosure IP-65 weathe proof (For kitchen area) | No's | 6 | 0 | 0
2.16 | Supply & installation 3-phase, 32A 3 pin Metal clad socket and plug top controlled by 32A, FP MCB in a polycarbonate enclosure IP-65 weather proof (For kitchen) | No's | 2 | 0 | 0
2.17 | Supply & installation 3-phase, 32A 3 pin Metal clad socket and plug top controlled by 32A, FP MCB in a metallic enclosure | No's | 5 | 0 | 0
| Total cost of Section 'C' LT Panels & DB's |  |  |  | 0

## Earthing System
PROJECT: MULTIPLEX FOR CINEPOLIS INDIA PVT. LTD
4 SCREEN MULTIPLEX AT K. MALL JODHPUR
BILL OF QUANTITIES FOR ELECTRICAL WORKS
SR. | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
D | EARTHING SYSTEM
1 | Providing & fixing of earth conductor, dressing as per following sizes including its necessary end connections complete. |  |  |  | 0
1.01 | 50 x 6mm GI strip | mtr | 40 | 0 | 0
1.02 | 50 x 3mm Cu. strip | mtr | 0 | 0 | 0
1.03 | 50 x 3mm GI strip | mtr | 0 | 0 | 0
1.04 | 25 x 6mm GI strip | mtr | 0 | 0 | 0
1.05 | 25 x 3mm GI strip | mtr | 60 | 0 | 0
1.06 | 8 S.W.G GI wire | mtr | 300 | 0 | 0
1.07 | 1C x 70 Sqmm Cu. Ar. Cable | mtr's | 0 | 0 | 0
1.08 | 1C x 35 Sqmm Cu.Ar. Cable | mtr's | 140 | 0 | 0
1.09 | 1C x 25 Sqmm Cu.Ar. Cable | mtr's | 0 | 0 | 0
1.1 | 1C x 16 Sqmm Cu. Ar.cable | mtr's | 0 | 0 | 0
1.11 | 1C x 10 Sqmm Cu. Ar.cable | mtr's | 150 | 0 | 0
1.12 | 1C x 95 Sqmm CU Flexible cable | mtr's | 0 | 0 | 0
1.13 | 1C x 16 Sqmm CU Flexible cable | mtr's | 0 | 0 | 0
1.14 | 1C x 10 Sqmm CU Flexible cable | mtr's | 20 | 0 | 0
1.15 | 1C x 6 Sqmm CU flexible wire | mtr's | 80 | 0 | 0
1.16 | 1C x 4 Sqmm CU flexible wire | mtr's | 60 | 0 | 0
2 | Earthing Tap off box with 300 mm long 50 x 6 mm Cu strip with required insulators . | Nos | 6 | 0 | 0
3 | Earth Busbar Box : 300mm x 150mm x 100mm Potential Free Box with required number of earthing bushings and insulation for earth terminals | No's | 8 | 0 | 0
| Total cost of Section 'D' Earthing |  |  |  | 0

## Light Fixtures
PROJECT: MULTIPLEX FOR CINEPOLIS INDIA PVT. LTD
4 SCREEN MULTIPLEX AT K. MALL JODHPUR
BILL OF QUANTITIES FOR ELECTRICAL WORKS
SR. | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
E | INSTALLATION OF LIGHT FIXTURES.
Installation of lighting fixtures is excluded from the scope of this tender.
1 | RECESSED LED PANEL ANKUR XPERTZ ANKUR XRL (592 X 592MM); COLOUR: WHITE LIGHT ; 40W; FINISH: WHITE; 2900 LF, Code in drawing D00955 | Nos | 5 | 0 | 0
2 | TUBE 18W LED 6500K. SUPPLY OF LED TUBE LIGHT; 4FT; WHITE ALUMINIUM ALLOY BODY WITH PMMA COVER; BEAM ANGLE: 120°, C.R.I. >80; LIFE SPAN : 50,000 HRS. Code in drawing D011164 | Nos | 30 | 0 | 0
3 | LED 9W TUBE LIGHT, 6500K, WHITE SHAPE, 2FT (609.6MM), 80LUX. BEAM ANGLE: 170°. IP20. C.R.I.>80. LIFESPAN 50.000H. Code in drawing D008611 | Nos | 8 | 0 | 0
4 | DOWNLIGHT LED FOR AUDI, 2700K, BLACK SHAPE, 6W. IP20. C.R.I.>85. DIAMETER 85MM AND 97MM HEIGHT. LIFESPAN 50.000H. Code in drawing D008615 | Nos | 19 | 0 | 0
5 | Recessed downlight LED, LED make OSRAM/LT 3000K, White aluminium die cast diameter 89 mm Height 55 mm 15 W, Beam angle 360 IP 20, CRI>80 Lifespan 50,000Hrs. code in drawing D009255 | Nos | 13 | 0 | 0
6 | RECESSED DOWNLIGHT LED, LED MAKE: OSRAM/LT, 3000K, WHITE ALUMINUM DIE-CAST, DIAMETER 74mm, HEIGHT 55mm. 7W. BEAM ANGLE: 36°, IP20, C.R.I.>80. LIFESPAN 50.000H., Code in drawing D011140 | Nos | 8 | 0 | 0
7 | LED STRIP, CEILING/WALL MOUNT, 3000°K, COPPER AND PCB, DOT FREE (WITH MILKY PVC COVER). 60 LED/M, 10W/M, IP20, C.R.I.>80. LIFESPAN: 3,000H. (5.4 Meter each length) Code in drawing D011168 | Nos | 5 | 0 | 0
8 | PENDANT LED, 3000K, BLACK EXTRUDED ALUMINIUM SHAPE, 4W, 300LUX. BEAM ANGLE: 24°. IP20. C.R.I.>85. DIMENSIONS: 12000X38MM AND 75MM HEIGHT. LIFESPAN 50.000H. Code in drawing D011141 | Mtrs | 36 | 0 | 0
9 | PENDANT LED, 3000K, BLACK EXTRUDED ALUMINIUM SHAPE, 4W, 300LUX. BEAM ANGLE: 24°. IP20. C.R.I.>85. DIMENSIONS: 12000X38MM AND 75MM HEIGHT. LIFESPAN 50.000H. Code in drawing D011142 | Mtrs | 12 | 0 | 0
10 | RECESSED DOWNLIGHT LED, LED MAKE: OSRAM/LT, 3000K, WHITE ALUMINUM DIE-CAST, DIAMETER 56mm, HEIGHT 38mm. 3W. BEAM ANGLE: 36°, IP20, C.R.I.>80. LIFESPAN 50.000H. Code in drawing D011143 | Mtrs | 10 | 0 | 0
11 | LED STRIP, CEILING/WALL MOUNT, 4000°K, COPPER AND PCB, DOT FREE (WITH MILKY PVC COVER). 60 LED/M, 10W/M, IP20, C.R.I.>80. LIFESPAN: 3,000H. Code in drawing D0118614 | Mtrs | 18 | 0 | 0
12 | EMERGENCY LIGHT WITH EXIT TEXT, WALL MOUNTED, LED MAKE OSRAM/LT, 6500K, MS BODY WHITE/BLACK, 6W. BEAM ANGLE: 120°, IP20, C.R.I. >85. LIFE SPAN: 50,000. FIXTURE DIMENSION: LENGTH 300mm, HEIGHT 272mm, WIDTH 10mm Code in drawing D009971 Exit Signage | Nos | 6 | 0 | 0
13 | EMERGENCY LIGHT WITHOUT EXIT TEXT, WALL MOUNTED, LED MAKE OSRAM/LT, 6500K, MS BODY WHITE/BLACK, 6W. BEAM ANGLE: 120°, IP20, C.R.I. >85. LIFE SPAN: 50,000. FIXTURE DIMENSION: LENGTH 300mm, HEIGHT 272mm, WIDTH 10mm | Nos | 6 | 0 | 0
14 | LED TUBE LIGHT 900MM LONG TO ILLUMINATE CONCESSIONS' BACK WALL. TO BE DEFINED. Code in drawing LT 26 |  | 6 | 0 | 0
15 | Maintenance 1X28 W LED luminary | Nos | 65 | 0 | 0
16 | MAINTENANCE AUDI LIGHT: FLOODLIGHT WITH U-CLAMP; 30W; BLACK IN COLOUR; COLOR TEMPERATURE: 3000K; LIFE SPAN: 50,000 HRS ; LUMINOUS EFFICACY 120LM/W. ALL COMPONENT LIKE CONTROL GEAR, STEP DOWN TRANSFORMERS, ETC., INTERNAL WIRING BETWEEN ACCESSORIES Code in drg : D000 865 | Nos | 24 | 0 | 0
| Total cost of Section 'E' Lighting fixtures |  |  |  | 0

## Data & Voice
PROJECT: MULTIPLEX FOR CINEPOLIS INDIA PVT. LTD
4 SCREEN MULTIPLEX AT K. MALL JODHPUR
BILL OF QUANTITIES FOR ELECTRICAL WORKS
SR. | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
F | COMMUNICATION DATA AND VOICE
1 | 20 pair jelly filled Armoured Cu telephone cable | mtr | 100 | 0 | 0
2 | TAG Box suitable for 50pair armoured cu tel cable with crown | No's | 1 | 0 | 0
3 | TAG Box suitable for 20pair armoured cu tel cable with crown | Sets | 2 | 0 | 0
4 | Supply and wiring for telephone system using 2 pair telephone cable in existing conduit. | mtr | 90 | 0 | 0
5 | Supply and installation of CAT 6A cable in existing conduit | mtr | 5025 | 0 | 0
5 | Supply and installation of CAT 6 S/FTP cable in existing conduit | Mtrs | 480 | 0 | 0
6 | Supply and installation of CAT 7 ( TMS to each proj Rm ) cable in existing conduit | mtr | 380 | 0 | 0
7 | Supply, laying, testing and commissioning of 12 Core Single Mode Optical Fibre Cable, conforming to ITU-T G.652D / G.657A1 standard, comprising colour-coded fibres housed in a loose tube / tight buffered construction, with FR / LSZH outer sheath suitable for indoor installation. | Mtrs | 165 | 0 | 0
8 | Supply, installation, testing and commissioning of High-Speed HDMI Cable, compliant with HDMI 2.0 / 2.1 standards, capable of supporting Full HD / 4K / 8K video resolution, HDR, Ethernet and Audio Return Channel (ARC/eARC) as applicable. Cable shall be factory-terminated with gold-plated HDMI Type-A connectors at both ends, with high-quality copper conductors, multi-layer shielding for EMI protection, and durable PVC / LSZH outer jacket. (Considering length 5 Mtrs) | Mtrs | 5 | 0 | 0
9 | Supply and installation of RG 6 cable in existing conduit | mtr | 4 | 0 | 0
10 | Supply, installation, testing and commissioning of clip on telephone type outlet mounted on a GI outlet box with front plate and all necessary accessories complete as required including the termination of wires.(RJ11) | No's | 4 | 0 | 0
11 | Supply, installation, testing and commissioning of clip on Data outlet mounted on a GI outlet box with front plate and all necessary accessories complete as required including the termination of wires.(RJ45) | No's | 95 | 0 | 0
12 | Supply and ,installation of Novar/ Steelways make floor mounted Ega box 250 mm by 250 mm for housing 2Nos 6A socket with 1Nos 6A switch on UPS and 1Nos 6A socket with 1Nos 6A switch on Raw power and 2Nos data/voice boxes complete as required. ( For QR code scanner) | No's | 1 | 0 | 0
13 | Supply and ,installation of Novar/ Steelways make floor mounted Ega box 100 mm by 100 mm for housing 6/16A switch and socket complete as required. (For DFMD) | No's | 1 | 0 | 0
| Total cost of Section 'F' Communication, Data & Voice |  |  |  | 0

## Audi Speaker System Wiring
PROJECT: MULTIPLEX FOR CINEPOLIS INDIA PVT. LTD
4 SCREEN MULTIPLEX AT K. MALL JODHPUR
BILL OF QUANTITIES FOR ELECTRICAL WORKS
SR. | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
G | AUDI SPEAKER SYSTEM WIRING
Audi speaker wiring in medium gauge PVC conduit
3.1 | Supply and installation of following sizes of FRLS Medium gauge PVC conduit recess /Surface in Floor/ wall including all accessories, GI fish wire, fixing hardware etc. including chasing the wall / floor and plastering the chased portion and making the good the damages etc. complete as required for PA & Music system wiring as required.
a | Medium gauge PVC conduit 20 mm dia | Mtr | 1500 | 0 | 0
b | Medium gauge PVC conduit 25 mm dia | Mtr | 750 | 0 | 0
c | Medium gauge PVC conduit 32 mm dia | Mtr | RO | 0
d | Medium gauge PVC conduit 40 mm dia | Mtr | RO | 0
e | Medium gauge PVC conduit 50 mm dia | Mtr | RO | 0
f | Medium gauge PVC conduit 65 mm dia | Mtr | RO | 0
3.2 | Supply, installation, testing & commissioning of audi speaker wiring using 2 Nos. 4 Sq.mm multistranded flexible FRLS PVC wire in already laid FRLS medium guage PVC conduit with accessories for auditorium speakers laying on surface / concealed as required. | Mtr | 12100 | 0 | 0
3.3 | Supply, installation, testing & commissioning of audi speaker wiring using 2 Nos. 6 Sq.mm multistranded flexible FRLS PVC wire in already laid FRLS medium guage PVC conduit with accessories for auditorium speakers laying on surface / concealed as required. | Mtr | 4378 | 0 | 0
| TOTAL OF AUDI SPEAKER SYSTEM |  |  |  | 0

## Temporary Work
PROJECT: MULTIPLEX FOR CINEPOLIS INDIA PVT. LTD
4 SCREEN MULTIPLEX AT K. MALL JODHPUR
BILL OF QUANTITIES FOR ELECTRICAL WORKS
SR. | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
H | Temporary Electrical Works
11 | Providing temporary construction lighting and power for the Floors including Project Managers office area by using required 20nos. 1 x 20 Watt LED fixtures with cover (minimum 250 Lux), required flexible double insulated FRLS copper wiring, distribution board, minimum 25 nos. 40 W LED flood light , earthing, throught the duration of the project. It will be the responsibility of Electrical Contractor to distribute power to all the contractors working at site. The rates shall be all inclusive. (All item mentioned above, shall be new and of good quality by considering site safety parameter.Old and repaired item shall never be allowed to used at site.) Wall chipping for utility sockets, safety glasses for UPS and Battery room, Hand gloves 1100V grade for electrical rooms, shall also be included. | LS | 1 | 0 | 0
| Total cost of Section 'G' Safety & Miscilanious |  |  |  | 0

## LV Summary
SECTION | Description | Amount
A | CCTV | 0
B | Public Addressal System | 0
C | Access Control | 0
| Total | 0

## CCTV
PROJECT : CINEPOLIS INDIA PVT LTD, K-MALL, JODHPUR
BILL OF QUANTITIES FOR CCTV SYSTEM |  |  |  | R0 - 06.11.2025
SR. NO. | SHORT TEXT (Character limit 40 only) | UNIT | Qty | RATE | AMOUNT (Rs.)
A | IP CCTV
Supply, Installation, Testing & Commissioning of Network (IP) Based CCTV Surveillance System comprising of following:
1 | IP Fixed Dome camera
| IP Fixed Dome camera with 1/3" CCD/CMOS, Progressive/De-interlace, Very High Definition resolution (1920 x 1080), min. Dual streaming, 25 FPS, H.264 / JMPEG compression support, 2.8 mm fixed focal lens, 0 lux with IR, Tamper detection, Wide dynamic Range, PoE power input, IP 43, as per detailed specifications. | EA | 33 | 0 | 0
2 | IP Fixed Dome camera (with audio recording)
| IP Fixed Dome camera (in-buit microphone) with 1/3" CCD/CMOS, Progressive/De-interlace, Very High Definition resolution (1920 x 1080), min. Dual streaming, 25 FPS, H.264 / JMPEG compression support, 2.8 mm fixed focal lens, 0 lux with IR, Tamper detection, Wide dynamic Range, PoE power input, IP 43, as per detailed specifications. | EA | 4 | 0 | 0
3 | Outdoor type IP Bullet camera
| Outdoor type IP Bullet camera with 1/2.8" CMOS, Progressive Scan, Day/Night, 2.8 mm - 12 mm motorised zoom lens, Support H.264 & MJPEG, 25/30 FPS @ 1080p (1920×1080), Smart Detection - Tripwire detection, Intrusion detection, Abandoned/Missing Object detection, Scene Change detection, Audio Detection, Face Detection, Support Corridor Mode, Digital WDR, Day/Night (ICR), 3D DNR, AWB, AGC, BLC, Multiple network monitoring: Web viewer, CMS & Mobile App, 1/1 Alarm in/out, 1/1 audio in/out, 30 Mtr IR Range, Micro SD memory support upto 128 GB, Support ONVIF, PSIA, CGI, IP67, PoE as per detailed specifications. | EA | 6 | 0 | 0
4.1 | 64 Ch Smart Network Video Recorder
| Smart Network Video Recorder: 64 channel IP camera license enabled input, H.264/MJPEG dual codec decoding, 320 Mbps incoming bandwidth, 4k/HDMI/VGA/TV support video output, 8/16 channel synchronous realtime preview, GRID interface, Two-way Talk, Support up to 12 Megapixel Recording, Support Multi-brand network cameras, ONVIF Version conformance, 16/4 Alarm i/o, Including 8 SATA HDDs suitable for 30 days backup, Support 1 eSATA port, 2 USB 2.0, 2 RJ-45 ports (10/ 100/ 1000 Mbps), 1 RS 485 Port, 1 RS 232 Port, Multiple network monitoring: Web viewer, CMS & Mobile App, support ANPR camera, as per detailed specifications | EA | 0 | 0 | 0
4.2 | 32 Channel Smart NVR
| 32 channel IP camera license enabled input & (SAME AS ABOVE) | EA | 1 | 0 | 0
4.3 | 16 Channel Smart NVR
| 16 channel IP camera license enabled input & (SAME AS ABOVE) | EA | 1 | 0 | 0
4.4 | 12 Channel Smart NVR
| (SAME AS ABOVE) | EA | RO
5 | 32" colour, HD monitor
| 32" colour, Flat Screen Type Professional CCTV Surveillance HD monitor 100-230 VAC 50 Hz, 24x7 with wall mounted swivel stand | EA | 1 | 0 | 0
6 | SURVILLANCE HARD DISC
| SURVILLANCE HARD DISC SUITABLE FOR 30 DAYS BACKUP (min 4 TB) (1+1) | EA | 2 | 0 | 0
7.1 | POE Switch 24 port
| Independent LAN for IP CCTV System: 24 port layer 2 switch with 10/100/1000 POE Web Semi-Managed Switches, mounted in 4 U Rack and with 2 combo SFP ports and all related termination accessories as per site specific System requirement. (Rack price also to be included) | EA | 2 | 0 | 0
7.2 | 16 port
| 16 Port layer 2 switch (SAME AS ABOVE) | EA | 0
8 | Cat-6 cable
| Cat-6 cable with required terminations as required with Cable tie's including PVC conduit & accessories | M | 3500 | 0 | 0
9 | Additional Item
| Any additional items required to complete fully functional system to meet detailed specifications. | EA | RO
| TOTAL OF IP CCTV |  |  |  | 0

## PA
PROJECT: MULTIPLEX FOR CINEPOLIS INDIA PVT. LTD
REFURBISHMENT OF 4 SCREEN MULTIPLEX AT P&M MALL PATNA | 4 SCREEN MULTIPLEX AT K. MALL JODHPUR
BILL OF QUANTITIES FOR PUBLIC ADDRESS SYSTEM WORK
SR. | Description | UNIT | QTY | RATE | AMOUNT
B | MUSIC AND PUBLIC ADDRESS SYSTEM
1 | 5 Zone Call Station with goose neck Microphone with zone selection & all call selection to be connected peer to peer with the network controller |  | 1 | 0 | 0
2 | Supply, installation, Testing, & commissioning of the Message Tone genetaror for pre-recorded message.Shall be an EN54-16 certified user interface. |  | 1 | 0 | 0
3 | Network controller + Amplifire - 5 zone with following features 1. Microcontroller based with builtin 240 Watt Amplifier 2. Accomodates 5 set of zones 3. Accomadates 5 Zone Call stations peer to peer 4. Automated Evacuation message facility |  | 1 | 0 | 0
3 | Rack for mounting the entire system. (All above components of the system to be rack mountable. | Set | 1 | 0 | 0
4 | SPEAKERS
3.1 | Supply, installation, testing & commissioning of 15 to 30W ceiling mounted speakers complete. | Nos | RO | 0
3.2 | Supply, installation, testing & commissioning of 15 to 30W wall mounted speakers complete. | Nos | RO | 0
3.3 | Supply, installation, testing & commissioning of 6 W RMS 4 Ohms full range PA speakers on bracket, false ceiling etc. with dual cone woofer 20 W peak Output, 100 Hz to 15KHz frequency with Line matching transformer for 95 dBA sound output. | Nos | 50 | 0 | 0
3.4 | Supply, installation, testing & commissioning of 10 W RMS 4 Ohms full range Horn type PA speakers on bracket, false ceiling etc. with dual cone woofer 10 W peak Output, 100 Hz to 15KHz frequency with Line matching transformer for 95 dBA sound output. | Nos | 8 | 0 | 0
5 | Supply, laying, testing & commissioning of cable for music system with 40/36 twin parallel FR PVC sheathed armoured Cable of approved make. End termination of FR cable with SIBG gland and required accesories. All complete as required and as per final direction & approval of the consultant | Mtr | 1900 | 0 | 0
| TOTAL OF PUBLIC ADDRESS SYSTEM |  |  |  | 0

## Access control
PROJECT: MULTIPLEX FOR CINEPOLIS INDIA PVT. LTD
REFURBISHMENT OF 4 SCREEN MULTIPLEX AT K. MALL JODHPUR
BILL OF QUANTITIES FOR ACCESS CONTROL SYSTEM WORKS
SR | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
C | ACCESS CONTROL SYSTEM
1 | Supply, installation, testing and commissioning of standalone Access Control System C3-400B 4 door multidoor access controller for supporting Proximity Card or a Biometric readers. System should be capable of handling Card / Biometric data with power supply as spec`s below | Set | 1 | 0 | 0
Multiple card / Biometric reading technologies supported, Inbuilt database backup to facilitate offline use Automatic locking & unlocking of the doors based on Fire Signal, System should support max 4 nos doors having Card cum Biometric readers located at different location System should be compatible for integrate with Clients Enterprise version (if required)
2 | Supply, Installation, Testing and Commissioning of Smart Card Reader (KR500E) with read range of 3" | Nos | 6 | 0 | 0
3 | Supply, Installation, Testing and Commissioning of normal exit & Emergency Release push button switch Polycarbonate housing. | Nos | 6 | 0 | 0
4 | Supply, Installation, Testing and Commissioning of Electromagnetic lock-600 lb holding force | Nos | 6 | 0 | 0
5 | Supply, Installation, Testing and Commissioning of Electromagneitc Lock with built in Magnetic contacts Single leaf Doors. 600 lbs capacity - L bracket as required (EM 600-LED ) | Nos | 6 | 0 | 0
6 | Supply, Installation, Testing and Commissioning of Electromagneitc Lock with builtin Magnetic contacts double leaf Doors. 600 lbs capacity - U bracket as required (EM 600-LED ) | Nos | 6 | 0 | 0
7 | Supply, Installation, Testing and Commissioning of Egress Switch | Nos | 6 | 0 | 0
8 | Supply, Installation, Testing and Commissioning of Proximity cards (PVC) | Nos | 20 | 0 | 0
9 | Supply, Installation, Testing and Commissioning of Proximity key fobs | Nos | 4 | 0 | 0
10 | Supply, Installation, Testing and Commissioning of Access Control Enterprise version Server Software + Access Control Enterprise version Client License loaded on Client machines | Set | 1 | 0 | 0
11 | Supply, Installation, Testing and Commissioning of following communication & power cables in the conduit/ LV receway.
11A | Communication cables
11.1 | Cat 6 | RMT | RO | 0
11.2 | Cat 6A | RMT | 50 | 0 | 0
11.3 | Cat 7 | RMT |  | 0
11B | Power cables
11.4 | 8 C X 18 AWG Shielded cable | RMT | 40 | 0 | 0
11.5 | 4c x 18 AWG Shielded cable | RMT | 300 | 0 | 0
11.6 | 4c x 24 AWG Shielded cable | RMT | 250 | 0 | 0
12 | Supply, Installation, Testing and Commissioning of Medium Grade - 25 mm FRPVC Conduit with fittings and accessories ISI Marked with GI saddle & spacers at every 0.3 Mtr and flexible conduits for all drops above false ceiling. | Mtrs | 60 | 0 | 0
13 | Supply, Installation, Testing and Commissioning of Fully closed GI Powder coated trunking of 16 Gauge with GI supports at every 3 mtrs, and Aluminum Junction Boxes @ every 6 mtr
13.1 | 50 x 50 mm | Mtrs | 45 | 0 | 0
13.2 | 63 x 38 mm | Mtrs | RO | 0
13.3 | 83 x 38 mm | Mtrs | RO | 0
13.4 | 100 x 40 mm | Mtrs | RO | 0
14 | Supply, Installation, Testing and Commissioning of Piezo sounders for Fire Exits | Nos | 2 | 0 | 0
15 | Supply, Installation, Testing and Commissioning of fingerprint Biometric cum card Reader, with Power + Control kit. | Nos | RO | 0 | 0
| TOTAL COST OF ACCESS CONTROL SYSTEM |  |  |  | 0
01 | The UPS power supply will be available near to the system.
02 | Vendor to quote seperatly if any item required to function the system.