## FIRE - SUMMARY
Project | : BLR 6A L2 & L1 COWRKS
Client | : COWRKS
Architects
Consultants | : E Sollutions Consultancy Pvt Ltd
Subject | : BOQ Summary
Date / Rev No | : 10.03.2026 / R1
SL.NO. | DESCRIPTION | AMOUNT IN INR |  |  | REMARKS
|  | SUPPLY | INSTALLATION | TOTAL
A | ADDRESSABLE FIRE ALARM SYSTEM | 113285 | 19150 | 132435
B | PUBLIC ADDRESS SYSTEM | 26250 | 7750 | 34000
C | SPRINKLER SYSTEM | 374528 | 177596 | 552124
D | FIRE EXIT SIGNAGE SYSTEM-LED Battery Back up | 9600 | 2300 | 11900
| Total | 523663 | 206796 | 730459

## FA
Project | : BLR 6A L2 & L1 COWRKS
Client | : COWRKS
Architects
Consultants | : E Sollutions Consultancy Pvt Ltd
Subject | : FPS Priced BOQ
Date / R. No | : 10.03.2026 / R1
SL. NO. | DESCRIPTION | UNIT | QUANTITY |  |  | RATE IN INR |  |  | AMOUNT IN INR
|  |  | L1 | L2 | TOTAL | SUPPLY | INSTALLATION | TOTAL | SUPPLY | INSTALLATION | TOTAL
A | Supply Installation Testing & Commissioning of ADDRESSABLE FIRE ALARM SYSTEM
1 | Supply Installation Testing & Commissioning of Multi Sensor detector (photo+heat) with base,powder coated back box and other accessories as required and Detectors shall be UL listed 268 7th edition - Above False Ceiling, Below False Floor and True Ceiling | Nos | 5 | 5 | 10 | 3205 | 300 | 3505 | 32050 | 3000 | 35050 | *Quoted EST
2 | Supply Installation Testing & Commissioning of Multisensor detector (photo+heat) with base,powder coated back box and other accessories as required and Detectors shall be UL listed 268 7th edition - Below False Ceiling | Nos |  |  | 0 |  |  | 0 | 0 | 0 | 0
3 | Supply Installation Testing and Commissioning of Response indicator for all detectors located above false ceiling and below false flooring. | Nos |  |  | 0 |  |  | 0 | 0 | 0 | 0
4 | Supply Installation Testing & Commissioning of Analogue Addressable Fault isolator module capable of monitoring shorted loop circuit and automatically restore communications when shorted conditions are corrected. (FIM's are used for every 20 detectors/devices). MS powder coated backbox and other accessories as required | Nos | 1 |  | 1 | 2815 | 300 | 3115 | 2815 | 300 | 3115
5 | Supply Installation Testing & Commissioning of Analogue Addressable Monitor module operating at 24V DC, 2A, rated at 230V, provided with SPDT contact. MS powder coated backbox and other accessories as required BB# POWER SUPPLY UNIT # WLD # RRS # FC# BFV# EVC# HSSD # GSS# SPARE# | Nos | 3 |  | 3 | 2815 | 300 | 3115 | 8445 | 900 | 9345
6 | Supply Installation Testing & Commissioning of Analogue Addressable Control module operating at 24V DC, 2A, rated at 230V, provided with SPDT contact.MS powder coated backbox and other accessories as required HOOTER# 1 SPARE#1 | Nos | 2 |  | 2 | 2815 | 300 | 3115 | 5630 | 600 | 6230
7 | Analogue Addressable Control relay module operating at 24V DC, 2A, rated at 230V, provided with SPDT contact. MS powder coated backbox and other accessories as required BB# Electrical Panel # AHU # ACS # PA # HSSD# GSS# Spare# | Nos | 3 |  | 3 | 2815 | 300 | 3115 | 8445 | 900 | 9345
8 | Addressable type Manual dual action (Push IN-Pull DOWN) Flush or surface mounted Manual Call Point in manufacturers prescribed matching red enamel outlet box complete with key operated test-reset lock. The word FIRE shall appear in front of station as per technical specifications. UL listed . | Nos | 1 | 1 | 2 | 3780 | 300 | 4080 | 7560 | 600 | 8160
9 | Addressable type fully solid state circuitory dual tone Electronic type Hooters Cum Strobe at 85 dBA @ 3m for Audible annunciation and 75cd flashing at 1 Hz for visual indication with required control module & power supply accessories as per specifications. UL listed . | Nos | 1 | 1 | 2 | 5795 | 300 | 6095 | 11590 | 600 | 12190
10 | 2C x 1.5 mm2, Stranded Annealed Bare Copper conductor,Type A ST1 PVC insulated,Armoured FRLS CU Cable 1100 V, with GI saddle spacers every 0.3 mtr with Single compression Cable Glands (metal) ,ABS Junction Boxes (wherever required), terminals,Ferruling complete. | Rmt | 175 | 175 | 350 | 105 | 35 | 140 | 36750 | 12250 | 49000
11 | Removing of exisiting Detectors from the existing location and refixing the same on the proposed/same location including Modification & alignment in existing cable based on site condition .Necessary costing for removing, refixing to be included in quote. (vendor is responsible for safe handling of detectors, if any damage occurs during removing , same shall be procured by vendor and install without extra cost) | Lot | 1 | 1 | 2 |  |  | 0 | 0 | 0 | 0 | *Details Required
| TOTAL | [7 empty] | 113285 | 19150 | 132435
| Total Detectors per Floor |  |  | #REF! | 1645
1645/112
| 112 Nos 90% Loading as per Edwards Loop capacity |  |  | 1 | 1

## PA
Project | : BLR 6A L2 & L1 COWRKS
Client | : COWRKS
Architects
Consultants | : E Sollutions Consultancy Pvt Ltd
Subject | : FPS Priced BOQ
Date / R. No | : 10.03.2026 / R1
SL. NO. | DESCRIPTION | UNIT | QUANTITY |  |  | RATE IN INR |  |  | AMOUNT IN INR
|  |  | L1 | L2 | TOTAL | SUPPLY | INSTALLATION | TOTAL | SUPPLY | INSTALLATION | TOTAL
B | SITC OF PUBLIC ADDRESS SYSTEM
1 | SITC of 6W RMS False Ceiling Mount Speakers with inbuilt 100V Line Matching Transformer, wide opening angle, optimized for music & speech applications with mounting clamps as per specifications or equivalent as per OEM. Tapping shall be done at 3W - Max Power: 8W,Rated Power: 6Watts, Power Tapping: 6/3/1.5W - Effective frequency range(-10 dB) : 150 Hz to 15KHz - SPL at rated power (1Khz at 1 m) 88 dB - Opening Angle 1 KHz / 4 KHz (-6 dB): 180/45 Note: Color of speaker should be finalised with architect / clinet before procurement. | Nos |  |  | 0 |  |  | 0 | 0 | 0 | 0
2 | SITC of 6W RMS True Ceiling Mount Speakers , Back Box ,with inbuilt 100V Line Matching Transformer, wide opening angle, optimized for music & speech applications with powder coated back box, supports as per specifications or equivalent as per OEM. Tapping shall be done at 3W - Max Power: 8W,Rated Power: 6Watts, Power Tapping: 6/3/1.5W - Effective frequency range(-10 dB) : 150 Hz to 15KHz - SPL at rated power (1Khz at 1 m) 108 dB - Opening Angle 1 KHz / 4 KHz (-6 dB): 180/45 Note: Color of speaker should be finalised with architect / clinet before procurement. | Nos | 5 | 5 | 10 | 1050 | 250 | 1300 | 10500 | 2500 | 13000
3 | 2C x 1.5 mm2, Stranded Copper conductor,Type A ST1 PVC insulated,Armoured FRLS Cable 650 V as per IS 1554, with GI saddle spacers every 0.3 mtr with Single compression Cable Glands,ABS Junction Boxes (wherever required), terminals,Ferruling complete. | Rmt. | 75 | 75 | 150 | 105 | 35 | 140 | 15750 | 5250 | 21000
4 | Removing of exisiting Speakerrs from the existing location and refixing the same on the proposed/same location including Modification & alignment in existing cable based on site condition .Necessary costing for removing, refixing to be included in quote. (vendor is responsible for safe handling of detectors, if any damage occurs during removing, same shall be procured by vendor and install without extra cost) | Lot | 1 | 1 | 2 |  |  | 0 | 0 | 0 | 0 | *Details Required
| TOTAL | [7 empty] | 26250 | 7750 | 34000

## FPS
Project | : BLR 6A L2 & L1 COWRKS
Client | : COWRKS
Architects
Consultants | : E Sollutions Consultancy Pvt Ltd
Subject | : FPS Priced BOQ
Date / R. No | : 10.03.2026 / R1
SL. NO. | DESCRIPTION | UNIT | QUANTITY |  |  | RATE IN INR |  |  | AMOUNT IN INR
|  |  | L1 | L2 | TOTAL | SUPPLY | INSTALLATION | TOTAL | SUPPLY | INSTALLATION | TOTAL
C | SITC of Sprinkler system Note : (vendor is responsible for safe handling of detectors, if any damage occurs during removing, same shall be procured by vendor and install without extra cost)
1 | Supply, Installation, Testing & Commissioning of GI Pipes, C class, ERW, Heavy grade conforming to IS: 1239 for pipes from 25 mm to 150mm dia. complete with fittings, supports, miscellaneous and consumables and Painting of pipes/valves with one coat of metal primer and two coat of fire red enamel paint of approved quality with DI Threaded Fittings and Buttwelded fittings. All the branching should be done with proper Tee fitting. No gas cutting allowed. Pipe to be painted with Red oxide primer (MS ) / Zinc chromate primer(GI) over that 2 coats synthetic red enamel paint as per Fire authorities requirement over all pipes and also inclusive of making hole in the wall, chasing, chipping, making good with plastering after completion of work, pipe sleeve of suitable higher size, sealing the sleeves with glass wool in between & fire sealant, etc. Cost of Steel supports for piping (like angles, channels, clamps, tie rods, brackets, nuts and bolts as per the standard shall also be included in the quoted rate. All pipes 80 mm dia & above should be supported by MS angle (Size 50x50x6mm) sections only
a | 25mm nominal dia | Rmt | 130 | 130 | 260 | 594 | 144 | 738 | 154440 | 37440 | 191880
b | 32mm nominal dia | Rmt | 70 | 65 | 135 | 756 | 180 | 936 | 102060 | 24300 | 126360
c | 40mm nominal dia | Rmt | 25 | 23 | 48 | 867 | 192 | 1059 | 41616 | 9216 | 50832
d | 50mm nominal dia | Rmt | 27 | 24 | 51 | 1212 | 240 | 1452 | 61812 | 12240 | 74052
e | 65mm nominal dia | Rmt |  |  | 0 |  |  | 0 | 0 | 0 | 0
f | 80mm nominal dia | Rmt |  |  | 0 |  |  | 0 | 0 | 0 | 0
g | 100mm nominal dia | Rmt |  |  | 0 |  |  | 0 | 0 | 0 | 0
h | 150mm nominal dia | Rmt |  |  | 0 |  |  | 0 | 0 | 0 | 0
2 | Supply testing and commissioning of 15 mm gunmetal/chrome quartzoid bulb, Std. response (Blub-5mm thick) sprinkler heads suitable for 68 deg. C, K-5.6(80lpm) ,Sprinklers shall be UL Listed / FM Approved. |  |  |  | 0
| a) Concealed Pendent with cover (color of cover plate as per architect choice) - 68deg C | Nos |  |  | 0 |  |  | 0 | 0 | 0 | 0
| b) Pendent - 68deg C @ BFC | Nos |  |  | 0 |  |  | 0 | 0 | 0 | 0
| c) Pendent Sprinkler | Nos | 10 | 10 | 20 | 650 | 200 | 850 | 13000 | 4000 | 17000
| d) Upright - 68deg C@ AFC (builder sprinkler areas) | Nos |  |  | 0 |  |  | 0 | 0 | 0 | 0
| e) sidewall sprinkler - 68deg C@ facade glass location | Nos |  |  | 0 |  |  | 0 | 0 | 0 | 0
| f) Dry bulb sprinkler with shaft size varying from 0.1 to 1.1m, with necessary accessories to install the same | Nos |  |  | 0 |  |  | 0 | 0 | 0 | 0
3 | Supply & fixing of approved type rosette plates ( Recessed type, in two piece) for Sprinklers below false ceiling area. |  |  |  | 0
| The Rosette shall be fabricated by M.S. plate of 2mm thick and the finish shall be powder coated and color shall be as approved by architects / clients. | Nos | 10 | 10 | 20 | 80 | 20 | 100 | 1600 | 400 | 2000
4 | Stainless steel corrugated flexible pipe(hose) for dropping sprinklers below false ceiling, pipe shall be UL Listed / FM Approved, 16 bar pressure rating and 1500 mm long 25 mm dia with union / reducer collar, clamps etc. as required. (BRAIDED) - To be connected to existing sprinkler network with required fittings/accessories | Nos |  |  | 0 |  |  | 0 | 0 | 0 | 0
5 | Stainless steel corrugated flexible pipe(hose) for dropping sprinklers below false ceiling, pipe shall be UL Listed/ FM Approved, 16 bar pressure rating and 1000 mm long 25 mm dia with union / reducer collar, clamps etc. as required.(BRAIDED) - To be connected to existing sprinkler network with required fittings/accessories | Nos |  |  | 0 |  |  | 0 | 0 | 0 | 0
6 | MODIFICATION OF BUILDER SPRINKLER PIPES-SIZES 25 NB TO 150 NB AT VARIOUS LOCATIONS-REMOVAL,RE-ROUTING, PAINTING WITH REQUIRED SUPPORTS, FITTINGS. DUMMY,BR.PIPE REROUTING WHEREEVER CLASHED WITH HVAC DUCTS, TRAYS OR ACHIEVING THE FALSE CEILING HEIGHTS | Lot | 1 | 1 | 2 |  | 15000 | 15000 | 0 | 30000 | 30000
7 | MODIFICATION OF BUILDER SPRINKLER BULBS AT VARIOUS LOCATIONS-REMOVAL,RE-REFIXING | Lot | 1 | 1 | 2 |  | 5000 | 5000 | 0 | 10000 | 10000
8 | Hydro Testing & commissioning of sprinkler system 24hr at 15 bar pressure for both existing and new pipes. As fitout scope is adding the sprinkler with Flexible drop in the Existing Sprinkler pipe networks.To ensure the no leakage on the hook up portion of the sprinkler system, hydrotest to be done. | Nos | 1 | 1 | 2 |  | 25000 | 25000 | 0 | 50000 | 50000
| TOTAL | [7 empty] | 374528 | 177596 | 552124

## LED BATTERY SIGNAGE
Project | : BLR 6A L2 & L1 COWRKS
Client | : COWRKS
Architects
Consultants | : E Sollutions Consultancy Pvt Ltd
Subject | : FPS Priced BOQ
Date / R. No | : 10.03.2026 / R1
SL. NO. | DESCRIPTION | UNIT | QUANTITY |  |  | RATE IN INR |  |  | AMOUNT IN INR
|  |  | L1 | L2 | TOTAL | SUPPLY | INSTALLATION | TOTAL | SUPPLY | INSTALLATION | TOTAL
D | SITC OF FIRE SIGNAGES Note : (vendor is responsible for safe handling of detectors, if any damage occurs during removing, same shall be procured by vendor and install without extra cost)
SITC of LED Configured Emergency Exit SIGNAGE system 1. Recessed/Surface/Suspendend Mounting Type (based on mockup approval) 2. LED light with Rechargeable battery backup of 120 minutes 3. Continously provides illumination through mains power supply 4. Suitable for different types of exit Facia 5. As per IS 9583-1981 6.Photoluminescent & maintained type 7.Suitable for 230v, 50Hz 8. Reference model Prolite PEL LED E/M(s)
1 | "DIRECTIONAL EMERGENCY EXIT " Battery Backed signage - with suspension chains . Double SIDE - 180*300mm The signages shall be fixed to the ceiling with the help of chain and dropped below false ceiling | Nos | 2 | 2 | 4 | 2400 | 400 | 2800 | 9600 | 1600 | 11200
2 | Removing and Refixing of Directional emergency Exit Battery Powered 2 Hrs Backup And Relocation of existing Extinguishers | Lot | 1 | 1 | 2 |  | 350 | 350 | 0 | 700 | 700
| TOTAL | [7 empty] | 9600 | 2300 | 11900