## General Notes
GENERAL NOTES - ITEMS OF WORK UNDER BILLS OF QUANTITIES FOR CIVIL INTERIOR AND ALLIED WORKS
Site is at 9th Floor level
The rates are inclusive of supply and installation, all fright, insurance, transportation, loading & unloading charges with respective floors, stacking, security, local delivery, clearance charges, rectification of defects or replacement of defective material. this material shall be delivered and installed at site in all respects without any further additional charges. No hidden charges shall be accepted.
A | These notes shall apply to other Bills in these documents.
B | The works under this Bills of Quantities shall be priced based on remeasurable quantities.
C | This Bill shall be read in conjunction with the General Conditions and Preliminaries, Specification of Materials and Workmanship, Drawings and all other Bills of Quantities contained in these documents which shall be construed as being complementary to one another
D | The Contractor shall provide and do everything reasonably necessary for the proper execution of the Works according to the true intent and meaning of the Drawings, the Specification and the Documents forming part of the Contract taken together the same as may or may not be particularly shown or described, provided that the same is reasonable to be inferred there from. If the Contractor should find any discrepancy in the Drawings or between the Drawings and the Specification or any other Documents forming part of the Contract, he shall immediately refer the same to the Employer's representative who shall decide which shall be followed.
E | The rates and prices herein shall be inclusive of all Works, materials and expenditure, whether separately or specifically mentioned or described in the Contract Documents or not, which are either indispensably necessary to carry out and bring to completion the works described in or to be inferred from the Contract documents taken as a whole or which may contingently become necessary to overcome difficulties and bring the said works so described or inferred to satisfactory completion.
F | For the purpose of valuation of variations, any omission or additions to the Contract Sum shall be based on measured quantities, applying the relevant unit rates (or pro-rated unit rate, as the case may be) found in the Bills of Quantities. As such, the Contractor is advised to price each item contained in the Bills in a fair and realistic manner.
G | Unless otherwise specifically stated in the Bills, the following shall be deemed to include with all items: -
(a) Labour and all costs in connection therewith
(b) Material and goods including materials required for lapping, jointing and the like and all costs in connection therewith such as materials conveyance and delivery
(c) Unloading, storing, returning packing, handling, hoisting and lowering materials
(d) Assembling, setting, fitting and fixing materials in position and all costs in connection therewith; such as handling waste and cutting waste
(e) Use of plant, tools and equipment and all cost in connection therewith
(f) All necessary protection, temporary staging, shoring, scaffolding, screens etc and other temporary work required in connection therewith
(g) Executing the whole of the Works in confined spaces as and when directed by the Employer's representative
(h) All necessary protection of Contractor's works against damage and making good of all works disturbed in connection therewith
(i) Removing all debris from site compliance to the LEED's requirement. 50% of the construction waste to be recycled or re-used.
(j) All other incidental works associated with the completion of the Works
(k) Establishment charges, overhead charges and profit
(l) All necessary house keeping shall be compiled as per Employer's representative's instructions.
(m) For direct PO's issued by Employer, handling and inland transport of import material till delivery at site.
(n) Unit price to deem to include Power and Water charges.
(o) All wood works shall be Factory/Machine made, vendor shall submit the shop drawings of all the wood works prior to production/execution.
(p) Vendor shall submit shop drawings of all metal works and equipment installations for approval.
(q) All built-in joinery shall be factory fabricated
(r ) All exposed surfaces shall be lipped in 2mm thick PVC lipping and 1mm thick laminate as applicable.
H | The following items are not fully descriptive in themselves and are not meant to limit the scope of Works. The Contractor shall inspect the site and fully determine for himself the full scope of each item and price the same accordingly. No claim will be entertained from the Contractor concerning lack of knowledge on his part in pricing of these items.
I | The quality and extent of the Works shall be that as shown and/or described in the Drawings, Specifications and the General Conditions and Preliminaries.
J | The Contractor shall verify for himself all sizes and dimensions stated in the items hereunder and be fully responsible for the accuracy of the same.
K | Quantity shall be measured in accordance with IS 1200 - Method of Measurement for Building and Civil Engineering works. Unless otherwise stated in the Standard Method of Measurement or herein, work shall be measured NET as fixed in position
L | Co-ordination with other Contractors for installation, testing & commissioning and completion of system as per operational requirement and complete satisfaction to the Employer's Representative.
M | Wastages of items are deemed to be included in the unit price
N | All ceilings shall be measured only on visible Horizontal planes. Vertical side of the Ceiling up to 600mm level are deemed to be included in the unit price and shall not be measured additionally
O | All Aluminium proprietary sections shall be measured based on actual visible length and all supports and associated works are deemed to be included in the unit price
P | All the cabinetries storages, racks shall be measured from the visible front elevation, unless and until specifically mentioned
Q | All the counter top shall be measured from the visible plan area, unless and until specifically mentioned.
R | All Proprietary system items need to be installed by authorised dealer / authorised vendor and certificated to be produced
S | One single master key shall be provided for all the locks for the entire building
T | Unless otherwise specified, all MS sections to be coated with Metal Primer and 2 coats of Enamel Paint.
U | All partitions shall be measured from true floor level to False Ceiling level and False ceiling level to bottom of true ceiling.
V | Glass partitions shall be measured based on actual visible height of the glass partition in length and height shall be measured.
W | All Column cladding face area shall be measured from true floor level to False Ceiling level. Cladding above the False ceiling level is deemed to be included in the unit price
X | Contractor scope shall include supply and installation of appropriate protective layer for all type of flooring till handing over the facility to the complete satisfaction of Architect
Y | All the paints shall be low VOC content as per the LEED requirement / Architect's approval
Z | Tenderer shall consider unique identification for the communal lockers in the office spaces / storages, meaning each locker will have a key unique to it. The Locks shall not be openable with Key for one locker with other(s).
AA | The description provided are brief. The Contractor shall inspect the site, STUDY THE DRAWINGS AND DETAILS and fully determine for himself the full scope of each item and price the same accordingly. No claim shall be permissible for lack of knowledge on Contractor's part in pricing of these items.
AB | All Samples of tiles, fittings etc.shall be presented after ensuring that the necessary quantities of the relevant item(s) for which the same are invited are available, (ex-stock, or otherwise) and shall be approved by the architect before placing of mass orders.
AC | The quantities of the various items mentioned in the schedule in the schedule of items are approximate and may vary up to any extent or be deleted altogether the quoted rates of each item shall remain firm for both the variation and extra items. The contractor, in his own interest, should get an indication of the probable extent of the work to be executed under any particular item in this schedule, before undertaking any preliminary and enabling work or purchasing bought out components related to the work.
AD | The rates quoted shall be inclusive of all mock-ups, associated samples prior to any mass production or procurement as per complete satisfaction of the Client and Architect. Inclusive of dismantling, demolishing and carting the material and making good of the surface.
AE | All services works, any interface works with other vendors have to be completed before finishing of partition panelling, other wall finishes and false Ceiling works. Signoff shall be taken from the Engineer incharge before proceeding with the final finishing works.
AF | All basic rates mentioned in the BOQ are exclusive of all Taxes, transportation, delivery of material at site, lead & lift.
AG | Vendor to include Freight and transit insurances up to delivery at site in the quoted price.
AH | Material shall be dispatched from the plant or warehouse only upon written communication from the Project Managers
AI | Vendor shall handover all logistics and commercial documents in Original to the Client's representative without fail
AJ | Without all above details their bid submission shall be considered NULL & VOID
AK | Vendor shall consider master key for all doors/door locks supplied and installed
NOTES TO WORK ITEMS UNDER BILLS OF QUANTITIES FOR MODULAR GRID FALSE CEILING WORKS
A | These notes shall apply to other Bills in these documents.
B | The works under this Bills of Quantities shall be priced based on remeasurable quantities.
C | This Bill shall be read in conjunction with the General Conditions and Preliminaries, Specification of Materials and Workmanship, Drawings and all other Bills of Quantities contained in these documents which shall be construed as being complementary to one another
D | The Contractor shall provide and do everything reasonably necessary for the proper execution of the Works according to the true intent and meaning of the Drawings, the Specification and the Documents forming part of the Contract taken together the same as may or may not be particularly shown or described, provided that the same is reasonable to be inferred there from. If the Contractor should find any discrepancy in the Drawings or between the Drawings and the Specification or any other Documents forming part of the Contract, he shall immediately refer the same to the Employer's Representative who shall decide which shall be followed.
E | The rates and prices herein shall be inclusive of all Works, materials and expenditure, whether separately or specifically mentioned or described in the Contract Documents or not, which are either indispensably necessary to carry out and bring to completion the works described in or to be inferred from the Contract documents taken as a whole or which may contingently become necessary to overcome difficulties and bring the said works so described or inferred to satisfactory completion.
F | For the purpose of valuation of variations, any omission or additions to the Contract Sum shall be based on measured quantities, applying the relevant unit rates (or pro-rated unit rate, as the case may be) found in the Bills of Quantities. As such, the Contractor is advised to price each item contained in the Bills in a fair and realistic manner.
G | Vendors to submit their SLA’s for Warranty & After sales Support with List of Support centres in India and committed Turn around Time’s to attend Warranty cases. Escalation mechanism with contact details to be shared in their RFP proposal
H | Vendor shall submit the terms of warranty along with the priced bids.
I | Necessary service cutouts shall be considered in the unit price quoted.
J | Unless otherwise specifically stated in the Bills, the following shall be deemed to include with all items: -
(a) Labour and all costs in connection therewith
(b) Material and goods including materials required for lapping, jointing and all costs in connection therewith such as materials conveyance and delivery etc., complete.
(c) Unloading, storing, returning packing, handling, hoisting and lowering materials
(d) Assembling, setting, fitting and fixing materials in position and all costs in connection therewith; such as handling waste and cutting waste
(e) Use of plant, tools and equipment and all cost in connection therewith
(f) All necessary protection, temporary staging, shoring, scaffolding, screens etc and other temporary work required in connection therewith
(g) Executing the whole of the Works in confined spaces as and when directed by the Employer's representative
(h) All necessary protection of Contractor's works against damage and making good of all works disturbed in connection therewith
(i) Removing all debris from site
(j) All other incidental works associated with the completion of the Works
(k) Establishment charges, overhead charges and profit
(l) All necessary house keeping shall be compiled as per Employer's representative's instructions.
(m) For direct PO's issued by Employer, handling and inland transport of import material till delivery at site.
(n) Unit price to deem to include Power and Water charges.
(o) In case of any scaffolding required, double height or single height as per the site requirement, the same shall be provided by the contractor at no extra cost.
(p) The rates quoted shall be inclusive of all mock-ups, associated samples prior to any mass production or procurement as per complete satisfaction of the Client and Architect Inclusive of dismantling, demolishing and carting the material and making good of the surface.
(q) All services works, any interface works with other vendors have to be completed before finishing of false Ceiling works. Sign off shall be taken from the Project Manager nominated by the client before proceeding with the final finishing works.
(r) Price quoted shall include all incidental wastages.
K | The following items are not fully descriptive in themselves and are not meant to limit the scope of Works. The Contractor shall inspect the site and fully determine for himself the full scope of each item and price the same accordingly. No claim will be entertained from the Contractor concerning lack of knowledge on his part in pricing of these items.
L | The quality and extent of the Works shall be that as shown and/or described in the Drawings, Specifications and the General Conditions and Preliminaries.
M | The Contractor shall verify for himself all sizes and dimensions stated in the items hereunder and be fully responsible for the accuracy of the same.
N | Quantity shall be measured in accordance with IS-1200 Method of Measurement for Building and Civil Engineering works. Unless otherwise stated in the Standard Method of Measurement or herein, work shall be measured NET as fixed in position.
O | Method of measurement for Ceiling shall be on the actual laid plan areas, excluding Columns, wall area, light fixtures, A/C diffusers and A/C grills etc., jointly measured after satisfactory completion of works at site
P | Deductions for column areas in Ceiling shall be made based on the final dimension of columns after cladding/ panelling
Q | Co-ordination with other Contractors for installation, testing & commissioning and completion of system as per operational requirement and complete satisfaction to the Employer's Representative.
R | Stained and damaged ceiling tile shall be replaced by the vendor prior to uncover of carpet protection, for which the quoted unit price is deemed to be included.
S | Vendor to include Freight and transit insurances up to delivery at site in the unit rates quoted.
Z | Without all above details their bid submission shall be considered NULL & VOID
NOTES TO WORK ITEMS UNDER BILLS OF QUANTITIES FOR ROLLER BLIND WORKS
A | These notes shall apply to other Bills in these documents.
B | The works under this Bills of Quantities shall be priced based on remeasurable quantities.
C | This Bill shall be read in conjunction with the General Conditions and Preliminaries, Specification of Materials and Workmanship, Drawings and all other Bills of Quantities contained in these documents which shall be construed as being complementary to one another
D | The Contractor shall provide and do everything reasonably necessary for the proper execution of the Works according to the true intent and meaning of the Drawings, the Specification and the Documents forming part of the Contract taken together the same as may or may not be particularly shown or described, provided that the same is reasonable to be inferred there from. If the Contractor should find any discrepancy in the Drawings or between the Drawings and the Specification or any other Documents forming part of the Contract, he shall immediately refer the same to the Employer's Representative who shall decide which shall be followed.
E | The rates and prices herein shall be inclusive of all Works, materials and expenditure, whether separately or specifically mentioned or described in the Contract Documents or not, which are either indispensably necessary to carry out and bring to completion the works described in or to be inferred from the Contract documents taken as a whole or which may contingently become necessary to overcome difficulties and bring the said works so described or inferred to satisfactory completion.
F | For the purpose of valuation of variations, any omission or additions to the Contract Sum shall be based on measured quantities, applying the relevant unit rates (or pro-rated unit rate, as the case may be) found in the Bills of Quantities. As such, the Contractor is advised to price each item contained in the Bills in a fair and realistic manner.
G | This project is not an EOU facility, vendor to consider the same for pricing accordingly.
H | Vendor shall provide warranty of 3 years from the date of installation and handing over on all products supplied and price the quote accordingly.
I | Vendor shall submit the terms of warranty along with the priced bids.
J | Unless otherwise specifically stated in the Bills, the following shall be deemed to include with all items: -
(a) Labour and all costs in connection therewith
(b) Material and goods including materials required for lapping, jointing and the like and all costs in connection therewith such as materials conveyance and delivery
(c) Unloading, storing, returning packing, handling, hoisting and lowering materials
(d) Assembling, setting, fitting and fixing materials in position and all costs in connection therewith; such as handling waste and cutting waste
(e) Use of plant, tools and equipment and all cost in connection therewith
(f) All necessary protection, temporary staging, shoring, scaffolding, screens etc and other temporary work required in connection therewith
(g) Executing the whole of the Works in confined spaces as and when directed by the Employer's Representative.
(h) All necessary protection of Contractor's works against damage and making good of all works disturbed in connection therewith
(i) Removing all debris from site as per instructions of Employer's representative.
(j) All other incidental works associated with the completion of the Works, and
(k) Establishment charges, overhead charges and profit
(l) All necessary house keeping shall be compiled as per Employer's representative's instructions.
(m) For direct PO's issued by Employer, handling and inland transport of import material till the delivery of material at site.
K | The following items are not fully descriptive in themselves and are not meant to limit the scope of Works. The Contractor shall inspect the site and fully determine for himself the full scope of each item and price the same accordingly. No claim will be entertained from the Contractor concerning lack of knowledge on his part in pricing of these items.
L | The quality and extent of the Works shall be that as shown and/or described in the Drawings, Specifications and as per the General Conditions and Preliminaries.
M | The Contractor shall verify for himself all sizes and dimensions stated in the items hereunder and be fully responsible for the accuracy of the same.
N | All manufacturing to begin, based on approved shop drawing & GFC only & not as per the tender BOQ.
O | Vendor to include Freight and transit insurances up to delivery at site in the quoted price.
NOTES TO WORK ITEMS UNDER BILLS OF QUANTITIES FOR GENERAL WORKS
(a) | Necessary providing with shelter of Lockable arrangements
(b) | DG backup to be considered as per the PM's Instructions
© | Project Progress monitoring cameras to create Time Lapse Video, matterport i.e. latest construction management technology includes capacity, time interval, reporting frequency, Internet clouding (Site Kick-off to Project handover) as per Project Manager's instructions. Submission of final compiled video is also part of scope.
(d) | Quoted rate shall includes as built documentation as per the architect / PM 's instructions
€ | Mock up & sample at free of cost mentioned in General notes. But whether contractor to surrender to client (or) he can take it back. Similarly for all the temporary arrangement which may be demobilized from site.
(f) | During construction all required statuory & Health safety premeasures related item to be considered in time of pandemic as per the project manager requirements
CONTRACTOR'S ADMINISTRATIVE ARRANGEMENTS
Site Administration
Supervision of the Works
The Contractor shall ensure that an efficient organization structure is maintained at all times, so that all instructions issued by Project Manager are communicated immediately to the site staff, and to all subcontractors and suppliers.
Safety and Health and Welfare of Work People
The Contractor shall provide for all costs and charges incurred in complying with all safety, health and welfare regulations pertaining to all work people employed on the Site, including those employed by all Subcontractors.
Vermin
The Contractor shall take all necessary precautions to prevent the establishment of pests and vermin within the buildings and environment by means of regular inspections. The Contractor shall ensure that the site and its environments are kept free from debris and waste materials likely to encourage the establishment of such pests and vermin.
Water for the Works
Provide temporary arrangements for storage and distribution around the Site and pay all costs and charges in connection therewith. Alter, shift and adapt all pipe work and fittings from time to time as necessary and clear away and make good on completion.
Note: Client shall provide water at free of cost in a single point at the site
Cleaning
Allow for daily removal of rubbish and for final cleaning the site, works and other completed sections while handing over the facility with sparkle clean quality
EHS or any other Pandemic related measures
EHS Readiness & COVID 19 Preparation for site ( Site Sanitization,Thermal screening, Safety Signages supply & installation, establishment of safety procedures,implemention of agreed logistics etc., )
Stores to place the materials to be constructed by contractor
Material Stacking cost to be included in the item rates quoted by contractor
Construction water & power 2% shall be deducted on monthly basis
WCP to be availed by the contractor as per the Govt. norms. CAR,PI,Pubilic liability will be taken by Moser, The same is 2.5% of the total package cost shall be deducted during the final contractor bill certifications towards insurance.
Vendor to follow all the following annexure
1. Builder Fitout Guidelines
2. EHS Guidelines
3. HSS - De Process
4, Material Management

## Project Requirements
PROJECT PRELIMINARY REQUIREMENTS
SL NO | DESCRIPTION
QUOTED LINE ITEM RATE SHALL INCLUDES BELOW MENTIONED PRELIMINARIES REQUIREMENT FOR THE PROJECT :
Definitions, Interpretation and Application
The Contract shall be deemed to include these Preliminaries and General Requirements, which are intended to cover the whole of the Works and form part of the Bill of Quantities.
The definitions and the interpretations forming part of the general conditions of contract shall apply to this Preliminaries and General Requirements
The Contractor shall satisfy himself as to the meaning of each item in the Bill of Quantities and the rates inserted shall be deemed to cover all obligations under the terms of the contract and all matters necessary for execution, completion and the remedy of all defects contained therein.
The below specified list of preliminaries works should be included part of the project cost. There is no additional cost paid for preliminaries works
CONTRACTOR'S ADMINISTRATIVE ARRANGEMENTS
Site Administration
1 | Supervision of the Works
The Contractor shall ensure that an efficient organization structure is maintained at all times, so that all instructions issued by Project Manager are communicated immediately to the site staff, and to all subcontractors and suppliers.
2 | Safety and Health and Welfare of Work People
The Contractor shall provide for all costs and charges incurred in complying with all safety, health and welfare regulations pertaining to all work people employed on the Site, including those employed by all Subcontractors.
3 | Vermin
The Contractor shall take all necessary precautions to prevent the establishment of pests and vermin within the buildings and environment by means of regular inspections. The Contractor shall ensure that the site and its environs are kept free from debris and waste materials likely to encourage the establishment of such pests and vermin.
CONTRACTOR'S FACILITIES
4 | Maintenance of labour Toilet ( Facility Handicap Toilets)
The Toilet to be cleaned 3 times per day as per the PM's instructions. inclusive of maintenance / cleaning of All number of Physically Challenged toilet for Labour ( provided by builder ) 3 times per day as per the PM's instructions.
Water for the constructions Works
5 | Provide temporary arrangements for storage and distribution around the Site from the point provided by builder and pay all costs related Piping, connection Etc., . The scope includes Alter, shift and adapt all pipe work and fittings from time to time as necessary and clearway and make good on completion. Vendor has to arrange necessary metering as per the PM instructions
Protecting the Works
6 | Provide for carefully and adequately covering up and protecting all of the Works in accordance with the BOQ Specification or best practices as approved by the Project Manager by whatever means necessary during execution and on completion until Taking Over by Project Manager. In pursuance of his obligations under the contract, the Contractor shall, wherever required or directed by Project Manager's Representative, cover up and protect the Works from any workmen or other agencies, Subcontractors, undertaking work subsequent to the completion of his work.
The existing facility common area's are already protect by the third party vendor, The same protection has to be taken care till the handover of the facility, If any damage happen on existing protection on common area ( Exp:Stair case, Lift lobby / AHU/ Service Lift Lobby/ Electrical rooms Etc., ) shall be replace and protected as per best site practice / PM instructions.
7 | REINSTATEMENT WORKS OF SERVIE LIFT LOBBY / STAIR CASE / LABOUR TOILETS
Removal of the all the protection & reinstate works the existing Stair case, Lift lobby, Service lift lobby, Basements other area Wall/ Flooring material / Ceiling / Doors Etc.,, The scope include the reinstatement of the all the Patch works for the damages happened during the constructions works as per the site conditions. And All the labour toilets / Handicapped toilet of the facility (Used as labour toilets ) shall be reinstated to the original condition with complete deep cleaning / Chemical Cleaning, Painting and fixture reinstallation.
8 | Complete Mock room including the Partition, finishes, coordinated with services as per the approved drawings with necessary internal arrangements as per MMA team direction. The Mock-up area works shall mobilized & Completed on priority for the MMA approval.
9 | SUPPLY AND INSTALLATION OF BINS FOR WASTE MANAGEMENT
Supply & installation of complete waste management bins as per the LEED requirements for the entire duration of the project - one collection point at each floor ,(3 No's 660ltr ) waste bins with colour code and label, necessary signages as required and complete as per the requirement of the MMA .
The dust bin shall be provided for the complete project duration.
Vendor has to carting away the debris ( no of loads should be calculated as per the project & site requirement ) from the site to the nearest Municipal dump yard as and when required as per the Project Manager instruction and as per the site requirement.
10 | SAFETY & LEED RELATED SIGNAGES
Vendor has to provide safety & LEED related signages made of standy signage with Matters/images pasted on vinyl stickers of A2 size on it as per the site & PM/architect requirements during the complete duration of the works.
Contractors responsibility to take care of storing their own materials with safe guarding
11 | Allow for daily removal of Debris and for final cleaning the site, works and other completed sections while handing over the facility with sparkle clean quality Other Costs, etc.
12 | The Contractor shall allow for and provide details of any costs, expenses, etc., incurred in carrying out the requirements of the contract, and not otherwise included separate statements identifying the levels of thein the Bill of Quantities. All costs and expenses not entered hereinafter shall be deemed to be included in the rates or prices inserted elsewhere in the Bill of Quantities:
EHS or any other Pandemic related measures
13 | HAND SANITIZER FOR THE ENTRY
Supply and installation of hand sanitizer with stand ( foot operated) as per of approved make for entire project duration
14 | DRINKING WATER
Supply of Drinking water for the site office, Labour lunch area, Meeting Rooms , Working floor labours (for all the labours)as per the site requirement and PM instruction.
Drinking water test report to be submitted following IS standards.
Drinking water availability to be ensured always.
Drinking water supply with dispenser
15 | FUMIGATIONS
Fumigation for the entire site premises on daily routine basis to control virus transmission at site. The works shall be carried as per PM's instructions

## Master Summary
PROJECT : | M/s SIEMENS HEALTHINEERS, GURGAON
SUBJECT : | BILL OF QUANTITIES FOR CIVIL AND INTERIOR FINISHING WORKS
DATE : | 17.10.2025
REVISION:R1
PROJECT : M/s SIEMENS HEALTHINEERS, GURGAON
Date:
MASTER SUMMARY OF GC CIVIL & INTERIOR WORKS
SL.NO | DESCRIPTION OF ITEMS | Nirmaan Price | Nirmaan Price | REMARKS
1 | CIVIL & INTERIOR WORKS
2 | GLASS PARTITION & DOORS
3 | TOILET C&I WORKS
4 | All Solid and Glass door
5 | SANITARY FIXTURES + PIPING
6 | RAISED FLOORING
7 | PLANT & POT
8 | SIGNAGE & GRAPHIC
9 | WHITE GOODS
10 | CARPET
11 | CHAIRS
12 | MODULAR FURNITURE
13 | LOOSE FURNITURE
14 | RFID LOCKERS & SLOTTED ANGLE RACKS
15 | ELECTRICAL | 0
16 | UPS
17 | LMS
18 | IT NETWORKING
19 | LIGHTING | 0
20 | HVAC
21 | FIRE PROTECTION SYSTEM
22 | SIGNAGES
23 | FIRE EXTINGUISHER
| SUB TOTAL FOR CIVIL & INTERIOR WORKS EXCLUDING TAXES | 0 | 0
| GST @18% | 0
| OTHER APPLICABLE TAXES @1% | 0
| SUB TOTAL FOR CIVIL & INTERIOR WORKS INCLUDING TAXES | 0

## BOQ_ELECTRICAL
PROJECT : | M/s SIEMENS HEALTHINEERS, GURGAON
SUBJECT : | BILL OF QUANTITIES FOR ELECTRICAL WORKS
CONSULT : | E SOLLUTIONS
DATE : | 2025-08-28
REVISION: | R0
Target Price
Sl No. | ITEM DESCRIPTION | Ref No | UNIT | QTY | Supply Rate | Installation Rate | Supply Amount | Installation Amount | Total Amount (INR) | REMARKS
1 | LT PANELS:
Panels as per technical specifications & schematic diagram.
Supply, Installation, Testing and Commissioning of Indoor type LT Switchboards, Floor mounting type, Bottom/Top entry. Refer enclosed SLD.
Enclosure: Compartmentalized Single front CRCA (Cold rolled Cold Annealed sheet steel)
Doors:2mm Body:2mm Gland:3mm covers and partitions:1.6mm
IP class:IP42 for Indoor/IP55 with weather proof enclosure for outdoor
Bus bars: Electrolytic grade conductivity as per standard IS 5082
Bus bar Material: As per SLD
Bus bar supports: DMC/FRP/SMC
Bus bar joints: Shrouded/Tinned
Protection releases: As per SLD (Adjustable over current & short circuit unless otherwise specified)
Ics=Icu for all breakers
Utilization category: All MCCB/ACB's shall be Cat: A except ACB's for Ltg & raw power input distribution panel shall be with Cat: B .
Loovers: Busbar chamber shall have louvers with fine mesh inside
Shade: Epoxy powder coated RAL 7032
Design: Modular type
Cable entry: As per site condition
Bus bar insulation: Aluminum bus bars shall be bare with color coding at the ends/Copper shall be bare with color coding at the ends/For Humidified areas the copper bus bars shall be coated with tin.
Note:
1. The Panel shall be fully as per the requirement of Electrical Inspectorate/ EB authorities.
1. Panel Should be as per IEC 61439 Design
2. Auxilliary contactor to be provided along with auto-manual switch where ever required.
3. All MCCB Breakers both Incoming & Outgoing shall have LED 'ON / OFF / TRIP' indications without fail.
4. CTs shall be with dual ratio and cast resin type only.
5. All doors to have double rubber gasket with shutter assembly & door seating frame.
6. All AC feeders will have time delays of 0-60 Seconds.
7. All MCCBs of 250A and above will be microprocessor based only.
8. Any panel if more than 1.5m width should be made in parts each part not exceeding 1.5m.
9. The current density for Aluminium busbars shall be 0.8 only.
10. The current density for Copper busbars shall be 1.2 only.
11. All UPS outgoing panels shall have neutral busbars double the size of phase.
12. All MCCB's shall have plug setting from (40or50)-100%.
13. All Lighting / RP and Lift panels shall have ELR for incomer of Prok. Dvs. Make only.
14. All test certificates must be provided immediately after commissioning.
15. SAFETY CERTIFICATE FOR THE PANELS SHALL BE PRODUCED FROM CEIG.
16. All meters shall be Digital type only.
17. FRLS PVC copper wires shall be used for control wiring
18. The MCCB should be current limiting type with trip time of less than 10 msec under short circuit conditions. The MCCB should be either 3 or 4 poles as specified in BOQ. MCCB shall comply with the requirements of the relevant standards IS13947 – Part 2/IEC 60947-2 and should have test certificates for Breaking capacities from independent test authorities CPRI / ERDA or any accredited international lab.
All Electrical Panel must be with inbuilt Fire suppression Panel
Important Note : - Breaker discrimination study need to carried out & Breaker/Breaker frames need to be selected accordingly.
1.01 | MAIN FLOOR LT PANEL |  | No | 1 |  |  | 0 | 0 | 0 |  | *Details Required
1.02 | 60 KVA UPS OUTPUT PANEL |  | No | 1 |  |  | 0 | 0 | 0 |  | *Details Required
1.2 | 4P RCBO with enclosures | [7 empty] | 0
1.2.1 | 16A |  | No |  |  |  | 0 | 0 | 0
1.2.2 | 20A |  | No | 2 |  |  | 0 | 0 | 0
1.2.3 | 40A |  | No | 4 |  |  | 0 | 0 | 0
1.3 | 4P & DP MCB & MCCB with enclosures | [7 empty] | 0
1.3.1 | 16A, FP, MCB |  | No |  |  |  | 0 | 0 | 0
1.3.2 | 40A, FP, MCB |  | No |  |  |  | 0 | 0 | 0
1.3.2 | 63A, FP, MCCB |  | No | 1 |  |  | 0 | 0 | 0
1.3.3 | 32A DP D-MCB |  | No |  |  |  | 0 | 0 | 0
1.3.4 | 40A DP C-MCB |  | No |  |  |  | 0 | 0 | 0
0
2 | LT CABLES & ENDTERMINATIONS
Supply, Laying, Testing and Commissioning of stranded XLPE insulated, Armoured/Unarmoured/Flexible, Aluminum / Copper conductor, laid in tray / hume pipe / in ready made trenches, with nylon cable ties / MS Clamps @ 600mm interval etc., as required. The cost of the nylon tie and overlapping GI strip shall be included in the cost of installation.
Supply, Installation, Testing and Commissioning of Compression type cable gland, aluminum sockets for aluminum cables / copper sockets for copper cables, insulation tape, anti corrosive paste, brass clamps for gland earthing with 14 SWG copper wire to connect to nearest earth flat.
Insulation: XLPE
Inner sheath: Extruded PVC only for Multicore
Outer sheath: Extruded Type ST2 PVC with FRLS
Voltage grade:1100Volts
Armoure: Galvanized Steel strip/Wire for multicore
Non Magnetic Aluminum Wire/Strip for Single core
Gland type : Brass with nickel plated
Compression : Double compression above 35 Sq.mm
Sealing Ring : Natural rubber for indoor, Neoprene for Outdoor
Note : Bimetalic lugs/strips need to be considered where copper cables connected to Aluminium busbars
2.1 | XLPE insulated, steel armoured, aluminium conductor 3.5 Core cables. | [7 empty] | 0
0
2.1.1a | 3.5 C x 300 sq.mm (XLPE) |  | Rm |  |  |  | 0 | 0 | 0
2.1.1b | End Termination |  | No |  |  |  | 0 | 0 | 0
2.1.2a | 3.5 C x 150 sq.mm (XLPE) |  | Rm | 0 |  |  | 0 | 0 | 0
2.1.2b | End Termination |  | No | 0 |  |  | 0 | 0 | 0
2.1.3a | 3.5 C x 95 sq.mm (XLPE) |  | Rm | 100 |  |  | 0 | 0 | 0
2.1.3b | End Termination |  | No | 2 |  |  | 0 | 0 | 0
2.1.4a | 3.5 C x 70 sq.mm (XLPE) |  | Rm | 0 |  |  | 0 | 0 | 0
2.1.4b | End Termination |  | No | 0 |  |  | 0 | 0 | 0
2.1.5a | 3.5 C x 50 sq.mm (XLPE) |  | Rm |  |  |  | 0 | 0 | 0
2.1.5b | End Termination |  | No |  |  |  | 0 | 0 | 0
2.1.6a | 3.5 C x 35 sq.mm (XLPE) |  | Rm | 0 |  |  | 0 | 0 | 0
2.1.6b | End Termination |  | No | 0 |  |  | 0 | 0 | 0
2.2 | XLPE/ PVC Insulated & Steel Armoured Aluminium Conductor cables
2.2.1a | 4C X 25 sq.mm (XLPE) |  | Rm | 190 |  |  | 0 | 0 | 0
2.2.1b | End Termination |  | No | 8 |  |  | 0 | 0 | 0
2.2.2a | 4C X 16 sq.mm (XLPE) |  | Rm | 180 |  |  | 0 | 0 | 0
2.2.2b | End Termination |  | No | 6 |  |  | 0 | 0 | 0
2.2.3a | 4C X 10 sq.mm (XLPE) |  | Rm | 190 |  |  | 0 | 0 | 0
2.2.3b | End Termination |  | No | 8 |  |  | 0 | 0 | 0
2.2.4a | 4C X 6 sq.mm (XLPE) |  | Rm |  |  |  | 0 | 0 | 0
2.2.4b | End Termination |  | No |  |  |  | 0 | 0 | 0
0
2.2.5a | 4C X 4 sq.mm (pvc) |  | Rm |  |  |  | 0 | 0 | 0
2.2.5b | End Termination |  | No |  |  |  | 0 | 0 | 0
2.3 | XLPE / PVC Insulated & Steel Armoured Copper Conductor cables (YFY Type)
2.3.1a | 4C X 25 sq.mm (XLPE) |  | Rm | 120 |  |  | 0 | 0 | 0
2.3.1b | End Termination |  | No | 4 |  |  | 0 | 0 | 0
2.3.2a | 4C X 16 sq.mm (XLPE) |  | Rm | 80 |  |  | 0 | 0 | 0
2.3.2b | End Termination |  | No | 8 |  |  | 0 | 0 | 0
0
2.3.3a | 4C X 10 sq.mm (XLPE) |  | Rm |  |  |  | 0 | 0 | 0
2.3.3b | End Termination |  | No |  |  |  | 0 | 0 | 0
2.3.4a | 4C X 10 sq.mm (PVC) |  | Rm |  |  |  | 0 | 0 | 0
2.3.4b | End Termination |  | No |  |  |  | 0 | 0 | 0
2.3.5a | 3C X 10 sq.mm (PVC) |  | Rm | 170 |  |  | 0 | 0 | 0
2.3.5b | End Termination |  | No | 8 |  |  | 0 | 0 | 0
2.3.6a | 3C X 6 sq.mm (PVC) |  | Rm | 0 |  |  | 0 | 0 | 0
2.3.6b | End Termination |  | No | 0 |  |  | 0 | 0 | 0
2.3.7a | 3C X 4 sq.mm (PVC) |  | Rm | 100 |  |  | 0 | 0 | 0
2.3.7b | End Termination |  | No | 4 |  |  | 0 | 0 | 0
2.3.8a | 1C X 10 sq.mm (PVC) |  | Rm | 100 |  |  | 0 | 0 | 0
2.3.8b | End Termination |  | No | 10 |  |  | 0 | 0 | 0
2.4 | PVC insulated, sheathed, unarmoured, flexible copper conductor cables - single & Multi Core (YY)
2.4.1a | 4C x 16 sq.mm |  | Rm | 40 |  |  | 0 | 0 | 0
2.4.1b | End Termination |  | No | 6 |  |  | 0 | 0 | 0
2.4.2a | 4C x 10 sq.mm |  | Rm |  |  |  | 0 | 0 | 0
2.4.2b | End Termination |  | No |  |  |  | 0 | 0 | 0
2.4.3a | 1 C x 70 sq.mm |  | Rm |  |  |  | 0 | 0 | 0
2.4.3b | End Termination |  | No |  |  |  | 0 | 0 | 0
2.4.4a | 1 C x 35 sq.mm |  | Rm | 200 |  |  | 0 | 0 | 0
2.4.4b | End Termination |  | No | 22 |  |  | 0 | 0 | 0
2.4.5a | 1 C x 35 sq.mm |  | Rm |  |  |  | 0 | 0 | 0
2.4.5b | End Termination |  | No |  |  |  | 0 | 0 | 0
2.4.6a | 1 C x 16 sq.mm |  | Rm | 90 |  |  | 0 | 0 | 0
2.4.6b | End Termination |  | No | 10 |  |  | 0 | 0 | 0
`
2.4.7a | 1 C x 10 sq.mm |  | Rm |  |  |  | 0 | 0 | 0
2.4.7b | End Termination |  | No |  |  |  | 0 | 0 | 0
2.4.8a | 1 C x 4 sq.mm |  | Rm |  |  |  | 0 | 0 | 0
2.4.8b | End Termination |  | No |  |  |  | 0 | 0 | 0
3 | MCB DISTRIBUTION BOARDS (DB)
Supply, Installation, Testing and Commissioning of MCB Distribution board as per approved installation dwgs.
Wall mounted MCB DBs with MS wire way box on top / bottom & on sides. MCBs shall be rated for 10kA with current limiting feature. Dummy ways to be covered with blank plates. All out going ways shall be labelled & laminated.
Enclosure:1.6mm CRCA Sheet Steel, Powder Coated
Door : Single Door, with fixing on both sides
Protection : IP 42
Cable Entry : Top & Bottom
Bus bar : Shall be tinned Copper and 200% rating for UPS DB Neutral Link
MCB's : 10kA 'C' Curve for Lighting & Raw power, 10kA 'D' Curve for UPS Distribution
Note:
1) Separate Earth bus/Neutral bus for each phase
2) Each Circuit shall have yellow ferrules with circuit number.
3) Accessories required for installation of DB's on Wall/Column/Gyp Board shall be considered
4) DB's shall be covered with powder coated (paint should match with DB Color) wire ways all around and up to ceiling to receive incoming circuits, how ever raceway shall be considered as a separate items
5) Laminated A3 OR A4 size SLD copy shall be pasted inside DB door
6) Safe shroud for Neutral link shall be provided
7) For all the DB details refer respective floor drawing, DB schematic
3.1 | LDB's :
3.1.1 | 4Tier 40Module TPN DB - Lighting DB
Incomer : 1No. 40A, 4P, MCB of 'C' Curve
Phase Isolator : 3Nos, 40A, DP, RCCB of 30mA
| Outgoing : 24 Nos. 10/16A SP MCB of 'C' curve |  | No. | 0 |  |  | 0 | 0 | 0
3.1.2 | 4Tier 56Module TPN DB - Lighting DB
Incomer : 1No. 40A, 4P, MCB of 'C' Curve
Phase Isolator : 3Nos, 40A, DP, RCBO of 30mA
| Outgoing : 18 Nos. 10/16A DP RCCB 30 mA |  | No. | 3 |  |  | 0 | 0 | 0
3.1.3 | 16Way SPN DB - Lighting DB - Emergency Lighting
Incomer : 1No. of 40A, DP, MCB
| Outgoing : 7Nos. of 10A, DP RCCB 30mA |  | No. | 1 |  |  | 0 | 0 | 0
3.1.4 | 8Way SPN DB - Lighting DB - Emergency Lighting
Incomer : 1No. of 32A, DP, MCB
| Outgoing : 6Nos. of 6A, SP, 'C' curve MCB |  | No. | 0 |  |  | 0 | 0 | 0
3.1.5 | 4Tier 40Module TPN DB - & VAV DB & EMERGENCY
Incomer : 1No. 40A, 4P, MCB of 'C' Curve
| Phase Isolator : 3Nos, 40A, DP, RCCB of 30mA |  | No. | 0 |  |  | 0 | 0 | 0
Outgoing : 24 Nos. 10/16A SP MCB of 'C' curve
3.2 | RDB's :
3.2.1 | 4Tier 56Module TPN DB
Incomer : 1No. of 63A, 4P, 'C' Curve MCB
Phase Isolator : 3Nos. of 40A, DP, RCCB 30mA
| Outgoing : 18 Nos. 16A DP RCCB 30 mA |  | No. | 2 |  |  | 0 | 0 | 0
3.2.2 | 4Tier 40Module TPN DB
Incomer : 1No. of 63A, 4P, 'C' Curve MCB
Phase Isolator : 3Nos. of 40A, DP, RCCB 30mA
| Outgoing : 12 Nos. 16A DP RCCB 30 mA |  | No. | 1 |  |  | 0 | 0 | 0
3.3 | UDB's :
3.3.1 | 4Tier 56Module TPN DB
Incomer : 1No. of 63A, 4P, 'D' Curve MCB
Phase Isolator : 3Nos. of 40A, DP, SI Type RCCB 30mA
| Outgoing : 18 Nos. 16A DP RCCB 30 mA |  | No. | 2 |  |  | 0 | 0 | 0
3.3.2 | 12Way SPN DB - UPS DB
Incomer : 1No. of 40A, DP, MCB
| Outgoing : 10Nos. of 16A, SP, 'D' curve MCB |  | No. | 0 |  |  | 0 | 0 | 0
3.4 | SERVER DB's :
3.4.1 | 6 Way TPN DB
Incomer : 1No. of 63A, 4P, 'C' Curve MCB
Phase Isolator : 3Nos. of 40A, DP, RCCB 30mA
| Outgoing : 9 Nos. of 32A, DP, RCCB 30mA |  | No. | 2 |  |  | 0 | 0 | 0
3.4.1 | 6 Way TPN DB
Incomer : 1No. of 63A, 4P, 'C' Curve MCB
Phase Isolator : 3Nos. of 40A, DP, RCCB 300mA
| Outgoing : 18 Nos. of 32A, SP, 'D' curve MCB |  | No. |  |  |  | 0 | 0 | 0
3.5 | VTPN DB :
3.5.1 | 12Way VTPN DB
Incomer : 1 No. 40A TP, MCB of 'C' curve
| Outgoing : 12 No. 40A TP, MCB of 'C' curve |  | No. | 0 |  |  | 0 | 0 | 0
3.5.2 | 6Way VTPN DB
Incomer : 1 No. 40A TP, MCB of 'C' curve
| Outgoing : 6 No. 40A TP, MCB of 'C' curve |  | No. | 1 |  |  | 0 | 0 | 0
4 | CIRCUIT / SUB MAINS:
Circuit mains using 1.1kV grade PVC insulated copper conductor (MSCC) wires / PVC insulated PVC sheathed three core cables drawn in MS CONDUIT or in existing raceway. For Lighting Rates quoted shall include supply of conduits, wires, Switches & other conduiting accessories. Circuit mains shall be measured from respective DB to the last point, looping from switch / socket to another switch /socket board will not be paid seperatelly. For RP & UPS points Rates quoted shall include supply of conduits & cables, Circuit mains shall be measured from respective DB to the last point, looping from switch / Socket to another switch / socket board will not be paid seperatelly. All circuit terminations shall be provided with solder less crimping type copper sockets / lugs, ferrules indicating source code on load side & load code on source side. There shall not be any joints in the circuits, only looping is allowed in terminal blocks & in switches / socket outlets.
NOTE:
1) Conduits running above false ceiling in multiples shall be supported by Slotted GI 'C' channel at distance not more than 0.5mtrs intervals. OR else with spacers & saddles at an intervals of 0.5mtrs
2) Accessories shall includes Bends, Collars, junction boxes, Spacers, saddles, screws, Flexibles
3) Conduits shall be ISI marked
4) The number of wires drawn in each conduit shall be as per IS 694 code.
5) No different phases shall be drawn in same conduit
6) Conduit joints shall be done with threading proper accessories only
4.01 | 3C x 2.5 sq.mm cable with PVC-FRLS insulated outer sheath & multi strand copper conductors, unarmoured, cable to be laid in 25mm dia MS CONDUITs (cost of conduits to include) for Lighting circuits |  | Rm | 2400 |  |  | 0 | 0 | 0
4.02 | 3C x 4 sq.mm cable with PVC-FRLS insulated outer sheath & multi strand copper conductors, unarmoured, cable to be laid in raceways / conduits (cost of raceways/conduits to exclude) for Rawpower and UPS circuits |  | Rm | 4100 |  |  | 0 | 0 | 0
4.03 | 3C x 6 sq.mm cable with PVC-FRLS insulated outer sheath & multi strand copper conductors, unarmoured, cable to be laid in raceways / conduits (cost of raceways/conduits to exclude) for IT Racks |  | Rm | 450 |  |  | 0 | 0 | 0
4.04 | 3C x 2.5 sq.mm cable with PVC-FRLS insulated outer sheath & multi strand copper conductors, unarmoured, cable to be laid in raceways, modular partitions, conduits (Cost of Raceways & Conduit to exclude) for Circuit Main, Looping & VAV |  | Rm | 2100 |  |  | 0 | 0 | 0
5 | POWER RECEPTACLES.
Supply, Installation, Testing and Commissioning of the following Modular/Industrial Switch, sockets with modular front plate, and accessories as per the site conditions.
The quoted rate for power socket outlets shall include a. Socket outlets - round / round cum flat / flat multi pin socket outlets b.Switches c. 14SWG metal boxes with knockout on all sides d. Front plate of required colours with accessories
Industrial type sockets shall be of Metal clad / Polycarbonate body with plug top. All switch / sockets shall be provided with printed labels / stickers indicating source code. Colour code for UPS socket plates : White/ as per architect. Colour code for RP socket plates : Black/Grey/ as per architect. All switch / sockets including front plate & frame which will be mounted on the metal boxes shall have removable film coat to protect from scraches & paint during installation.
Note: Safety shutters to prevent accidental contact with live parts shall be provided. No indicator shall be provided for switches
a. All switches and sockets are modular type which shall be made of fire retardant; selfextinguish polycarbonate plastic, able to withstand the glow wire test ai 960 deg. C. b. The switches shall confirm IS 3854 :1997, The internal design of terminals and contact shall make the switch capable of high overload conditions, the switch shall be of flush type with silver inlay contact on pure copper. c. Socket outlets shall be of the three pins. All sockets shall fully comply with IS 1293: 2005 specifications. All wiring accessories shall be BIS approved.
5.1 | Modular : Round multipin type Without Box
5.1.1 | 6A socket controlled by 6A switch, excluding box (For UPS power) |  | No. | 0 |  |  | 0 | 0 | 0
5.1.2 | 2 x 6A socket controlled by 16A switch, excluding box (For UPS) |  | No. | 90 |  |  | 0 | 0 | 0
5.1.3 | 2x 6A socket controlled by 16A switch, excluding box (For - Raw) |  | No. |  |  |  | 0 | 0 | 0
5.1.4 | 3x 6A socket controlled by 16A switch , excluding box (For UPS power) |  | No. | 0 |  |  | 0 | 0 | 0
5.1.5 | 3x 6A socket controlled by 16A switch , excluding box (For Raw power) |  | No. | 0 |  |  | 0 | 0 | 0
5.1.6 | 1 no. 6/16A socket controlled by 16A switch, excluding box. (For UPS Power) |  | No. | 0 |  |  | 0 | 0 | 0
5.1.7 | 1 no. 6/16A socket controlled by 16A switch, excluding box. (For Raw Power) - For HAT |  | No. | 40 |  |  | 0 | 0 | 0
5.1.8 | 1 no. 6A socket outlet without switch excluding box. (For UPS Power) |  | No. | 0 |  |  | 0 | 0 | 0
Modular : Round multipin type With Box
5.1.9 | 1 no. 6A socket controlled by 6A SP switch, Including Box (UPS power - For Fire Damper +Security room+cctv etc) |  | No. | 20 |  |  | 0 | 0 | 0
5.1.10 | 1 x 6A socket controlled by 6A switch, Including box (For UPS power) |  | No. | 15 |  |  | 0 | 0 | 0
5.1.11 | 2 x 6A socket controlled by 16A switch, Including box (For UPS power - For Meeting Rooms AV Point) |  | No. | 15 |  |  | 0 | 0 | 0
5.1.12 | 3 x 6A Universal socket controlled by 16A switch, Including box (For UPS power ) |  | No. | 0 |  |  | 0 | 0 | 0
5.1.13 | 1 no. 6/16A socket controlled by 16A switch, Including box. (For HVAC Power) |  | No. | 0 |  |  | 0 | 0 | 0
5.1.14 | 1 no. 6/16A socket controlled by 16A switch, Including box. (For Raw Power - For Maintenance Purpose, Repro, & Pantry) |  | No. | 50 |  |  | 0 | 0 | 0
5.1.15 | 1 no. 6/16A socket controlled by 16A switch, Including box. (For UPS Power) |  | No. | 0 |  |  | 0 | 0 | 0
5.1.16 | 2x 6A socket controlled by 16A switch, including box (For Raw power - Collab Area) |  | No. | 0 |  |  | 0 | 0 | 0
5.1.16 | Readymade floor mounted Junction box - To locate 1 Set of 2 x 6A socket + 1no of 16A Switch and 2 Data outlets Similar to FrazerTechno make - 8 Module Cost need to include power outlets + Data outlets |  | No. | 1 |  |  | 0 | 0 | 0
5.1.17 | Readymade floor mounted Junction box - To locate 1 Set of 2 x 6A socket + 1no of 16A Switch and 2 Data outlets Similar to FrazerTechno make - 8 Module Cost need to include power outlets + Data outlets Note: The floor box should be with SS finish Top cover of Thickness 3mm & Access outlet of size 250mm x 250mmx 56mm with top cover thickness of 4 mm. |  | No. | 1 |  |  | 0 | 0 | 0
5.2 | SERVER/HUB Room Rack Sockets - With Box
5.2.1 | 1No. 25A 3 pin 1phase Interlocked type socket with plug top controlled by 16A DP MCB |  | No. |  |  |  | 0 | 0 | 0
5.2.2 | 1No. 32A 3 pin 1phase Interlocked Industrial type socket with plug top controlled by 32A DP MCB |  | No. | 10 |  |  | 0 | 0 | 0
5.2.3 | 1No. 32A 5 pin 3phase interlocked Industrial type socket with plug top controlled by 32A 4P MCB |  | No. | 0 |  |  | 0 | 0 | 0
5.3 | Industrial Sockets (IP 67)
5.3.1 | 16A 3pin 1phase Industrial socket with plug top controlled by 16A DP MCB |  | No. | 0 |  |  | 0 | 0 | 0
5.3.2 | 32A 3pin 1phase Industrial socket with plug top controlled by 32A DP MCB |  | No. | 0 |  |  | 0 | 0 | 0
5.3.3 | 16A 5pin 3phase Industrial socket with plug top controlled by 16A TPN MCB - Rawpower |  | No. | 0 |  |  | 0 | 0 | 0
5.3.4 | 32A 5pin 3phase Industrial socket with plug top controlled by 32A TPN MCB - Rawpower |  | No. | 0 |  |  | 0 | 0 | 0
5.3.5 | 16 A,4P, Isolator controlled by MCB |  | No. | 0 |  |  | 0 | 0 | 0
5.3.6 | 40A,4P,I solator controlled by MCB |  | No. | 0 |  |  | 0 | 0 | 0
5.3.7 | 63A,4P, Isolator controlled by MCB |  | No. | 0 |  |  | 0 | 0 | 0
5.4 | Data Backbox
5.4.1 | 2 Module GI back box for data,TV, HDMI outlets in partions |  | No. | 95 |  |  | 0 | 0 | 0
5.5 | Power Strip
5.5.1 | Power Provision for Power strip with 2 Round Power socket with 800 length - Meeting Rooms ( Sockets are part of furniture vendor scope) |  | No. | 1 |  |  | 0 | 0 | 0
5.5.2 | Power Provision for Power strip with 3 Round Power socket with 1200 length - Meeting Rooms (Sockets are part of furniture vendor scope) |  | No. | 4 |  |  | 0 | 0 | 0
6 | POINT WIRING
LIGHT POINTS
Supply, installation, testing & commissioning of light points using 1100V, 3Rx1.5Sqmm FRLS multi-strand copper conductor wire in 20mm Dia 2mm thick FRLS MS Conduit, ISI marked & specified type switches, metal boxes and accessories. The point wiring shall be terminated in a terminal block inside the junction box. Point wiring shall commence from the control box to light points. The quoted rate shall be inclusive of conduits with bush adapter for light fixture connection wherever required. All switches & accessories shall be covered with removable film coat to protect from scratches and paint. Black Colour Conduit - Lighting Green Conduit - Emergency Lighting
A | Switch control
Primary Point
I. Primary light point means wiring from first switch control to the first light outlet. The switch and all necessary accessories would be part of primary point.
| 3 core PVC transparent clear electrical cable flex cable shall be included at the drop of light fixture, flexibles with connectors and adaptors |  | No. | 70 |  |  | 0 | 0 | 0
Secondary Point
I. Secondary light point means extension of light outlet from existing primary point with 20mm dia MS conduit with 3Cx2.5Sq.mm FRLS cable 1100V with 20mm dia MS conduit. Same to be controlled by the existing switch of primary point. (Looping from the Secondary points to the sensors also to be included)
| 3 core PVC transparent clear electrical cable flex cable shall be included at the drop of light fixture. |  | No. | 330 |  |  | 0 | 0 | 0
B | MCB control
Supply, installation, testing & commissioning of light points using 1100V, 3Rx1.5Sqmm FRLS multi-strand copper conductor wire in 20mm Dia 2mm thick FRLS PVC Conduit, ISI marked. The cost for MCB & wiring from DB to first light point shall not be included. Black Colour Conduit - Lighting & Emergency Lighting
Secondary Point
| I. Secondary light point means extension of light outlet from existing primary point with ceiling rose & complete accessories. Same to be controlled by the existing MCB in DB |  | No. | 6 |  |  | 0 | 0 | 0
7 | CABLE TRAYS
Slotted angle Hot Dip Galvanized - GI (65 - 70 Micron as per IS2629) ready made cable trays of 14SWG. Quoted rates for installation shall include necessary anchor fasteners / 'L' angle supports @ 1200mm interval & all accessories, etc., to suit site conditions. Tray shall be made out of 2mm thick sheet, standard length 2.5mtr GI coupler plate 2.5 mm thick with eight holes and 8 nos. 1 1/2' x 3/8 GI passivated nut bolts with 2 no's plain washers & GI clamp for tray fixing along with GI hardware.
7.1 | Ladder type cable tray
7.1.1 | 750 x 75mm Size |  | M | 0 |  |  | 0 | 0 | 0
7.1.2 | 600 x 50mm Size |  | M | 0 |  |  | 0 | 0 | 0
7.1.3 | 450 x 50mm Size |  | M | 0 |  |  | 0 | 0 | 0
7.1.4 | 300 x 50mm Size |  | M | 0 |  |  | 0 | 0 | 0
7.1.5 | 200 x 50mm Size |  | M | 0 |  |  | 0 | 0 | 0
7.1.6 | 150 x 50mm Size |  | M | 0 |  |  | 0 | 0 | 0
7.1.7 | 100 x 50mm Size |  | M | 0 |  |  | 0 | 0 | 0
7.2 | Perforated Type Cable tray with cover (For LT Cables & Communication Cables)
Supply, installation, testing & commissioning of 2 mm Powder quoted Galvanized - GI (65 - 70 Micron as per IS2629) perforated type cable tray complete with all necessary coupler plates, elbows, tees, bends, reducers, stiffeners, grip/Anchor bolts or fasteners and other accessories and hardware need to be considered. Also the Quoted rate shall be inclusive of all hardware i.e. bolts, nuts, screws. washers, etc. Tray shall be made out of 2mm thick sheet, standard length 2.5mtr GI coupler plate 2.5 mm thick with eight holes and 8 nos. 1 1/2' x 3/8 GI passivated nut bolts with 2 no's plain washers & GI clamp for tray fixing along with GI hardware.
1.The quoted rate for the cable tray size up to 450mm shall be inclusive of suitable size threaded rod with suitable "C" channel at every 1000 mm interval of supports.
2.The quoted rate for above 450mm cable tray shall be with 25X25X5 mm thick MS angles at every 1000 mm interval of support.
3.Colour of the tray should be as per Interior views / Finalised by Architects during GFC stage
7.2.1 | 1000 x 75mm Size |  | M | 0 |  |  | 0 | 0 | 0
7.2.2 | 750 x 75mm Size |  | M | 0 |  |  | 0 | 0 | 0
7.2.3 | 600 x 50mm Size |  | M | 0 |  |  | 0 | 0 | 0
7.2.4 | 450 x 50mm Size |  | M | 25 |  |  | 0 | 0 | 0
7.2.5 | 300 x 50mm Size |  | M | 50 |  |  | 0 | 0 | 0
7.2.6 | 200 x 50mm Size |  | M | 100 |  |  | 0 | 0 | 0
7.2.7 | 150 x 50mm Size |  | M | 30 |  |  | 0 | 0 | 0
7.2.8 | 100 x 50mm Size |  | M | 0 |  |  | 0 | 0 | 0
7.2.9 | 80 x 50mm Size |  | M | 0 |  |  | 0 | 0 | 0
7.3 | Perforated Type with Cover (For Lighting Cables) | [7 empty] | 0
Supply, installation, testing & commissioning of 2 mm Powder quoted Galvanized - GI(65 - 70 Micron as per IS2629) perforated type cable tray complete with all necessary coupler plates, elbows, tees, bends, reducers, stiffeners, grip/Anchor bolts or fasteners and other accessories and hardware need to be considered. Also the Quoted rate shall be inclusive of all hardware i.e. bolts, nuts, screws. washers, etc. Tray shall be made out of 2mm thick sheet, standard length 2.5mtr GI coupler plate 2.5 mm thick with eight holes and 8 nos. 1 1/2' x 3/8 GI passivated nut bolts with 2 no's plain washers & GI clamp for tray fixing along with GI hardware.
1.The quoted rate for the cable tray size up to 450mm shall be inclusive of suitable size threaded rod with suitable "C" channel at every 1000 mm interval of supports.
2.The quoted rate for above 450mm cable tray shall be with 25X25X5 mm thick MS angles at every 1000 mm interval of support.
3.Colour of the tray should be as per Interior views / Finalised by Architects during GFC stage
7.3.1 | 300 x 100mm Size |  | M | 0 |  |  | 0 | 0 | 0
7.3.2 | 200 x 100mm Size |  | M | 0 |  |  | 0 | 0 | 0
7.3.3 | 150 x 50mm Size |  | M | 100 |  |  | 0 | 0 | 0
7.3.4 | 50 x 50mm Size |  | M | 0 |  |  | 0 | 0 | 0
7.4 | Basket Tray (For SERVER Room - Network cables)
Providing and Fixing of Cabloffill wire mesh cable tray system made out of Electrozinc Steel Wire Cable trays [As per ISO-20-81/82, NF/EN-12-329, DIN 50961] and bent into final shape , All cable trays, shall be manufactured with a longitudinal ‘T-welded’ safety edge and Trays shall be constructed with a 50 mm x 100 mm mesh configuration complete with couplers, C mountings and all accessories as required.
Note: The rate shall include all necessary supporting structure using appropriate L angles/ Channels etc for the tray size.
7.4.1 | 300 mm wide x 100 mm depth x 4 mm dia Cablofil |  | M | 20 |  |  | 0 | 0 | 0
7.4.2 | 400 mm wide x 100 mm depth x 4 mm dia Cablofil |  | M | 0 |  |  | 0 | 0 | 0
7.4.3 | 500 mm wide x 100 mm depth x 4 mm dia Cablofil |  | M | 0 |  |  | 0 | 0 | 0
8 | RACEWAYS
Supply & Installation of following size Pregalvanized - GI raceway / wire way with cover, made out of 16 SWG for body and 14 SWG for cover. Junction boxes to be provided with enough supports inside the box. Raceway installed above false ceiling/floor shall include necessary mounting supports, junction boxes and accessories to fix it firmly to the ground/ ceiling. The raceways shall be fixed to the floor with GI/MS (25mm x 3mm) strips so that there is no movement of the channels when civil work (pouring of cement concrete) is being done. Rate includes necessary floor cutting and chipping with machine of minimum 50mm depth, removal of debris out of site and neatly finished with M15 grade concrete up to the finished floor level. Race ways to be covered with Chicken mesh before concreting. Curing compound to be applied after initial setting of the concrete. All edges, cut faces shall be free of burrs & shall be smooth. The channels shall be earthed at the boxes and at the joints with 14 SWG bare copper wire with screws so that earth is continuous. Jointing of the race ways to be done with welding.
8.1 | Junction boxes
8.1.1 | Junction Boxes - Power
8.1.1a | 410 x 410 x 50mm Size |  | No. | 0 |  |  | 0 | 0 | 0
8.1.1b | 310 x 310 x 50mm Size |  | No. | 5 |  |  | 0 | 0 | 0
8.1.1c | 260 x 260 x 50mm Size |  | No. | 0 |  |  | 0 | 0 | 0
8.1.1d | 210 x 210 x 50mm Size |  | No. | 5 |  |  | 0 | 0 | 0
8.1.1e | 160 x 160 x 50mm Size |  | No. | 5 |  |  | 0 | 0 | 0
8.1.1f | 110 x 110 x 50mm Size |  | No. | 3 |  |  | 0 | 0 | 0
8.1.1g | 90 x 90 x 50mm Size |  | No. | 53 |  |  | 0 | 0 | 0
8.1.2 | Junction Boxes - Network
8.1.2a | 460 x 460 x 50mm Size |  | No. | 0 |  |  | 0 | 0 | 0
8.1.2b | 410 x 410 x 50mm Size |  | No. | 4 |  |  | 0 | 0 | 0
8.1.2c | 310 x 310 x 50mm Size |  | No. | 0 |  |  | 0 | 0 | 0
8.1.2d | 260 x 260 x 50mm Size |  | No. | 0 |  |  | 0 | 0 | 0
8.1.2e | 210 x 210 x 50mm Size |  | No. | 5 |  |  | 0 | 0 | 0
8.1.2f | 160 x 160 x 50mm Size |  | No. | 10 |  |  | 0 | 0 | 0
8.1.2g | 110 x 110 x 50mm Size |  | No. | 3 |  |  | 0 | 0 | 0
8.1.2h | 90 x 90 x 50mm Size |  | No. | 35 |  |  | 0 | 0 | 0
8.2 | Floor Raceways
Supply & Installation of following size Tubular Pre galvanised raceway , made out of 16 SWG GI.
8.2.1 | Floor Raceways - Power
8.2.1a | 300 x 40mm Size |  | M | 0 |  |  | 0 | 0 | 0
8.2.1b | 250 x 40mm Size |  | M | 0 |  |  | 0 | 0 | 0
8.2.1c | 200 x 40mm Size |  | M | 0 |  |  | 0 | 0 | 0
8.2.1d | 150 x 40mm Size |  | M | 15 |  |  | 0 | 0 | 0
8.2.1e | 100 x 40mm Size |  | M | 10 |  |  | 0 | 0 | 0
8.2.1f | 80 x 40mm Size |  | M | 40 |  |  | 0 | 0 | 0
8.2.2 | Floor Raceways - Network
8.2.2a | 450 x 40mm Size |  | M | 0 |  |  | 0 | 0 | 0
8.2.2b | 400 x 40mm Size |  | M | 5 |  |  | 0 | 0 | 0
8.2.2c | 300 x 40mm Size |  | M | 0 |  |  | 0 | 0 | 0
8.2.2d | 250 x 40mm Size |  | M | 0 |  |  | 0 | 0 | 0
8.2.2e | 200 x 40mm Size |  | M | 20 |  |  | 0 | 0 | 0
8.2.2f | 150 x 40mm Size |  | M | 20 |  |  | 0 | 0 | 0
8.2.2g | 100 x 40mm Size |  | M | 20 |  |  | 0 | 0 | 0
8.2.2h | 80 x 40mm Size |  | M | 60 |  |  | 0 | 0 | 0
8.2.2i | PVC trunk-100 x 50mm - similar to MK make |  | M | 0 |  |  | 0 | 0 | 0
8.3 | Ceiling Raceways
Supply & Installation of following size Powder Quoted Galvanized - GI (65 - 70 Micron as per IS2629) raceway / wire way with cover, made out of 14 SWG GI for body and 14 SWG GI for cover. Junction boxes to be provided with enough supports inside the box. Raceway installed above false ceiling shall include necessary mounting supports, junction boxes and accessories to fix it firmly to the ceiling. All edges, cut faces shall be free of burrs & shall be smooth. The channels shall be earthed at the boxes and at the joints with 14 SWG bare copper wire with screws so that earth is continuous. Jointing of the race ways to be done using fisher plates & 'Slotted Channel' angle supports @ 600mm interval etc., to suit site conditions.
Colour of the tray should be as per Interior views / Finalised by Architects during GFC stage
Junction boxes
Supply & Installation of following size junction boxes, made out of 14 SWG Powder quoted Galvanized - GI (65 - 70 Micron as per IS2629) for body and cover.
8.3.1 | Junction Boxes - Power
8.3.1a | 410 x 410 x 50mm Size |  | No. | 0 |  |  | 0 | 0 | 0
8.3.1b | 310 x 310 x 50mm Size |  | No. | 6 |  |  | 0 | 0 | 0
8.3.1c | 260 x 260 x 50mm Size |  | No. | 0 |  |  | 0 | 0 | 0
8.3.1d | 210 x 210 x 50mm Size |  | No. | 3 |  |  | 0 | 0 | 0
8.3.1e | 160 x 160 x 50mm Size |  | No. | 0 |  |  | 0 | 0 | 0
8.3.1f | 110 x 110 x 50mm Size |  | No. | 0 |  |  | 0 | 0 | 0
8.3.1g | 90 x 90 x 50mm Size |  | No. | 14 |  |  | 0 | 0 | 0
8.3.2 | Junction Boxes - Network
8.3.2a | 460 x 460 x 50mm Size |  | No. | 0 |  |  | 0 | 0 | 0
8.3.2b | 410 x 410 x 50mm Size |  | No. | 0 |  |  | 0 | 0 | 0
8.3.2c | 310 x 310 x 50mm Size |  | No. | 0 |  |  | 0 | 0 | 0
8.3.2d | 260 x 260 x 50mm Size |  | No. | 0 |  |  | 0 | 0 | 0
8.3.2e | 210 x 210 x 50mm Size |  | No. | 0 |  |  | 0 | 0 | 0
8.3.2f | 160 x 160 x 50mm Size |  | No. | 5 |  |  | 0 | 0 | 0
8.3.2g | 110 x 110 x 50mm Size |  | No. | 0 |  |  | 0 | 0 | 0
8.3.2h | 90 x 90 x 50mm Size |  | No. | 0 |  |  | 0 | 0 | 0
8.4 | Ceiling Raceways - Power
8.4.1 | Supply & Installation of following size raceway, made out of 14 SWG Powder quoted - GI (65 - 70 Micron as per IS2629).
Colour of the tray should be as per Interior views / Finalised by Architects during GFC stage
8.4.1a | 400 x 40mm Size |  | M | 0 |  |  | 0 | 0 | 0
8.4.1b | 300 x 40mm Size |  | M | 20 |  |  | 0 | 0 | 0
8.4.1c | 250 x 40mm Size |  | M | 0 |  |  | 0 | 0 | 0
8.4.1d | 200 x 40mm Size |  | M | 15 |  |  | 0 | 0 | 0
8.4.1e | 150 x 40mm Size |  | M | 0 |  |  | 0 | 0 | 0
8.4.1f | 100 x 40mm Size |  | M | 0 |  |  | 0 | 0 | 0
8.4.1g | 80 x 40mm Size |  | M | 60 |  |  | 0 | 0 | 0
8.4.2 | Ceiling Raceways - Network
8.4.2a | 450 x 40mm Size |  | M | 0 |  |  | 0 | 0 | 0
8.4.2b | 400 x 40mm Size |  | M | 0 |  |  | 0 | 0 | 0
8.4.2c | 300 x 40mm Size |  | M | 0 |  |  | 0 | 0 | 0
8.4.2d | 250 x 40mm Size |  | M | 0 |  |  | 0 | 0 | 0
8.4.2e | 200 x 40mm Size |  | M | 0 |  |  | 0 | 0 | 0
8.4.2f | 150 x 40mm Size |  | M | 0 |  |  | 0 | 0 | 0
8.4.2g | 100 x 40mm Size |  | M | 0 |  |  | 0 | 0 | 0
8.4.2h | 80 x 40mm Size |  | M | 0 |  |  | 0 | 0 | 0
8.5 | Floor Raceways
8.5.1 | 600 x 100mm Size |  | M | 0 |  |  | 0 | 0 | 0
8.5.2 | 500 x 100mm Size |  | M | 0 |  |  | 0 | 0 | 0
8.5.3 | 300 x 100mm Size |  | M | 0 |  |  | 0 | 0 | 0
8.6 | Supply & Installation of following size Powder coated raceway made out of 16 SWG GI/MS for body and 14 SWG GI/MS for cover. - The shade shall be as per site approval Minimum 2 colours need to be considered in the Quote. Colour will be finalised as per IT team requirement.
Vendor need to take confirmation from Architect/Consultant team before procuring the above line iteam.
8.6.1 | 300 x 150mm Size |  | M | 0 |  |  | 0 | 0 | 0
8.6.2 | 150 x 150mm Size |  | M | 0 |  |  | 0 | 0 | 0
8.6.3 | 100 x 150mm Size |  | M | 0 |  |  | 0 | 0 | 0
8.7 | Raceways for AV
Supply & Installation of following size Hot Dip Galvanized - GI (65 - 70 Micron as per IS2629) raceway / wire way with cover, made out of 16 SWG GI for body and 14 SWG GI for cover. Junction boxes to be provided with enough supports inside the box. Raceway installed above false ceiling/floor shall include necessary mounting supports, junction boxes and accessories to fix it firmly to the ground/ ceiling. The raceways shall be fixed to the floor with GI strips so that there is no movement of the channels when civil work (pouring of cement concrete) is being done. All edges, cut faces shall be free of burrs & shall be smooth. The channels shall be earthed at the boxes and at the joints with 14 SWG bare copper wire with screws so that earth is continuous. Jointing of the race ways to be done with welding.
8.7.1 | 300 x 40mm Size |  | M |  |  |  | 0 | 0 | 0
8.7.2 | 150 x 40mm Size |  | M | 30 |  |  | 0 | 0 | 0
8.7.3 | 100 x 40mm Size |  | M |  |  |  | 0 | 0 | 0
8.8 | Supply & Laying of following size ISI Marked MS CONDUITs.Rate shall include wall chasing & rough plastering, clamping / fixing arrangement.
8.8.1 | 32mm dia - For Network |  | M | 200 |  |  | 0 | 0 | 0
8.8.2 | 25mm dia - For Power |  | M | 500 |  |  | 0 | 0 | 0
8.8.3 | 20mm dia |  | M | 200 |  |  | 0 | 0 | 0
8.8.4 | Flexble Conduit 25mm |  | M | 50 |  |  | 0 | 0 | 0
8.8.5 | Flexble Conduit 20mm |  | M | 50 |  |  | 0 | 0 | 0
8.8.6 | 50 x 50 mm Casing & Caping |  | M | 0 |  |  | 0 | 0 | 0
8.8.7 | 40 mm width chipping and refilling to lay the conduit in floor |  | M | 0 |  |  | 0 | 0 | 0
9 | EARTHING
9.1 | EARTH ELECTRODES
9.1.1 | GI Pipe Electrode Earthing System
| Pipe Earth Electrode using 38 mm dia class B GI pipe complete as per IS 3043 with salt, charcoal, brick masonary chamber with heavy duty RCC cover (suitable to take fire tender load) tender truckmovement) of 450mm x 450mm x 300mm chamber.(Earth strip to be left upto the Earthpit for Connection) |  | No. |  |  |  | 0 | 0 | 0
9.1.2 | Copper plate Electrode Earthing System
| Plate Earth Electrode using 19 mm dia Class B copper plate of size 600 x 600 x 3 mm thick.with heavy duty RCC cover (suitable to take fire tender truck load) of 450mm x 450mm x 300mm chamber.(Earth strip to be left upto the Earthpit for Connection) |  | No. |  |  |  | 0 | 0 | 0
9.1.3 | Maintenance Free Copper Pipe Electrode Earthing System
| Providing, installing, testing and commissioning of maintance free earthing station including the following items 1.400(L)x400(W)x450(D)mm, 150mm thick block work inspection chamber with CI Cover/ Lid. 2.25x 6 Cu Strips links for main connection of Pipe with external strips inside the chamber with exothermic welding. 3. 20mm dia Copper Pipe 4. 40Kg Chemical earth enhancing material System shall be in full compliance with IS:3043 Earthing Standards/ NBC 2016 (latest). 5. Cost to include necessary excavation to an extent of 400(W & L), back filling around the Rod/ Pipe. |  | No. |  |  |  | 0 | 0 | 0
9.2 | EARTH STRIPS
GI/Cu earth strips on cable tray or below ground as per site condition. All Cu. Strips shall be run in pvc heat shrinkable sleeve & mounted on insulation mounts. Cost of civil works shall be included for strips laid below ground.
9.2.1 | 6 Sq.mm Copper Wire |  | M | 0 |  |  | 0 | 0 | 0
9.2.2 | 4 Sq.mm Copper Wire |  | M | 0 |  |  | 0 | 0 | 0
9.2.3 | 25 x 3mm GI Earth flat |  | M | 150 |  |  | 0 | 0 | 0
9.2.4 | 25 x 6mm GI Earth flat |  | M | 300 |  |  | 0 | 0 | 0
9.2.5 | 25 x 10mm GI Earth flat |  | M | 0 |  |  | 0 | 0 | 0
9.2.6 | 50 x 6mm GI Earth flat |  | M | 0 |  |  | 0 | 0 | 0
9.2.7 | 50 x 10mm GI Earth flat |  | M | 0 |  |  | 0 | 0 | 0
9.2.8 | 25 x 3mm Cu Earth flat |  | M | 0 |  |  | 0 | 0 | 0
9.2.9 | 25 x 6mm Cu Earth flat |  | M | 0 |  |  | 0 | 0 | 0
9.3 | XLPE Insulated Copper Conductor Unarmoured Cables (2XY Type)
1.1kV grade, copper conductor, XLPE insulated, unarmoured, power cables. The cables shall be laid on tray / hume pipe /in ready made trenches, with nylon cable ties / MS Clamps @ 600mm interval etc., as required. Rate quoted shall exclude cost of tray. Cost of civil works like earth escavation & refilling shall be included for strips laid below ground. and cable dessing and tagging to be done properly
9.3.1a | 1 Core x 150 Sq. mm |  | M | 0 |  |  | 0 | 0 | 0
9.3.1b | End terminations |  | Nos | 0 |  |  | 0 | 0 | 0
9.3.1a | 1 Core x 70 Sq. mm |  | M | 0
9.3.1b | End terminations |  | Nos | 0
9.3.1a | 1 Core x 50 Sq. mm |  | M | 0 |  |  | 0 | 0 | 0
9.3.1b | End terminations |  | Nos | 0 |  |  | 0 | 0 | 0
9.3.1a | 1 Core x 35 Sq. mm |  | M | 0 |  |  | 0 | 0 | 0
9.3.1b | End terminations |  | Nos | 0 |  |  | 0 | 0 | 0
9.3.2a | 1 Core x 25 Sq. mm |  | M | 0 |  |  | 0 | 0 | 0
9.3.2b | End terminations |  | Nos | 0 |  |  | 0 | 0 | 0
9.3.3a | 1 Core x 16 Sq. mm |  | M | 150 |  |  | 0 | 0 | 0
9.3.3b | End terminations |  | Nos | 8 |  |  | 0 | 0 | 0
9.3.4a | 1 Core x 10 Sq. mm |  | M | 0 |  |  | 0 | 0 | 0
9.3.4b | End terminations |  | Nos | 0 |  |  | 0 | 0 | 0
9.3.5a | 1 Core x 6 Sq. mm |  | M | 150 |  |  | 0 | 0 | 0
9.3.5b | End terminations |  | Nos | 4 |  |  | 0 | 0 | 0
9.3.6a | 1 Core x 4Sq. mm |  | M | 200 |  |  | 0 | 0 | 0
9.3.6b | End terminations |  | Nos | 72 |  |  | 0 | 0 | 0
9.4 | Busbar of 0.5 Mtr length made out of 50x6 mm GI strip with drill holes of M8 at 25mm interval mounted on insulators. |  | No. | 0 |  |  | 0 | 0 | 0
9.5 | Busbar of 0.5 Mtr length made out of 25x6 mm GI strip with drill holes of M8 at 25mm interval mounted on insulators. |  | No. | 4 |  |  | 0 | 0 | 0
9.6 | Busbar of 0.5 Mtr length made out of 25x3 mm GI strip with drill holes of M8 at 25mm interval mounted on insulators. |  | No. | 0 |  |  | 0 | 0 | 0
9.7 | Busbar of 0.5 Mtr length made out of 25x3 mm Cu strip with drill holes of M8 at 25mm interval mounted on insulators. |  | No. | 0 |  |  | 0 | 0 | 0
9.8 | Busbar of 0.5 Mtr length made out of 25x6 mm Cu strip with drill holes of M8 at 25mm interval mounted on insulators. |  | No. | 3 |  |  | 0 | 0 | 0
9.9 | Bimetallic Connectors for Connecting Copper cable to GI Busbar |  | No. | 0 |  |  | 0 | 0 | 0
9.1 | Antistatic Earthing Mat with all interconnecting accessories |  | Sq. Mt. | 0 |  |  | 0 | 0 | 0
10 | Earthing Test shall be carried out and report should be shared with DLF |  | L/s | 1 |  |  | 0 | 0 | 0
10 | MISCELLANEOUS ITEMS
10.01 | Rubber mats of 1.1 KV grade 1.8 Mtrs x 0.9 Mtrs and of sufficient thickness as required by the Electrical Inspectorate and confirming to IS 15652 Class A along with expiry date. |  | No. | 8 |  |  | 0 | 0 | 0
10.02 | Shock treatment chart as approved by the Electrical Inspectorate mounted on teak wood frame and suitable for wall mounting. |  | No. | 2 |  |  | 0 | 0 | 0
10.03 | First aid kit |  | No. | 1 |  |  | 0 | 0 | 0
10.04 | Danger boards as per IS 2551 to mention voltage level in min three languages marked in red as per EB requirements. |  | No. | 2 |  |  | 0 | 0 | 0
10.05 | MS Fabricated Items |  | Kg. | 800 |  |  | 0 | 0 | 0
10.06 | Supply & fixing of rubber gloves of Approved Make & as per supply voltage |  | No. | 2 |  |  | 0 | 0 | 0
10.07 | A0 Laminated Schematic with glass frame |  | No | 1 |  |  | 0 | 0 | 0
10.08 | MS Powder coated pipe support to mount the Occupancy sensor in the office Area. Necessary hardwares to install the same need to consider in the quote. |  | No. | 12 |  |  | 0 | 0 | 0
10.09 | 2 hour fire rated fire retardant material sealing (UL Listed) all electrical ducts and openings made in the slab / wall / partition to take conduits / cable trays / raceways etc as required complete / as directed by the site incharge |  | Sqm. | 3 |  |  | 0 | 0 | 0
10.1 | 150mm wide x 100mm depth 18G DB cabinet MS Powder coated including supply & installation. |  | Rm | 30 |  |  | 0 | 0 | 0
10.11 | Construction Power related Works including Panel, Isolator, Sockets, Light fixture, Cable, Wires & Earthing etc |  | LS | 1 |  |  | 0 | 0 | 0
10.12 | Professional Charges: CEIG Inspection : Professional charges towards filing application, preparation of drawings in necessary formats for approval, follow up and arranging approval of drawings, scheme by Local electricity authority / Electrical Inspectorate, obtaining clearance from electricity authority / Electrical Inspectorate. |  | LS | 1 |  |  |  | 0 | 0
10.13 | As built drawings
| Preparation and Submission of as built drawings, (3 sets of hard copies and soft copy in a CD) 1. Schematic distribution diagram 2. Floor plans 3. Reflected ceiling plans if any. 4. Earthing schemes and plans. and other related drawings. |  | LS | 1 |  |  | 0 | 0 | 0
[7 empty] | 0 | 0 | 0

## DB QA
Sl No | DB |  | MAIN INCOMER |  | SUB INCOMER |  | OUTGOING
| DB Name | Qty | TYPE/SIZE | QTY | TYPE | QTY | TYPE | QTY | DB Name | Qty
1 | 4Tier 56Module TPN DB - LDB | 3 | 40A MCB FP C-CURVE | 3 | 40A 30mA RCBO | 9 | 16A 30mA RCCB | 18 | 4 Tier 56 Module | 3
2 | 16Way SPN DB - ELDB | 1 | 40A DP MCB C-CURVE | 1 |  |  | 10A 30mA RCCB | 7 | 16 Way SPN | 1
3 | 4Tier 56Module TPN DB - RDB | 2 | 63A MCB FP C-CURVE | 2 | 40A 30mA RCCB | 6 | 16A 30mA RCCB | 18 | 4 Tier 56 Module | 2
4 | 4Tier 40Module TPN DB - RDB | 1 | 63A MCB FP C-CURVE | 1 | 40A 30mA RCCB | 3 | 16A 30mA RCCB | 12 | 4 Tier 40 Module | 1
5 | 4Tier 56Module TPN DB - UDB | 2 | 63A MCB FP D-CURVE | 2 | 40A 30mA RCCB | 6 | 16A 30mA RCCB | 18 | 4 Tier 56 Module | 2
| 6 WAY TPN - SDB | 2 | 63A MCB FP C-CURVE | 2 | 40A 30mA RCCB | 6 | 32A 30mA RCCB | 9 | 6 Way TPN | 2
| 6 Way VTPN DB | 1 | 40A MCB TP C-CURVE | 1 |  |  | 40A MCB TP C-CURVE | 6 | 6 Way VTPN | 1
|  | 12 |  | 12 |  | 30 |  | 88 |  | 12

## Light fixture
| PROJECT : | M/s SIEMENS HEALTHINEERS, GURGAON
| SUBJECT : | BILL OF QUANTITIES FOR LIGHTING SYSTEM
| CONSULT : | E SOLLUTIONS
| DATE : | 2025-08-28
| REVISION: | R0
Sl No. | Ref No. | Description | Areas | Fixture Image | UOM | Unit Load (W) | Qty | Supply Rate | Installation Rate | Supply Amount | Installation Amount | Total Amount (INR) | REMARKS
| A | Task Light Fixtures |  |  |  |  | 456
1 | CL-02 | 10W/M LED Neon Strip Light with Al.Channel, 4000K, IP20, Non Dimmable , Flicker Free Driver with Surge Protection Device, IP20 LED Lifespan L80@50000 H; CRI > 90; UGR≤19; 3 or Less SDCM. Lm Flux > 100 lm/W Installation: The LED Strips to be supplied with Al channel and Cover. Size: L- As per the drawing, W-16mm , H-16mm | Reception |  | Mtr's | 10 | 28 |  |  | 0 | 0 | 0
2 | CL-03 | 10W/M LED Strip Light with Al.Channel, 3000K, IP20, Non Dimmable , Flicker Free Driver with Surge Protection Device, IP20 LED Lifespan L80@50000 H; CRI > 90; UGR≤19; 3 or Less SDCM. Lm Flux > 100 lm/W Installation: The LED Strips to be supplied with Al channel and Cover. Size: L- As per the drawing , W-15mm , H-10mm | Wellness Room |  | Mtr's | 10 | 8 |  |  | 0 | 0 | 0
3 | CL-04 | 10W/M LED Linear Wall Grazer Light Fixture, 10° Distribution, 4000K, IP20, Dimmable (DALi 2 D4i)., Flicker Free Driver with Surge Protection Device, IP 20, LED Lifespan L80@50000 H; CRI > 90; UGR≤19; 3 or Less SDCM. Lm Flux > 100 lm/W Installation: Surface Mounted. The LED Strips to be supplied with Mounting Clips. Size: 20mm x 20mm, L - as per drawing | Arena, |  | Mtr's | 10 | 8 |  |  | 0 | 0 | 0
4 | CL-04a | 10W/M LED Linear Wall Grazer Light Fixture, 10° Distribution, 4000K, IP20, Non Dimmable ., Flicker Free Driver with Surge Protection Device, IP 20, LED Lifespan L80@50000 H; CRI > 90; UGR≤19; 3 or Less SDCM. Lm Flux > 100 lm/W Installation: Surface Mounted. The LED Strips to be supplied with Mounting Clips. Size: 20mm x 20mm, L - as per drawing | Corridor |  | Mtr's | 10 | 7 |  |  | 0 | 0 | 0
5 | CL-05 | 10W/M LED Strip Light with Al.Channel, 4000K, IP20, DALI Dimmable (DALi 2 D4i), Flicker Free Driver with Surge Protection Device, IP20 LED Lifespan L80@50000 H; CRI > 90; UGR≤19; 3 or Less SDCM. Lm Flux > 100 lm/W Installation: The LED Strips to be supplied with Al channel and Cover.Size : L- As per the drawing, W-15mm , H-10mm | 2Pax, 1Pax , Board Room , Worklounge, Printer , Booth Seating |  | Mtr's | 10 | 38 |  |  | 0 | 0 | 0
6 | CL-05a | 10W/M LED Strip Light with Al.Channel, 4000K, IP20, Non Dimmable, Flicker Free Driver with Surge Protection Device, IP20 LED Lifespan L80@50000 H; CRI > 90; UGR≤19; 3 or Less SDCM. Lm Flux > 100 lm/W Installation: The LED Strips to be supplied with Al channel and Cover.Size : L- As per the drawing, W-15mm , H-10mm | 2Pax, 1Pax ,Printer,Booth Seating |  | Mtr's | 10 | 26 |  |  | 0 | 0 | 0
7 | CL-06 | 5W/M LED Strip Light with Al.Channel, 4000K, IP20, Non Dimmable (DALi 2 D4i) , Flicker Free Driver with Surge Protection Device, IP20 LED Lifespan L80@50000 H; CRI > 90; UGR≤19; 3 or Less SDCM. Lm Flux > 100 lm/W Installation: The LED Strips to be supplied with Al channel and Cover.Size : L- As per the drawing, W-15mm , H-10mm | Corridor |  | Mtr's | 5 | 8 |  |  | 0 | 0 | 0
8 | CL-07 | 10W/M LED Strip Light with Al.Channel, 4000K, IP20,Non Dimmable , Flicker Free Driver with Surge Protection Device, IP54 LED Lifespan L80@50000 H; CRI > 90; UGR≤19; 3 or Less SDCM. Lm Flux > 100 lm/W Installation: The LED Strips to be supplied with Al channel and Cover.Size : L- As per the drawing, W-15mm , H-10mm | Washrooms |  | Mtr's | 10 | 9.5 |  |  | 0 | 0 | 0
9 | R-01 | 10W LED Recessed Fixed Downlight Fixture with Darklight Reflector, 4000K, IP20, 60° Distribution, Dimmable (DALI 2 D4i ) , Flicker Free Driver with Surge Protection Device, LED Lifespan L80@50000 H; CRI > 90; UGR≤19; 3 or Less SDCM. Lm Flux - 100 lm/W Size : Dia - 93mm , H-95mm | Flex Room, 4 Pax, 6 Pax Meeting room , 4 Pax Hybrid Meeting Room |  | No's | 10 | 37 |  |  | 0 | 0 | 0
10 | R-01a | 10W LED Recessed Fixed Downlight Fixture with Darklight Reflector, 4000K, IP20, 60° Distribution, Non-Dimmable , Flicker Free Driver with Surge Protection Device, LED Lifespan L80@50000 H; CRI > 90; UGR≤19; 3 or Less SDCM. Lm Flux - 100 lm/W Size : Dia - 93mm , H-95mm | Reception , 4 Pax Visitor Meeting Room, Corridor , Printer |  | No's | 10 | 47 |  |  | 0 | 0 | 0
11 | R-02 | 15W LED Recessed Downlight Fixture, 3000K IP20, Diffused Distribution , Non Dimmable , Flicker Free Driver with Surge Protection Device, LED Lifespan L80@50000 H; CRI > 90; UGR≤19; 3 or Less SDCM. Lm Flux - 100 lm/W Size : Dia - 150mm , H-53mm | Wellness Room |  | No's | 15 | 7 |  |  | 0 | 0 | 0
12 | R-02a | 15W LED Recessed Downlight Fixture, 4000K IP20, Diffused Distribution , Non Dimmable , Flicker Free Driver with Surge Protection Device, LED Lifespan L80@50000 H; CRI > 90; UGR≤19; 3 or Less SDCM. Lm Flux - 100 lm/W Size : Dia - 150mm , H-53mm | Store Room |  | No's | 15 | 6 |  |  | 0 | 0 | 0
13 | R-03 | 10W LED Recessed Downlight Fixture, 4000K IP20, Diffused Distribution , Non Dimmable , Flicker Free Driver with Surge Protection Device, LED Lifespan L80@50000 H; CRI > 90; UGR≤19; 3 or Less SDCM. Lm Flux - 100 lm/W Size : Dia - 150mm , H-53mm | Washrooms |  | No's | 10 | 24 |  |  | 0 | 0 | 0
14 | S-01 | 30W/mtr Suspended Linear Direct/ Indirect Fixture (70% Direct and 30% Indirect) 4000K, Micro prismatic Diffuser, IP20, Dimmable (DALi 2 D4i). Flicker Free Driver with Surge Protection Device, LED Lifespan L80@50000 H; CRI > 90; UGR≤19; 3 or Less SDCM. Lm Flux - 110 lm/W; Size: Profile Length - 1400mm, W- 60 mm, H- 80mm | Workstation |  | No's | 30 | 20 |  |  | 0 | 0 | 0
15 | S-02 | 10W/m, LED Suspended/Surface Mount Rectangular Linear Sleek Profile Fixture with Curved Corners, Microprismatic Diffuser, 4000K, IP20, Dimmable (DALi 2 D4i). Flicker Free Driver with Surge Protection Device, LED Lifespan L80@50000 H; CRI > 90; UGR≤19; 3 or Less SDCM. Lm Flux - 100 lm/W; Size: Profile: Length x W:60mm, H:80mm. | Flex Room, 4 Pax, 6 Pax Meeting room, 4 Pax Hybrid Meeting Room |  | Mtrs | 10 | 32 |  |  | 0 | 0 | 0
16 | S-02a | 10W/m, LED Suspended/Surface Mount Rectangular Linear Sleek Profile Fixture with Curved Corners, Microprismatic Diffuser, 4000K, IP20,Non Dimmable . Flicker Free Driver with Surge Protection Device, LED Lifespan L80@50000 H; CRI > 90; UGR≤19; 3 or Less SDCM. Lm Flux - 100 lm/W; Size: Profile: Length x W:60mm, H:80mm. | Reception , 4 Pax Visitor Meeting Room |  | Mtrs | 10 | 20.5 |  |  | 0 | 0 | 0
17 | S-03 | 15W LED Pendant Cylindrical Fixture with Darklight Reflector, 4000K, IP20, 60° Distribution, Dimmable (DALI 2 D4i) , Flicker Free Driver with Surge Protection Device, LED Lifespan L80@50000 H; CRI > 90; UGR≤19; 3 or Less SDCM. Lm Flux - 100 lm/W. Size : Dia- 80mm, H- 125- 150mm | Open Office, Open Collab, Teams Table |  | No's | 15 | 40 |  |  | 0 | 0 | 0
18 | S-04 | 15W, LED Surface Mounted Multispot Fixture, 60 Deg Distribution, 4000K, IP20, Non Dimmable. Flicker Free Driver with Surge Protection Device, LED Lifespan L80@50000 H; CRI > 90; UGR≤19; 3 or Less SDCM. Lm Flux - 100 lm/W; Size: Profile: Length: 164mm, Width:51mm , Height-90mm . | Corridor |  | No's | 15 | 40 |  |  | 0 | 0 | 0
19 | S-05 | 20W/ mtr, LED Suspended Linear Fixture with microprismatic diffuser, 4000K, IP20, Dimmable (DALi 2 D4i). Flicker Free Driver with Surge Protection Device, LED Lifespan L80@50000 H; CRI > 90; UGR≤19; 3 or Less SDCM. Lm Flux - 100 lm/W; Size: Profile: Length x Width: 60mm, Height- 80mm. | Board Room |  | Mtrs | 20 | 12 |  |  | 0 | 0 | 0
20 | S-06 | 36W/4ft Suspended LED Batten Light Fixture, Diffused Distribution, 4000K, Non Dimmable, SDCM≤3, Life Span - L70@50000H. Driver: Non Dimmable , Flicker free With < 3%. | AHU Room , UPS , Battery Room , Network Room |  | No's | 36 | 20 |  |  | 0 | 0 | 0
21 | S-07 | 2 x 8W, LED Suspended Mount Twin Downlight Fixture with Al reflector, 60 Deg Distribution, 4000K, IP20, DALI Dimmable(DALI 2 D4i). Flicker Free Driver with Surge Protection Device, LED Lifespan L80@50000 H; CRI > 90; UGR≤19; 3 or Less SDCM. Lm Flux - 100 lm/W; Size: W 80mm, H 90mm, L 148mm | Arena |  | No's | 12 | 9 |  |  | 0 | 0 | 0
22 | S-09 | 15W LED Surface Cylindrical Fixture with Darklight Reflector, 4000K, IP20, 60° Distribution, Dimmable (DALI 2 D4i) , Flicker Free Driver with Surge Protection Device, LED Lifespan L80@50000 H; CRI > 90; UGR≤19; 3 or Less SDCM. Lm Flux - 100 lm/W, Fixture with inbuilt driver. Installation: Safety Cable is must. Size : Dia- 80mm, H- 90mm- 120mm | Work Lounge |  | No's | 15 | 9 |  |  | 0 | 0 | 0
23 | BL-01 | SITC of Backlit Stretch Fabric, 4.5W/Sq Ft, LED Backlit Module, Stretch Fabric customized as per ceiling design, 4000K, IP20, Dimmable (DALI 2 D4i) , Flicker Free Driver with Surge Protection Device, LED Lifespan L80@50000 H; CRI > 90; UGR≤19; 3 or Less SDCM. Lm Flux - 100 lm/W. Note: Vendor to provide complete supply and installation of Stretch Fabric, Wooden/Metal Boxing, LED, Driver etc. | Project Room |  | Sq Ft | 15 | consider in C&I BOQ
|  | Total for Task Lights: | [9 empty] | 0
| B | Decorative Light Fixtures
24 | D-02 | 10W LED Decorative Wall Scones , 4000K, IP20, Non Dimmable , LED Lifespan L80@50000 H; CRI > 90; 3 or Less SDCM. Lm Flux > 100 lm/W, Installation: Wall Mounted , Size: Dia - 300mm, H- 90mm | 2 Pax , 1 Pax Meeting Room, Phone Booth |  | No's | 10 | 3 |  |  | 0 | 0 | 0
1 | D-03 | 10W LED Decorative Hanging Globe Pendant Light Fixture , 4000K IP20, Dimmable (DALI 2 D4i) ; LED Lifespan L80@50000 H; CRI > 90; 3 or Less SDCM. Lm Flux > 100 lm/W, Installation: Suspended Size: Dia- 250mm | Team Zone |  | No's | 10 | removed qty | [5 empty] | Type of product to be finalized based on approval on Architect's intent.
1 | D-03 (Option 2) | 15W/M LED Decorative Linear Pendant Light Fixture with tubular source, 4000K IP20, Dimmable (DALI 2 D4i); LED Lifespan L80@50000 H; CRI > 90; 3 or Less SDCM. Lm Flux > 100 lm/W, Installation: Suspended Size: 1.5m Length | Team Zone |  | No's | 10 | 2 |  |  | 0 | 0 | 0
1 | D-04 | 20W LED Decorative Hanging Globe Pendant Light Fixture, 4000K IP20, Dimmable (DALI 2 D4i) ; LED Lifespan L80@50000 H; CRI > 90; 3 or Less SDCM. Lm Flux > 100 lm/W, Installation: Rod Suspended. Size: Dia- 300mm | Work Lounge |  | No's | 20 | 4 |  |  | 0 | 0 | 0
1 | D-05 | 150W LED Decorative Acosutic Hanging Box Light Fixture with fluted edges, 4000K IP20, DALI Dimmable (DALI 2 D4i) ; LED Lifespan L80@50000 H; CRI > 90; 3 or Less SDCM. Lm Flux > 100 lm/W, Installation: Suspended Size: Dia- L- 2920mm, W- 900mm | Workstation |  | No's | 150 | 2 |  |  | 0 | 0 | 0
25 | D-06 | 30W LED Decorative Acoustic Pendant Light Fixture , 4000K IP20, Dimmable (DALI 2 D4i) ; LED Lifespan L80@50000 H; CRI > 90; 3 or Less SDCM. Lm Flux > 100 lm/W, Installation: Suspended Size: Dia- 600mm | Ope Collab |  | No's | 30 | 2 |  |  | 0 | 0 | 0
2 | D-07 | 30W LED Decorative Acoustic Pendant Light Fixture , 4000K IP20, Dimmable (DALI 2 D4i) ; LED Lifespan L80@50000 H; CRI > 90; 3 or Less SDCM. Lm Flux > 100 lm/W, Installation: Suspended Size: Dia- 600mm | Ope Collab |  | No's | 30 | 1 |  |  | 0 | 0 | 0
2 | D-08 | 10W LED Decorative Hanging Globe Pendant Light Fixture, 3000K IP20, Non Dimmable ; LED Lifespan L80@50000 H; CRI > 90; 3 or Less SDCM. Lm Flux > 100 lm/W, Installation: Rod Suspended. Size: Dia- 300mm | Wellness Room |  | No's | 10 | removed qty
2 | D-09 | 10W LED Decorative Hanging Globe Light Fixture, 4000K, IP20, Non Dimmable , LED Lifespan 50000 H; CRI > 90; 3 or Less SDCM. Lm Flux > 60 lm/W, Installation: Suspended. Size- Dia - 140mm, H- 150mm | Washroom |  | No's | 10 | removed qty
2 | D-10 | 30W LED Ceiling Mounted 2x2 Light Fixture with Sidelit Diffuser with centre opening, 4000K, IP20, DALI Dimmable, LED Lifespan 50000 H; CRI > 90; 3 or Less SDCM. Lm Flux > 100 lm/W, Installation: on Acoustic Coffer Ceiling, Size- 600mm x 600mm. Note: Vendor to include acoustic panel to cover the centre opening. | Work Lounge |  | No's | 30 | 21 |  |  | 0 | 0 | 0 | Qty. to be updated based on final simulation report.
26 | D-12 | 15W LED Decorative Pendant Light Fixture, 4000K, IP20, DALI Dimmable , LED Lifespan 50000 H; CRI > 90; 3 or Less SDCM. Lm Flux > 60 lm/W, Installation: Suspended. Size- Dia - 600mm x 200mm H | Booth Seating - Façade Side |  | No's | 15 | 2 |  |  | 0 | 0 | 0
3 | D-12a | 15W LED Decorative Pendant Light Fixture, 4000K, IP20, Non Dimmable , LED Lifespan 50000 H; CRI > 90; 3 or Less SDCM. Lm Flux > 60 lm/W, Installation: Suspended. Size- Dia - 600mm x 200mm H | Booth Seating |  | No's | 15 | removed qty
3 | D-13 | 20W LED Decorative Metal Dome Pendant Light Fixture with Diffused Distribution with Diffuser, 4000K, IP20, DALI Dimmable , LED Lifespan 50000 H; CRI > 90; 3 or Less SDCM. Lm Flux > 60 lm/W, Installation: Suspended. Size- Dia - 600mm | 11 Pax Meeting Room |  | No's | 20 | 3 |  |  | 0 | 0 | 0
|  | Total for Decorative Lights: | [9 empty] | 0
|  | Total for A+B: | [9 empty] | 0
|  | GST: | [10 empty] | GST is extra as applicable
Grand Total: