## SUMMARY OF ELECTRICAL & ELV BOQ
Name of Project: “Interior Fit-out work in the office space of Power Finance Corporation Limited, Tower-H, World Trade Centre, Nauroji Nagar, New Delhi-110029 including Operation & Maintenance for 06 years”
SUMMARY OF ELECTRICAL & ELV BOQ
SECTION | DESCRIPTION | Amount (In Rs.)
|  | DSR | Non DSR | Total
SUB HEAD A | WIRING IN STEEL & PVC CONDUIT
SUB HEAD B | MCCB, MCB & DB'S
SUB HEAD C | RISING MAINS & BUS TRUNKING - ALUMINIUM
SUB HEAD D | BUS BAR TRACK FOR LIGHTING
SUB HEAD E | CABLE TRAYS & RACEWAY
SUB HEAD F | EARTHING
SUB HEAD G | MV CABLES (SUPPLY & LAYING)
SUB HEAD H | MV CABLE JOINTING & END TERMINATION
SUB HEAD I | MV PANELS (AS PER SLD)
SUB HEAD J | UPS
SUB HEAD K1 | FIRE DETECTION AND ALARM SYSTEM
SUB HEAD K2 | VESDA (ASPIRATION) SYSTEM (FOR SERVER, UPS & BATTERY ROOMS)
SUB HEAD L | ACCESS CONTROL SYSTEM
SUB HEAD M | CCTV SYSTEM
SUB HEAD N | ADDRESSABLE WATER LEAK DETECTION SYSTEM
SUB HEAD O | ADDRESSABLE DIGITAL RODENT REPELLENT SYSTEM
SUB HEAD P | EMERGENCY LIGHTING SYSTEMS - WITH CENTRAL BATTERY SYSTEM
SUB HEAD Q | LIGHT FIXTURES
SUB HEAD R1 | LMS - LIGHTING MANAGEMENT SYSTEM
SUB HEAD R2 | MOTORISED SHADES - WITHOUT FABRIC
TOTAL
Total Cost in Rs.
HIGH SIDE - ELECTRICAL WORKS
SUB HEAD S | SECURITY EQUIPMENTS
SUB HEAD T | ELECTRICAL VEHICLE CHARGER
SUB HEAD U | PARKING MANAGEMENT / GUIDANCE SYSTEM
SUB HEAD V | SOLAR PV (12KW) SYSTEM - DISMANTILING & RE- INSTALLATION
TOTAL
Total Cost in Rs.

## ELECTRICAL & ELV BOQ
ITEM NO. | DSR / NDSR (MR) | ITEM DESCRIPTIONS | Unit | Area 1 |  |  |  | Area 2
|  |  |  | Qty | Supply rate | Install Rate | Amount | Qty | Supply rate | Install Rate | Amount
SUB HEAD A | CHAPTER-1 | WIRING IN STEEL & PVC CONDUIT
1 | 1.3 | Wiring for light point/ fan point/ exhaust fan point/ call bell point with 1.5 sq.mm FRLS/HFFR PVC insulated copper conductor single core cable in surface/ recessed steel conduit, with modular switch, modular plate, suitable GI box and earthing the point with 1.5 sq.mm FRLS/HFFR PVC insulated copper conductor single core cable etc. as required.
1.1 | 1.3.3 | Group C | Point |  | 1000
2 | 1.5 | Wiring for light/ power plug with 2x4 sq.mm FRLS/HFFR PVC insulated copper conductor single core cable in surface/ recessed steel conduit along with 1 No. 4 sq. mm FRLS PVC insulated copper conductor single core cable for loop earthing as required. | Meter |  | 25754
3 | 1.6 | Wiring for light/ power plug with 4x4 sq. mm FRLS/HFFR PVC insulated copper conductor single core cable in surface/ recessed steel conduit along with 2 Nos. 4 sq.mm FRLS/HFFR PVC insulated copper conductor single core cable for loop earthing as required. | Meter |  | 12877
4 | 1.7 | Wiring for circuit/ submain wiring along with earth wire with the following sizes of FRLS/HFFR PVC insulated copper conductor, single core cable in surface/ recessed steel conduit as required.
4.1 | 1.7.1 | 2 X 1.5 sq. mm + 1 X 1.5 sq. mm earth wire | Meter |  | 3535
4.2 | 1.7.2 | 2 X 2.5 sq. mm + 1 X 2.5 sq. mm earth wire | Meter |  | 19210
4.3 | 1.7.3 | 2 X 4 sq. mm + 1 X 4 sq. mm earth wire | Meter |  | 100
4.4 | 1.7.4 | 2 X 6 sq. mm + 1 X 6 sq. mm earth wire | Meter |  | 640
4.5 | 1.7.5 | 2 X 10 sq. mm + 1 X 6 sq. mm earth wire | Meter |  | 100
4.6 | 1.7.6 | 2 X 16 sq. mm + 1 X 6 sq. mm earth wire | Meter |  | 120
4.7 | 1.7.7 | 1 X 2.5 sq. mm + 2 X 2.5 sq. mm earth wire | Meter |  | 100
4.8 | 1.7.8 | 4 X 4 sq. mm + 2 X 4 sq. mm earth wire | Meter |  | 1200
6 | 1.19 | Supplying and drawing co-axial TV cable RG-6 grade, 0.7 mm solid copper conductor PE insulated, shielded with fine tinned copper braid and protected with PVC sheath in the existing surface/ recessed steel/ PVC conduit as required. | Meter |  | 300
7 | 1.2 | Supplying and fixing of following sizes of steel conduit along with accessories in surface/recess including painting in case of surface conduit, or cutting the wall and making good the same in case of recessed conduit as required.
7.1 | 1.20.1 | 20 mm | Meter |  | 18830
7.2 | 1.20.2 | 25 mm | Meter |  | 19573
7.3 | 1.20.3 | 32 mm | Meter |  | 260
8 | 1.24 | Supplying and fixing following modular switch/ socket on the existing modular plate & switch box including connections but excluding modular plate etc. as required.
8.1 | 1.24.1 | 5/6 A switch | Each |  | 1180
8.2 | 1.24.2 | 15/16 A switch | Each |  | 1091
8.3 | 1.24.3 | 3 pin 5/6 A socket outlet | Each |  | 1180
8.4 | 1.24.4 | 6 pin 15/16 A socket outlet | Each |  | 3734
9 | 1.26 | Supplying and fixing modular blanking plate on the existing modular plate & switch box excluding modular plate as required. | Each |  | 481
10 | 1.27 | Supplying and fixing following size/ modules, GI box along with modular base & cover plate for modular switches in recess etc. as required.
10.1 | 1.27.1 | 1 or 2 Module (75mmX75mm) | Each |  | 26
10.2 | 1.27.2 | 3 Module (100mmX75mm) | Each |  | 4914
10.4 | 1.27.4 | 6 Module (200mmX75mm) | Each |  | 536
11 | 1.28 | Supplying and fixing following Modular base & cover plate on existing modular metal boxes etc. as required
11.1 | 1.28.1 | 1 or 2 Module | Each |  | 907
11.2 | 1.28.2 | 3 Module | Each |  | 4914
11.5 | 1.28.5 | 8 Module | Each |  | 881
12 | 1.31 | Supplying and fixing suitable size GI box with modular plate and cover in front on surface or in recess, including providing and fixing 3 pin 5/6 A modular socket outlet and 5/6 A modular switch, connections etc. as required. | Each |  | 673
13 | 1.32 | Supplying and fixing suitable size GI box with modular plate and cover in front on surface or in recess, including providing and fixing 6 pin 5/6 & 15/16 A modular socket outlet and 15/16 A modular switch, connections etc. as required. | Each |  | 1967
14 | 1.49 | Numbering of ceiling fan/ exhaust fan/ fluorescent fittings as required. | Each |  | 13991
15 | 1.54 | Wiring for group controlled (looped) light point/fan point /exhaust fan point / call bell point (without independent switch etc.) with 1.5 sq. mm FRLS/HFFR PVC insulated copper conductor single core cable in surface/ recessed steel conduit, and earthing the point with 1.5 sq. mm FRLS/HFFR PVC insulated copper conductor single core cable etc. as required.
15.1 | 1.54.3 | Group C | Point |  | 12572
Note:
● Circuit for Light point not consider in office area, only considered for Toilet etc. where Lighting Track is not covered. ● Wiring mainly laid in raceway / on cable tray. ● Raceway & Cable Tray cost not to be included here. ● In case of raised floor, with raceway & cable tray running under raised floor for wiring, no conduiting upto furniture is to be considered. Wire will be kept on the floor upto the furniture entry.
TOTAL CARRIED OVER TO SUMMARY
SUB HEAD B | CHAPTER- 2 | MCCB, MCB & DB'S
1 | DSR-2025- 2.3 | Supplying and fixing following way, single pole and neutral, sheet steel, MCB distribution board, 240 V, on surface/ recess, complete with tinned copper bus bar, neutral bus bar, earth bar, din bar, interconnections, powder painted including earthing etc. as required. (But without MCB/RCCB/Isolator)
1.1 | DSR-2025- 2.3.1 | 6 way , Double door | Each |  | 20
2 | DSR-2025- 2.4 | Supplying and fixing following way, horizontal type three pole and neutral, sheet steel, MCB distribution board, 415 V, on surface/ recess, complete with tinned copper bus bar, neutral bus bar, earth bar, din bar, interconnections, powder painted including earthing etc. as required. (But without MCB / RCCB /Isolator).
2.1 | DSR-2025- 2.4.1 | 4 way (4 + 12), Double door | Each |  | 5
2.2 | DSR-2025- 2.4.3 | 8 way (4 + 24), Double door | Each |  | 12
2.3 | MR | 12 way (4 + 36), Double door | Each |  | 96
3 |  | Supplying and fixing of following ways surface/ recess mounting, vertical type, 415 V, TPN MCB distribution board of sheet steel, dust protected, duly powder painted, inclusive of 200 A tinned copper bus bar, common neutral link, earth bar, din bar for mounting MCBs (but without MCBs and incomer ) as required . (Note : Vertical type MCB TPDB is normally used where 3 phase outlets are required.)
3.1 | MR | 6 way (4 + 18), Double door | Each |  | 22
4 | DSR-2025- 2.10 | Supplying and fixing 5 A to 32 A rating, 240/415 V, 10kA, "C" curve, miniature circuit breaker suitable for inductive load of following poles in the existing MCB DB complete with connections, testing and commissioning etc. as required.
4.1 | DSR-2025- 2.10.1 | Single pole | Each |  | 3082
4.2 | DSR-2025- 2.10.4 | Triple pole | Each |  | 120
6 | DSR-2025- 2.12 | Supplying and fixing following rating, double pole, 240 V, isolator in the existing MCB DB complete with connections, testing and commissioning etc. as required.
6.1 | DSR-2025- 2.12.1 | 40A | Each |  | 20
7 | DSR-2025- 2.13 | Supplying and fixing following rating, four pole, 415V, isolator in the existing MCB DB complete with connections, testing and commissioning etc. as required.
7.1 | DSR-2025- 2.13.1 | 40A | Each |  | 21
7.2 | DSR-2025- 2.13.2 | 63A | Each |  | 109
8 | DSR-2025- 2.14 | Supplying and fixing following rating, double pole, (single phase and neutral), 240 V, residual current circuit breaker (RCCB), having a sensitivity current 30 mA in the existing MCB DB complete with connections, testing and commissioning etc. as required.
8.1 | DSR-2025- 2.14.2 | 40A | Each |  | 29
8.2 | DSR-2025- 2.14.3 | 63A | Each |  | 327
9 | DSR-2025- 2.16 | Supplying and fixing DP sheet steel enclosure on surface/ recess along with 25/32 A 240 V "C" curve DP MCB complete with connections, testing and commissioning etc. as required | Each |  | 67
10 | DSR-2025- 2.17 | Supplying and fixing TP sheet steel enclosure on surface/ recess along with 16/25/32 A 415 V "C" curve TP MCB complete with connections, testing and commissioning etc. as required. | Each |  | 84
11 | DSR-2025- 2.23 | Supplying and fixing Cable End Box (Loose Wire Box) suitable for following single pole and neutral, sheet steel, MCB distribution board, 240 Volts, on surface/ recess, complete with testing and commissioning etc. as required.
11.1 | DSR-2025- 2.23.1 | For 6 way, Double door SPN MCB DB | Each |  | 20
12 | DSR-2025- 2.24 | Supplying and fixing Cable End Box (Loose Wire Box) suitable for following triple pole and neutral, sheet steel, MCB distribution board, 415 Volts, on surface/ recess, complete with testing and commissioning etc.as required.
12.1 | DSR-2025- 2.24.1 | For 4 way, Double door TPN MCB DB | Each |  | 5
12.2 | DSR-2025- 2.24.3 | For 8 way, Double door TPN MCB DB | Each |  | 12
12.3 | MR | For 12 way, Double door TPN MCB DB | Each |  | 96
13 | DSR-2025- 2.25 | Supplying and fixing Cable End Box (Loose Wire Box) suitable for triple pole and neutral, sheet steel, Vertical MCB distribution board, 415 Volts, on surface/ recess, complete with testing and commissioning etc. as required. | Each |  | 22
TOTAL CARRIED OVER TO SUMMARY
SUB HEAD C | CHAPTER- 3 | RISING MAINS & BUS TRUNKING - ALUMINIUM
1 | MR | RISING MAINS - (UPS POWER) INDOOR (RUNNING IN THE ELECTRICAL SHAFTS/ THROUGH ELECTRICAL ROOMS)
Design, Manufacture, Supply, Installation, Testing, and Commissioning of Sandwich Bus way 650 volts system rising mains with cooling Fins, 6bar - 3PH, 2N & 1E Aluminium conductor, Class 'F' Insulation, with aluminium body / powder coated sheet steel enslosure with 2x25x6 aluminium earth tape as earth throughout the continuous length as per specification suitable for 3ph 4wire 50HZ, of short circuit fault withstand capacity for 1 Sec as specified below. The bus way shall have system for plug in tap off box at desired levels and single bolt double head section jointing system. Jointing system shall be with thermal sensative temperature indicators. The Tap off boxes shall have Door Interlocking mechanism and mechanical interlocking with Bus duct housing during ‘ON’ position to prevent being taking of in energized condition. Supporting system shall be fail proof even in the earth quake situations, as per sesmic requirement of site.
1. RISING MAINS SUPPORTING SYSTEM TO BE DESIGNED BY A COMPETENT AGENCY TO ENSURE SAFETY OF THE INSTALLATION, BUILDING AND THE PERSONS. CONTRACTOR TO HIRE A SPECIALISED AGENCY FOR DESIGN AND INSTALLATION OF THE RISING MAINS SUPPORT SYSTEM AND ASSUME COMPLETE RESPONSIBILTY ON ADEQUACY OF THE SUPPORT SYSTEM. CONTRACTOR TO SUBMIT A CERTICATE FROM THE STRUCTUAL CONSULTANT ALONG WITH THE DESIGN AND DRAWINGS SUBMITTED TO THE CLIENT/PMC.
2. ALSO QUOTE FOR SESIMIC SUPPORTS AS AN ALTERNATE FOR THE COMPLETE INSTALLATION FOR THE COMPLETE RISING MAIN SYSTEM.
Notes:
a. For Rising Mains, no temperature deration upto 45°C, Ambient temperature.
b. Flexible connections need to be included in the price and need to be provided as required for thermal expansion/ building expansion joints / panel end connections /one vertical expansion for every floor.
c. 200% Neutral & 100% Internal earth type Rising Main.
d. 200% sized Neutral as of phase current.
Note: Final configuration of Rising Main, Bus Ducts and Tap Offs to be cross checked from the SLD and details as per SLD shall be final.
1.1 | MR | RISING MAIN INSIDE ELECTRICAL SHAFT/INSIDE ELECTRICAL ROOM ON TYPICAL FLOORS:- 630Amp
1.1.1 | MR | Straight Vertical Run inside Floor Electrical Shaft / Floor Electrical Room - 630Amp 25KA, (3P + 2N+1E) Aluminium - (IP55) | RM |  | 200
1.1.2 | MR | Flange End | Nos. |  | 2
1.1.3 | MR | Vertical Expansion Joints inside Floor Electrical Shaft / Floor Electrical Room - 630Amp 25KA, (3P + 2N+1E) Aluminium - (IP55) | Nos. |  | 20
1.1.4 | MR | End Cap at top (at last floor) (IP55) | Nos. |  | 2
1.1.5 | MR | Copper Flexible-Braided Type, Max Length-300 mm | Nos. |  | 4
1.1.6 | MR | GI Fabriacted Support to Install Rising Main @ 4 Nos at every Floor | Nos. |  | 120
1.1.7 | MR | Vertical Bends | Nos. |  | 5
1.1.8 | MR | Horizontal Bends | Nos. |  | 10
1.2 | MR | RISING MAIN INSIDE ELECTRICAL SHAFT/INSIDE ELECTRICAL ROOM ON TYPICAL FLOORS:- - 1000Amp
1.2.1 | MR | Straight Vertical Run inside Floor Electrical Shaft / Floor Electrical Room - 1000Amp 25KA, (3P + 2N+1E) Aluminium - (IP55) | RM |  | 200
1.2.2 | MR | Flange End | Nos. |  | 2
1.2.3 | MR | Vertical Expansion Joints inside Floor Electrical Shaft / Floor Electrical Room - 1000Amp 25KA, (3P + 2N+1E) Aluminium - (IP55) | Nos. |  | 20
1.2.4 | MR | End Cap at top (at last floor) (IP55) | Nos. |  | 2
1.2.5 | MR | Copper Flexible-Braided Type, Max Length-300 mm | Nos. |  | 4
1.2.6 | MR | GI Fabriacted Support to Install Rising Main @ 4 Nos at every Floor | Nos. |  | 120
1.2.7 | MR | Vertical Bends | Nos. |  | 5
1.2.8 | MR | Horizontal Bends | Nos. |  | 10
1.3 |  | TAP-OFF BOXES - INDOOR:
Supply and installation of following 3P MCCB + 2N Link of breaking capacity as called for, for fixing in the incoming Tap-off box. Tap-off box housing shall be fabricated out of 14G CRCA painted or powder coated (as approved) sheet steel. The tap-off box should be factory fabricated and complete with solid aluminium links of rated capacity from MCCB to rising mains and suitable size of gland plate etc.The tap-off box shall be suitable for termination of XLPE insulated Al. conductor armoured cable including shrouding of terminal ends. as required. (On UPS IT + WS Rising Mains)
1.3.1 | MR | 100Amp, 3P MCCB + 2N Link with fixed thermal & magnetic releases (IP55). Fault Rating: 25 KA | Nos. |  | 24
1.3.2 | MR | 160Amp, 3P MCCB + 2N Link with fixed thermal & magnetic releases (IP55). Fault Rating: 25 KA | Nos. |  | 16
1.3.3 | MR | 200Amp, 3P MCCB + 2N Link with fixed thermal & magnetic releases (IP55). Fault Rating: 25 KA | Nos. |  | 2
1.3.4 | MR | 63Amp, 3P MCCB + 2N Link with fixed thermal & magnetic releases (IP55). Fault Rating: 25 KA | Nos. |  | 2
Note:
1. The aluminium housing shall serve as a continuous protective earth (PE) conductor. With a housing size of 2.5 mm², which exceeds the required earthing size, external earthing is not necessary.
2. Busbar system shall have CE marking
2 |  | BUS BAR TRACK FOR RACKS POWER SUPPLY
Design, Supply, installation, testing and commissioning of 4W Aluminium Bus Bar System for Racks with Accessories as follows:
2.1 | MR | Straight Feeder 100 A (3 Mtrs Length) with IP-55 Protection is 4W (3P+100%Neutral +100% + PE(As housing) | Meter |  | 48
2.2 | MR | Support Bracket (at 1.5 Mtr Interval) | Nos. |  | 32
2.3 | MR | 100A End Feed Unit | Nos. |  | 16
2.4 | MR | End Cover | Nos. |  | 16
2.5 | MR | 40 A Tap Off Boxes | Sets |  | 48
Design, Supply, installation, testing and commissioning of 4W Copper Bus Bar System for Server Room with Accessories as follows:
2.6 | MR | Straight Feeder 250 A (3 Mtrs Length) with IP-55 Protection is 4W (3P+100%Neutral +100% + PE(As housing) | Meter |  | 42
2.7 | MR | Support Bracket (at 1.5 Mtr Interval) | Nos. |  | 28
2.8 | MR | 250A End Feed Unit | Nos. |  | 4
2.9 | MR | End Cover | Nos. |  | 4
2.1 | MR | 40 A Tap Off Boxes | Sets |  | 32
Note: Cost to include visit to OEM factory before delivery of materials at site for a FAT, process and quality inspection of the proposed materials in the tender under this head for 3 persons from user / project manager / designer firm.
TOTAL CARRIED OVER TO SUMMARY
SUB HEAD D |  | BUS BAR TRACK FOR LIGHTING
Design, Supply, installation, testing and commissioning of 8W (4W) Copper Bus Bar System for Lighting with Accessories as follows:
1 | MR | Straight Feeder 25 A (3 Mtrs Length) with IP-55 Protection is [4W], (3P+100%Neutral +100% + PE(As housing) +(3P+100%Neutral +100% + PE(As housing) | Meter |  | 2500
2 | MR | DL Lighting Fitting Bracket (at 1.5 Mtr Interval) | Nos. |  | 1650
3 | MR | 25A End Feed Unit | Nos. |  | 100
4 | MR | End Cover | Nos. |  | 100
5 | MR | Flexible Joints | Nos. |  | 200
6 | MR | 10/16 A Single Phase Tap Off Boxes with fuse | Sets |  | 1320
7 | MR | Support | Lot |  | 1
Note:
1. The aluminium housing shall serve as a continuous protective earth (PE) conductor. With a housing size of 2.5 mm², which exceeds the required earthing size, external earthing is not necessary. 2. Test certificate at 50–55° shall be required. 3. Hanging arrangement shall be inclusive of busduct supply. 4. Cost to include visit to OEM factory before delivery of materials at site for a FAT, process and quality inspection of the proposed materials in the tender under this head for 3 persons from user / project manager / designer firm.
TOTAL CARRIED OVER TO SUMMARY
SUB HEAD E | CHAPTER- 4 | CABLE TRAYS & RACEWAY
1 |  | Hot Dipped Galvanized Iron Cable Tray
1.1 | DSR-2025- 4.6 | Supplying and installing following size of perforated Hot Dipped Galvanised Iron cable tray (Galvanisation thickness not less than 50 microns) with perforation not more than 17.5%, in convenient sections, joined with connectors, suspended from the ceiling with two numbers GI Suspenders i/c base of suitable size GI angle, GI bolts & nuts, fastner etc as required.
a. | DSR-2025- 4.6.2 | 150 mm width X 50 mm depth X 1.6 mm thickness | Meter |  | 1695
b. | DSR-2025- 4.6.4 | 300 mm width X 50 mm depth X 1.6 mm thickness | Meter |  | 617
c. | DSR-2025- 4.6.6 | 450 mm width X 50 mm depth X 2.0 mm thickness | Meter |  | 68
e. | DSR-2025- 4.6.11 | 600 mm width X 62.5 mm depth X 2.0 mm thickness | Meter |  | 314
1.2 | DSR-2025- 4.7 | Supplying and installing following size of perforated Hot Dipped Galvanised Iron cable tray "bends" (galvanisation not less than 50 microns) with perforation not more than 17.5%, in convenient sections, joined with connectors, suspended from the ceiling with two numbers GI Suspenders i/c base of suitable size GI angle, GI bolts & nuts, fastner etc as required.
a. | DSR-2025- 4.7.2 | 150 mm width X 50 mm depth X 1.6 mm thickness | Each |  | 80
b. | DSR-2025- 4.7.4 | 300 mm width X 50 mm depth X 1.6 mm thickness | Each |  | 32
b. | DSR-2025- 4.7.6 | 450 mm width X 50 mm depth X 2.0 mm thickness | Each |  | 8
d. | DSR-2025- 4.7.11 | 600 mm width X 62.5 mm depth X 2.0 mm thickness | Each |  | 3
1.2 | DSR-2025- 4.8 | Supplying and installing following size of perforated Hot Dipped Galvanised Iron cable tray "Tee" (galvanisation not less than 50 microns) with perforation not more than 17.5%, in convenient sections, joined with connectors, suspended from the ceiling with two numbers GI Suspenders i/c base of suitable size GI angle, GI bolts & nuts, fastner etc as required.
a. | DSR-2025- 4.8.2 | 150 mm width X 50 mm depth X 1.6 mm thickness | Each |  | 47.3
b. | DSR-2025- 4.8.4 | 300 mm width X 50 mm depth X 1.6 mm thickness | Each |  | 12.1
b. | DSR-2025- 4.8.6 | 450 mm width X 50 mm depth X 2.0 mm thickness | Each |  | 7.7
d. | DSR-2025- 4.8.11 | 600 mm width X 62.5 mm depth X 2.0 mm thickness | Each |  | 1.1
2 |  | RACEWAYS
Notes:
All necessary specials and fittings, brass bushes etc.
Approved cover plates for inspection, junction and outlet boxes.
2mm thick outlet boxes and junction boxes.
All fixing accessories such as clips, nails, screws etc.
Providing and fixing approved saddles, hooks and grouting the same as required, in the case of all exposed conduit work.
Embedding conduits and accessories in wall, floors etc. during construction and / or cutting chases and making good as approved.
Providing 14 SWG GI pull wire in all conduit work.
Repainting of GI conduit, outlet boxes and junction boxes when ever damaged.
Important Notes:-
Contractor to get the samples of floor and ceiling raceways to be approved from the Architect/ Project Manager/ Consultant/ Client before supply & erection.
Depth of the floor raceway is to be decided by the contractor after checking/ examining screed depth available at site. For this purpose chipping to be carried out at various places on the floor/ floors to carefully assess the depth/ floor margin available. Final approval is to be obtained from the Architect/ Project Manager/ Client before ordering/ fabricating raceway. The sizes & depths of raceways given in the BOQ are only tentative & indicative.
Contractor is also supposed to check and confirm the adequacy of raceway sizes by calculating the exact number of electrical circuit wires & N/W wires for respective Electrical & N/W raceways.
Electrical & N/W raceways to be run separated by a gap of not less than 450mm or more.
'N/W' stands for Networking cables.
1N/ 2N/ 3N/ 4N stands for One node/ Two nodes/ Three nodes & Four nodes respectively of voice & data face plates/ wires.
2.1 | MR | GI RACEWAY IN FLOOR SCREED
Supply & Fixing of factory fabricated pre-galvanised sheet steel raceway in 2mm thickness for bottom & sides and 2mm/ 3mm thick top cover as called for in the BOQ below, including necessary civil work such as chase cutting in screed, fixing/ jamming the raceway, aligning & leveling and finishing with sand cement plaster & chicken wire mesh:
40mm Depth
2.1.1 | MR | 100mm x 40mm (2mm top cover) | RM |  | 2406
2.1.2 | MR | 150mm x 40mm (2mm top cover) | RM |  | 743
2.1.3 | MR | 250mm x 40mm (3mm top cover) | RM |  | 880
2.1.4 | MR | 300mm x 40mm (3mm top cover) | RM |  | 546
2.1.5 | MR | 375mm x 40mm (3mm top cover) | RM |  | 371
2.2 |  | RACEWAY FLOOR JUNCTION BOXES (IN SCREED)
Providing & Fixing of GI sheet steel 4 WAY junction boxes with top cover to suite the raceway fixing & necessary civil work such as floor chipping, jamming of junction box and repair of floor:
Raceway junction box
2.2.1 | MR | 100mm x 100mm x 50mm (For Floor Conduit) | Nos. |  | 410
2.2.1 | MR | 150mm x 150mm x 50mm (For 100mm wide raceway) | Nos. |  | 698
2.2.2 | MR | 200mm x 200mm x 50mm (For 150mm wide raceway) | Nos. |  | 213
2.2.3 | MR | 300mm x 300mm x 50mm (For 225mm wide raceway) | Nos. |  | 186
2.2.4 | MR | 350mm x 350mm x 50mm (For 300mm wide raceway) | Nos. |  | 115
2.2.5 | MR | 425mm x 425mm x 50mm (For 375mm wide raceway) | Nos. |  | 43
2.3 |  | RACEWAY - IN CEILING
Supply & Fixing of factory fabricated MS Powder coated sheet steel raceway in 1.6 / 2 mm thickness for bottom, sides & top coper as called for in the BOQ below, including necessary civil work such as hanging the ceiling raceway from slab by a suitable GI flat support with galvanized steel rods screwed into RCC slab with the help of dash fasteners. Vendor to design the supporting system with adequately sized supports & spacing to with stand the load of raceway & wires etc. Raceways shall be complete with junction boxes of required size & required quantity to be included in the cost of the raceways:
For 50mm Depth
2.3.2 | MR | 150 x 50 (1.6mm) | RM |  | 165
2.3.3 | MR | 250 x 50 (1.6mm) | RM |  | 142
2.3.4 | MR | 300 x 50 (2mm) | RM |  | 121
2.4 |  | RACEWAY - IN CEILING FOR WI-FI / CCTV / ACS ETC.
Supply & Fixing of factory fabricated MS Powder coated sheet steel raceway in 1.6 / 2 mm thickness for bottom, sides & top coper as called for in the BOQ below, including necessary civil work such as hanging the ceiling raceway from slab by a suitable GI flat support with galvanized steel rods screwed into RCC slab with the help of dash fasteners. Vendor to design the supporting system with adequately sized supports & spacing to with stand the load of raceway & wires etc. Raceways shall be complete with junction boxes of required size & required quantity to be included in the cost of the raceways:
For 50mm Depth
2.4.1 | MR | 100 x 50 (1.6mm) | RM |  | 1163
2.4.2 | MR | 150 x 50 (1.6mm) | RM |  | 887
2.4.3 | MR | 300 x 50 (2mm) | RM |  | 286
TOTAL CARRIED OVER TO SUMMARY
SUB HEAD F | CHAPTER- 5 | EARTHING
1 | DSR-2025- 5.6 | Earthing with copper earth plate 600 mm X 600 mm X 3 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7 Meter long etc. with charcoal/ coke and salt as required. | Set |  | 12
2 | DSR-2025- 5.8 | Supplying and laying 25 mm X 5 mm copper strip at 0.50 metre below ground as strip earth electrode, including connection/ terminating with nut, bolt, spring, washer etc. as required. (Jointing shall be done by overlapping and with 2 sets of brass nut bolt & spring washer spaced at 50mm) | Meter |  | 15
3 | DSR-2025- 5.1 | Providing and fixing 25 mm X 5 mm copper strip in 40 mm dia G.I. pipe from earth electrode including connection with brass nut, bolt, spring, washer excavation and re-filling etc. as required. | Meter |  | 200
4 | DSR-2025- 5.15 | Providing and fixing 25 mm X 5 mm G.I. strip on surface or in recess for connections etc. as required. | Meter |  | 4000
5 | DSR-2025- 5.16 | Providing and fixing 6 SWG dia G.I. wire on surface or in recess for loop earthing as required. | Meter |  | 1500
6 | DSR-2025- 5.2 | Providing and fixing earth bus of 50 mm X 5 mm copper strip on surface for connections etc. as required. | Meter |  | 150
7 | MR | SINGLE CORE COPPER ARMOURED CABLE EARTHING- EARTHING CABLES / LEADS:
Supply of 1.1kV grade XLPE insulated, Extruded FR-LSH PVC inner sheath Type ST-2, FR- LSH PVC outer sheath Type ST-2, stranded Copper conductor, Armoured cable in existing PVC pipes/ on existing cable trays etc. including terminations with tinned copper lugs / thimbles:
a. |  | 1C x 150 sq.mm XLPE insulated Cu. Ar. Cable | RM |  | 400
8 | MR | SINGLE CORE COPPER UNARMOURED CABLE EARTHING:
Supply of 1.1kV grade XLPE insulated, Extruded FR-LSH PVC sheath Type ST-2 with Anti termite and Anti rodent properties, Copper Conductor, Un. Armoured cables in existing PVC pipes/ on existing cable trays etc. including terminations with tinned copper lugs / thimbles:
8.1 | MR | 1C x 150 sq.mm XLPE insulated Cu. Un. Ar. Cable | RM |  | 75
8.2 | MR | 1C x 95 sq.mm XLPE insulated Cu. Un. Ar. Cable | RM |  | 75
8.3 | MR | 1C x 25 sq.mm XLPE insulated Cu. Un. Ar. Cable | RM |  | 100
8.4 | MR | 1C x 16 sq.mm XLPE insulated Cu. Un. Ar. Cable | RM |  | 675
8.5 | MR | 2C x 16 sq.mm XLPE insulated Cu. Un. Ar. Cable | RM |  | 1500
9 | DSR-2025- 10.8 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size on cable tray as required.
9.1 | DSR-2025- 10.8.1 | Upto 35 sq. mm (clamped with 1mm thick saddle) | Meter |  | 2250
9.2 | DSR-2025- 10.8.2 | Above 35 sq. mm and upto 95 sq. mm (clamped with 25x3mm MS flat clamp) | Meter |  | 75
9.3 | DSR-2025- 10.8.3 | Above 95 sq. mm and upto 185 sq. mm (clamped with 25/40x3mm MS flat clamp) | Meter |  | 475
10 | MR | Supply, Laying & terminations of 1.1KV grade single core FR-LSH (Flame Retardant, Low smoke & low halogen, special PVC insulated), copper conductor unsheathed wires as per IS: 694 in existing conduits, raceways, trays etc. & connections with tinned copper lugs / thimbles (earth wires)
10.1 | MR | 1C x 6 sq.mm XLPE insulated Cu. Un. Ar. Cable | RM |  | 2000
10.2 | MR | 1C x 4 sq.mm XLPE insulated Cu. Un. Ar. Cable | RM |  | 500
11 |  | DEDICATED EARTH BOX
11.1 | MR | 16G CRCA powder coated dedicated earth box of required size with 2x50x6mm copper earth link on insulated supports. | Nos. |  | 12
TOTAL CARRIED OVER TO SUMMARY
SUB HEAD G | CHAPTER- 10 | MV CABLES (SUPPLY & LAYING)
The rate shall also include the following:
Effecting adequate and proper connections at terminations.
Providing all fixing accessories such as clamping devices nuts, bolts and screws.
Excavation for laying of cables, filling of sand, brick protection, back filling of earth, watering, ramming and making good as approved in directly ground burry.
Wherever the cables are of aluminum and bus bars of copper bimetallic lugs shall be used.
All cable shall be laid with one diameter gap or as specified or as called for.
All cable shall be IS approved.
Fire retardent paint one meter on both side of wall penetration and at termination as per specifications.
Burried LT cables to be laid atleast 750mm below ground.
All cutouts / sleeves shall be sealed with fire retardant sealent as approved.
Leave sufficient cable loops at both the cable ends.
Use Tinned copper thimbles/lugs with copper cables/copper wires.
Cable Clamps:
Cable fixing clamps , saddles & screws on trays / walls / slabs
Indoor Application:
· Aluminium
· Readymade type clamps or Made from 20mm x 3mm aluminium sheet / strips.
· 8mm SS-304 Screws for cable size 90mm² and above.
· 6mm SS-304 Screws for cable size less than 90mm².
Outdoor Application:
· SS-304
· Clamps Made from 20x1.8mm SS-304 sheet / strips.
· 8mm SS-304 Screws for cable size 90mm² and above.
· 6mm SS-304 Screws for cable size less than 90mm².
Clamps spacing
· 600mm C/C in vertical fashion in shaft on vertical trays.
· 1000mm C/C on horizontal tray or cable racks.
1 |  | ARMOURED CABLES - ALUMINIUM / COPPER:
XLPE INSULATED, FRLS(H) PVC SHEATHED ALUMINIUM / COPPER CONDUCTOR ARMOURED CABLES (IS:7098 Part-I):
Supply of following sizes of 1.1kV grade XLPE insulated, Extruded FRLS(H) PVC inner sheath Type ST-2, FRLS(H) PVC outer sheath Type ST-2, stranded Aluminium / Copper conductor, Armoured cables as per IS:7098 Part-I.
4 CORES - ARMOURED - ALUMINIUM / COPPER
1.1 | MR | 4Cx 25 sq.mm. Al. Ar. XLPE cable | RM |  | 600
1.2 | MR | 4C x 16 sq.mm.Cu. Ar. XLPE cable | RM |  | 590
1.3 | MR | 4C x 10 sq.mm.Cu. Ar. XLPE cable | RM |  | 4675
1.4 | MR | 4C x 6 sq.mm.Cu. Ar. XLPE cable | RM |  | 3373
1.5 | MR | 4C x 4 sq.mm.Cu. Ar. XLPE cable | RM |  | 11160
3.5/3.0 CORES - ARMOURED - ALUMINIUM / COPPER
1.6 | MR | 3.5Cx 300 sq.mm. Al. Ar. XLPE cable | RM |  | 2750
1.7 | MR | 3.5Cx 240 sq.mm. Al. Ar. XLPE cable | RM |  | 900
1.8 | MR | 3.5Cx 185 sq.mm. Al. Ar. XLPE cable | RM |  | 315
1.9 | MR | 3.5Cx 150 sq.mm. Al. Ar. XLPE cable | RM |  | 15
1.1 | MR | 3.5Cx 120 sq.mm. Al. Ar. XLPE cable | RM |  | 150
1.11 | MR | 3.5Cx 95 sq.mm. Al. Ar. XLPE cable | RM |  | 400
1.12 | MR | 3.5Cx 70 sq.mm. Al. Ar. XLPE cable | RM |  | 600
1.13 | MR | 3.5Cx 50 sq.mm. Al. Ar. XLPE cable | RM |  | 485
1.14 | MR | 3.5Cx 35 sq.mm. Al. Ar. XLPE cable | RM |  | 155
3 CORES - ARMOURED - ALUMINIUM / COPPER
1.15 | MR | 3Cx 300 sq.mm. Al. Ar. XLPE cable | RM |  | 400
1.16 | MR | 3Cx 95 sq.mm. Al. Ar. XLPE cable | RM |  | 120
1.17 | MR | 3C x 70 sq.mm.Cu. Ar. XLPE cable | RM |  | 20
1.18 | MR | 3C x 50 sq.mm.Cu. Ar. XLPE cable | RM |  | 140
1.2 | MR | 3C x 16 sq.mm.Cu. Ar. XLPE cable | RM |  | 880
1.21 | MR | 3C x 10 sq.mm.Cu. Ar. XLPE cable | RM |  | 20
1.22 | MR | 3C x 6 sq.mm.Cu. Ar. XLPE cable | RM |  | 480
1.23 | MR | 3C x 4 sq.mm.Cu. Ar. XLPE cable | RM |  | 9000
2 CORES - ARMOURED - ALUMINIUM / COPPER
1.24 | MR | 2C x 70 sq.mm.Cu. Ar. XLPE cable | RM |  | 20
1.25 | MR | 2C x 50 sq.mm.Cu. Ar. XLPE cable | RM |  | 140
1.27 | MR | 2C x 16 sq.mm.Cu. Ar. XLPE cable | RM |  | 880
1.28 | MR | 2C x 10 sq.mm.Cu. Ar. XLPE cable | RM |  | 20
2 CORES - ARMOURED - ALUMINIUM
1.29 | MR | 2C x 95 sq.mm.Al. Ar. XLPE cable | RM |  | 120
2 |  | UN ARMOURED CABLES - COPPER:
SUPPLY OF CABLES- XLPE INSULATED, FRLS(H) PVC SHEATHED COPPER CONDUCTOR UN. ARMOURED CABLES (IS:7098 Part-I):
Supply of following sizes of 1.1kV grade XLPE insulated, Extruded FRLS(H) PVC sheath Type ST-2 with Anti termite and Anti rodent properties, Copper Conductor, Un. Armoured cables as per IS:7098 Part-I.
2.1 | MR | 1Cx 185 sq.mm. Cu. Un. Ar. XLPE cable | RM |  | 1545
2.2 | MR | 1Cx 95 sq.mm. Cu. Un. Ar. XLPE cable | RM |  | 50
2.3 | MR | 1Cx 70 sq.mm. Cu. Un. Ar. XLPE cable | RM |  | 140
2.4 | MR | 1Cx 50 sq.mm. Cu. Un. Ar. XLPE cable | RM |  | 100
2.5 | MR | 1Cx 16 sq.mm. Cu. Un. Ar. XLPE cable | RM |  | 500
2.6 | MR | 4Cx 4 sq.mm. Cu. Un. Ar. XLPE cable | RM |  | 1270
2.7 | MR | 3Cx 4 sq.mm. Cu. Flexible PVC cable | RM |  | 39517.45
3 |  | FIRE SURVIVAL CABLES : COPPER CONDUCTOR CABLES
Supply of Fire Survival armoured cables of 600/1000V rated with Copper circular conductor having glass mica fire barrier tape covered by an XLPE insulation and LSZH for inner & outer sheath. Generally as per BS 7846, IEC-60502-1 & BS-8519 (latest edition). Should retain circuit integrity as per BS 8491:2008 (950°C for 3 hours) for cables having overall dia of 20mm and above. Cables with overall dia below 20 mm should retain circuit integrity as per BS 8434-2. 3rd Party inspection required prior to despatch of every lot. Cables shall be LPCB / TUV / BRE Global certified.
3.2 | MR | 2c x 4 Sq.mm Copper Conductor Ar. FS Cable | RM |  | 20
3.3 | MR | 3c x 4 Sq.mm Copper Conductor Ar. FS Cable | RM |  | 160
3.4 | MR | 3c x 6 Sq.mm Copper Conductor Ar. FS Cable | RM |  | 160
3.5 | MR | 4c x 4 Sq.mm Copper Conductor Ar. FS Cable | RM |  | 375
4 | 10.8 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size on cable tray as required.
4.1 | 2010-08-01 | Upto 35 sq. mm (clamped with 1mm thick saddle) | Meter |  | 33623
4.2 | 2010-08-02 | Above 35 sq. mm and upto 95 sq. mm (clamped with 25x3mm MS flat clamp) | Meter |  | 2335
4.3 | 2010-08-03 | Above 95 sq. mm and upto 185 sq. mm (clamped with 25/40x3mm MS flat clamp) | Meter |  | 2025
4.4 | 2010-08-04 | Above 185 sq. mm and upto 400 sq. mm (clamped with 40x3mm MS flat clamp) | Meter |  | 4050
TOTAL CARRIED OVER TO SUMMARY
SUB HEAD H | CHAPTER- 11 | MV CABLE JOINTING & END TERMINATION
1 | DSR-2025- 11.1 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
1.5 | MR | 2 X 95 sq. mm | Each |  | 4
1.9 | DSR-2025- 11.1.13 | 3 X 95 sq. mm (38mm) | Each |  | 4
1.1 | DSR-2025- 11.1.19 | 3 X 300 sq. mm (70mm) | Each |  | 8
1.11 | DSR-2025- 11.1.21 | 3½ X 35 sq. mm (32mm) | Each |  | 16
1.12 | DSR-2025- 11.1.22 | 3½ X 50 sq. mm (35mm) | Each |  | 30
1.13 | DSR-2025- 11.1.23 | 3½ X 70 sq. mm (38mm) | Each |  | 20
1.14 | DSR-2025- 11.1.24 | 3½ X 95 sq. mm (45mm) | Each |  | 28
1.15 | DSR-2025- 11.1.25 | 3½ X 120 sq. mm (45mm) | Each |  | 2
1.16 | DSR-2025- 11.1.26 | 3½ X 150 sq. mm (50mm) | Each |  | 2
1.17 | DSR-2025- 11.1.27 | 3½ X 185 sq. mm (57mm) | Each |  | 22
1.18 | DSR-2025- 11.1.29 | 3½ X 240 sq. mm (62mm) | Each |  | 12
1.19 | DSR-2025- 11.1.30 | 3½ X 300 sq. mm (70mm) | Each |  | 60
1.22 | DSR-2025- 11.1.34 | 4 X 25 sq. mm (28mm) | Each |  | 48
2 |  | CABLE TERMINATION (IS:7098 Part-I) - FOR COPPER CABLES
Cable end Termination of following sizes XLPE insulated, Extruded FRLS(H) PVC sheath Type ST-2 with Anti termite and Anti rodent properties, Copper Conductor, Un. Armoured / Armoured cables as per IS:7098 Part-I including cost of aluminium, heavy duty crimpping lugs, double compression glands, insulation tape and all necessary material to complete the termination.
2.1 | MR | 1Cx 50 sq.mm. Cu. Un. Ar. XLPE cable | Each |  | 10
2.2 | MR | 1Cx 16 sq.mm. Cu. Un. Ar. XLPE cable | Each |  | 200
2.3 | MR | 1Cx 70 sq.mm. Cu. Un. Ar. XLPE cable | Each |  | 22
2.4 | MR | 1Cx 95 sq.mm. Cu. Un. Ar. XLPE cable | Each |  | 20
2.5 | MR | 1Cx 185 sq.mm. Cu. Un. Ar. XLPE cable | Each |  | 196
2.6 | MR | 4Cx 4 sq.mm. Cu. Un. Ar. XLPE cable | Each |  | 148
2.7 | MR | 4Cx 16 sq.mm. Cu. Ar. XLPE cable | Each |  | 90
2.8 | MR | 4Cx 10 sq.mm. Cu. Ar. XLPE cable | Each |  | 218
2.9 | MR | 4Cx 6 sq.mm. Cu. Ar. XLPE cable | Each |  | 156
2.1 | MR | 4Cx 4 sq.mm. Cu. Ar. XLPE cable | Each |  | 658
2.11 | MR | 3Cx 70 sq.mm. Cu. Ar. XLPE cable | Each |  | 4
2.12 | MR | 3Cx 50 sq.mm. Cu. Ar. XLPE cable | Each |  | 28
2.13 | MR | 3Cx 16 sq.mm. Cu. Ar. XLPE cable | Each |  | 40
2.14 | MR | 3Cx 10 sq.mm. Cu. Ar. XLPE cable | Each |  | 4
2.15 | MR | 3Cx 6 sq.mm. Cu. Ar. XLPE cable | Each |  | 30
2.16 | MR | 3Cx 4 sq.mm. Cu. Ar. XLPE cable | Each |  | 496
2.17 | MR | 2Cx 70 sq.mm. Cu. Ar. XLPE cable | Each |  | 4
2.18 | MR | 2Cx 50 sq.mm. Cu. Ar. XLPE cable | Each |  | 28
2.19 | MR | 2Cx 16 sq.mm. Cu. Ar. XLPE cable | Each |  | 40
2.2 | MR | 2Cx 10 sq.mm. Cu. Ar. XLPE cable | Each |  | 4
2.22 | MR | 2Cx 4 sq.mm. Cu. Ar. XLPE cable | Each |  | 20
2.23 | MR | 3Cx 4 sq.mm. Cu. Flexible PVC cable | Each |  | 2000
TOTAL CARRIED OVER TO SUMMARY
SUB HEAD I |  | MV PANELS (AS PER SLD)
Design, manufacture, assembly, wiring, testing at works and supply to site of following panels/ distribution boards/ switch boards. The boards shall be designed and fabricated as per general specifications, technical details, specifications and notes as
Also, refer to General Notes and Specifications for Panels/ Boards
GENERAL NOTES FOR ACB's & MCCB's:
ACB's & MCCB's shall be of 3P or 4P as called for in the BOQ.
Ics = Icu = 100% for the MCCB's, MPCB's & ACB's
MCCB's shall be with extended rotary handle.
Exact rating (Amps), Poles, Type/Duty, Short circuit rating of MCCB is to be selected by the contractor as per load, fault and requirement and also approval taken.
All Switchgear selections shall be as per manufacturer's recommendation.
Contractor to submit manufacturer's selection charts for approval.
Only one make of switchgear to be used in a board /panel.
All communicable meters should be looped inside the panels and this loop has to be brought to one terminal point in the panel for connectivity.
No BMS cable should be directly connected to VFD and hence these points will have to be brought on to the terminal blocks inside the panel.
All energy meters shall be dual source and communicable type.
EMC & RFI FILTRATION FOR VFD's.
VFD’s for sensitive installations where life critical data communications are of importance ,like: • Hospitals • Airports • Electronic Industry • Data centres • Communication centres These installations Must have ‘C1’ category of RFI & EMC filters for 50 meters of cable length. These are applicable to all the VFD’s of AHU’s, fans, blowers, pumps , chillers and cooling towers. For these above mentioned critical applications, if chiller motors and pump motors are more than 90Kw, then ‘C2’ category of filters to be used if ‘ C1’ is not available. VFD’s for normal buildings and others similar installations shall have ‘C3’ category of RFI & EMC filter for AHU’s , fans, blowers, pumps, cooling towers & Chillers .
THDI for VFD's between 35% and 40% except VFD's for chillers, which will have THDI not exceeding 25%.
All VFD's shall be IP-20, if installed inside the panels and shall be IP55 if installed without enclosure.
Incomer switchgear, bus bars, supports and outgoing switchgear shall be of same fault level withstand capacity as mentioned for the panel.
All starter feeders/ VFD feeders in panels means complete with starter & VFD as the case may be as per specifications.
Use separate PLC's for Load management and separate for interlocking of breakers and bus couplers .
In the Main LT Panel, DG Power Panel, LT Panel cum DG Power Panel & Fire Emergency Panel: An external power source from 24V DC batteries with battery charger,independant of main supply has been proposed for trip circuit: ● 24 V DC bus to be run inside the panel ● For ON / OFF / Trip Indications.(24V DC) ● For Trip circuit healthy indications.(24V DC) ● For Shunt trip coil (24V DC).
In the Main LT Panel, DG Power Panel, LT Panel cum DG Power Panel & Fire Emergency Panel: It is recommend not to have 230V supply on panel door for Metering & Indication lamps. Therefore 415/√3 / 110 / √3 PT is considered to get 110 / √3 for ( 3 nos. Single phase PT's) for: ● R, Y, B Phase indication lamp at the incomer : 63V ● Incomer Metering / MFM meters:110V
In the Motor Control Panel & Other Panels : It is recommend not to have 230V supply on panel door for Metering & Indication lamps. Therefore 415/√3 / 110 / √3 PT is considered to get 110 / √3 for ( 3 nos. Single phase PT's) for: ● R, Y, B Phase indication lamp at the incomer : 63V ● Incomer Metering / MFM meters:110V incomer metering ● On, Off, Trip indication lamps at incomer: 110V
In the Motor Control Panel & Other Panels: It is also recommended to have a control transformer 415V (2 Phase) / 110V (1 Phase) for: • Starter's contactor coil (110V)
Metering & Indications:
A. For Main LT Panel, DG Power Panel, LT Panel cum DG Power Panel & Fire Emergency Panel, provide:
Incomer Metering Chamber:
• Provide a Separate Metering Chamber for the Incomer to house a 415V / √3 / 110V / √3 PT.
• Door to have R, Y, B (63.5V) LED indication lamps for incomer.
• Door to have MFM / Metering (110V) incomer metering.
• Door to have ON / OFF / TRIP Indication LED: 24V DC
Bus PT Chamber for metering of outgoing feeders:
Provide a separate Bus PT Chamber next to Bus coupler ACB section to house a 415V / √3 / 110V / √3 PT for MFM / Metering (110V) of outgoing feeders.
Outgoing feeders to have ON,OFF,TRIP LED Indication lamps:24VDC
B. For Motor Control Centres & Other Panels, provide:
Incomer Metering Chamber:
• Provide a Separate Metering Chamber for the Incomer to house a 415V / √3 / 110V / √3 PT.
• Door to have R, Y, B (63.5V) LED indication lamp for incomer.
• Door to have VAF / Metering (110V) incomer metering.
• Door to have ON, OFF, Trip Indication for incomer (110V).
Control Transformer Chamber:
Provide a separate Control Transformer Chamber to house a 415V (2 Phase) / 110V (1 Phase) Control Transformer for outgoing feeders for:
• ON / OFF / Trip Indication (110V) for out going feeders.
• Starter / Contactor Coils (110V) for out going feeders.
Notes:
• For 24V DC supply, battery & battery charger shall be employed, specified separately in another sub-head of the BOQ.
• ‘DC’ control cabling to be laid from Battery & Battery charger unit to ‘DC’ DB and then to:
o Main LT Panel
o DG Power Panel
o Main LT Panel cum DG Power Panel
o Fire Emergency Panel
GENERAL NOTES FOR TRANSIENT VOLTAGE SURGE SUPPRESSOR (TVSS):
Transient Voltage Surge Suppressors (TVSS) shall be mounted out side the panel / switch board in a sheet steel enclosure.
It shall be suitable for handling required (specified) surge handling capacity, shall be 10 modes protection with noise filters. (EMI & RFI) and with inbuilt back up fuse protection.
Surge suppressor shall be complete with isolating / protective device in the form of MCB / MCCB of KA rating (breaking capacity) as of switch board.
10 MODE transient voltage surge suppressor (MOV-Metal Oxide Varistors). It shall be complete with EMI & RFI filters. TVSS assembly cartrage shall be encapsulated inside a NEMA / an IEC enclosure & shall be completely sealed. It shall have inbuilt fuse protection & thermal disconnector and a RED LED indications or a mechanical flag for indication of end of life and a potential free contact for remote / BMS indication for end of lift. TVSS shall be Type B + Type C as per German Standard or Type 1 + Type 2 as per IEC standards.
Type 1 (Type B) : For Lightning Surges Type 2 (Type C) : For Switching Surges
10 Modes are :
a) RY, YB, BR 3
b) RN, YN, BN 3
c) RG, YG, BG, NG 4
Total 10 Modes
IMPORTANT NOTES FOR ELECTRICAL PANELS, SWITCHGEAR & MOTOR CONTROL CENTRES
SWITCHGEAR OF ONLY ONE MAKE / MANUFACTURER TO BE USED.
TYPE-2 CO-ORDINATION TO BE FOLLOWED.
ICS = ICU = 100% FOR THE MCCB'S, MPCB'S & ACB'S
MOTORISED (EDO) ACB’S SHALL HAVE CLOSING COIL, SHUNT TRIP COIL & UNDER VOLTAGE RELEASE.
MANUAL (MDO) ACB’S SHALL HAVE SHUNT TRIP COIL.
ACB’S UPTO 4000A SHALL BE SINGLE FRAME TYPE.
ALL ACB’s OF ALL RATINGS, MANUAL & MOTORISED SHALL BE OF DRAW OUT TYPE.
MCCB’S WITH FIXED THERMAL & MAGNETIC RELEASES, WHEREVER CALLED FOR, CAN ALSO BE WITH ADJUTABLE THERMAL & FIXED MAGNETIC, IF THIS COMES AS A STANDARD FEATURE OF THE PRODUCT.
MCCB’s UPTO 250A SHALL BE WITH FIXED RELEASES & ABOVE 250A SHALL BE WITH MICRO PROCESSOR BASED RELEASES.
MOTOR DUTY MPCB’S & MCCB’S TO BE SELECTED AS PER SWITCHGEAR MANUFACTURER’S RECOMMENDATION / CHARTS.
IN CASE OF ANY DISCREPANCY BETWEEN SPECIFICATIONS, BOQ & DRAWING (SLD), THE BEST
TEMPERATURE DERATION OF SWITCHGEAR TO BE TAKEN INTO ACCOUNT WHILE SELECTING IT EVEN IF IT IS NOT ACCOUNTED FOR IN THE BOQ / DRAWING (SLD).
MOTOR DUTY MCCB’S ARE AVAILABLE IN 50KA FAULT WITHSTAND CAPACITY, EVEN IF IT IS SPECIFIED OTHERWISE IN BOQ / DRAWINGS (SLD).
MPCB’S LESS THAN 36KA FAULT WITHSTAND CAPACITY NOT TO BE USED, EVEN IF IT HAS BEEN SPECIFIED OTHERWISE.
STANDARD RANGE OF MCCB’S IS:
16A, 25A, 32A, 40A, 50A, 63A, 80A, 100A, 125A, 160A, 225A, 250A, 320A, 400A, 500A, 630A
STANDARD FAULT WITHSTAND RATINGS OF MCCB’S ARE:
16KA, 25KA, 35KA/36KA, 50KA, 65KA/70KA, 100KA
STANDARD MPCB’S FAULT WITHSTAND RATINGS ARE:
25KA, 36KA, 50KA, 100KA, 150KA
MPCB’S UPTO 63A SHALL BE THERMAL-MAGNETIC TYPE WITH ADJUSTABLE O/L TRIP SETTING AND ABOVE 63A SHALL BE WITH MICROPROCESSOR BASED RELEASE.
ALL MCCB’S & MPCB’S SHALL BE WITH DIRECT / EXTENDED ROTARY HANDLES.
ARRANGEMENT OF PAD LOCKING & FOOL PROOF LOTO (LOCKOUT & TAG OUT) TO BE AVAILABLE WITH ALL MCCB’S & MPCB’S FOR MAINTENANCE, SERVICING, REPAIRS AND INSPECTION FOR SAFETY REASONS ON MOTORS / EQUIPMENT. ALSO, DOOR INTERLOCK DEFEAT FUNCTION SHOULD NOT BE PROVIDED.
CLIENT’s MAINTENANCE TEAM TO UTILIZE LOTO FEATURE BEFORE INITIATING ANY REPAIR / MAINTENANCE ON ALL ELECTRICAL EQUIPMENT / PUMPS / MOTORS / FANS / BLOWERS ETC.
ATS
For Main LT Panel, Fire Emergency Panel & DG Set Aux. Panel:
o ATS shall be ASCO Make Series 7000 for above 1200Amps and Series 300 below 1200 Amps or equivalent.
o Main LT Panel & Fire Emergency Panel shall have 4P ATS.
o DG Set Aux. Panel shall have 4P ATS.
o ATS with controller, controller with AMF function.
o ATS with 100% overlapping neutral.
o ATS: Solenoid operated, RS485 Communication.
o Utilization category: AC 33A.
o Same phase angle transition & in phase monitoring.
o 85KA for 0.3 sec (fault withstand)
For Lift Panel & UPS Input / Output Panels:
o ATS shall be ASCO Make Series 300 or equivalent
o 4P ATS
o ATS with 100% overlapping neutral.
o ATS: Solenoid operated.
o 85KA for 0.3 sec (fault withstand).
SWITCHGEAR SELECTION SHOULD ACHIEVE DISCRIMINATION EVEN IF IT IS NOT SHOWN IN BOQ / DRAWING (SLD).
BURDEN CALCULATIONS FOR CT’S, PT’S AND CONTROL TRANSFORMERS TO BE SUMITTED ALONG WITH SHOP DRWINGS.
INCOMER SWITCHGEAR, BUS BARS, SUPPORTS AND OUTGOING SWITCHGEAR SHALL BE OF SAME FAULT LEVEL WITHSTAND CAPACITY AS MENTIONED FOR THE PANEL.
SUGGESTED “MCCB” SELECTION FOR CAPACITOR APPLICATION WITH DETUNED FILTERS:
5 KVAR - 16A TP MCCB (TH + MG) – F
10 KVAR - 25A TP MCCB (TH + MG) – F
15 KVAR - 40A TP MCCB (TH + MG) – F
20 KVAR - 50A TP MCCB (TH + MG) – F
25 KVAR - 63A TP MCCB (TH + MG) – F
50 KVAR - 125A TP MCCB (TH + MG) – F
CAPACITORS SHALL BE HEAVY DUTY MPP CONSTRUCTION.
Automatic power Factor Correction relay in Capacitor panels: APFCR shall be microprocessor based , communicable type with RS485 port.
7% & 14% DETUNED REACTORS SHALL BE COPPER WOUND, CLASS H INSULATION.
DEDICATED COPPER EARTHING LINK OF SUITABLE SIZE ON INSULATED SUPPORTS FOR:
ALL UPS DB’S, PDU’S, UPS OUTPUT PANELS & FLOOR UPS PANELS/ SDB - UPS PANELS WILL HAVE A DEDICATED COPPER EARTH LINK OF ADEQUATE SIZE SUPPORTED ON INSULATED SUPPORTS FOR 3RD PIN EARTHING (ISOLATED GROUND).
THE GROUNDING EARTH LINK SHALL ALSO BE PROVIDED IN ADDITION TO DEDICATED EARTH BUS.
MOTOR FEEDERS
A. MOTOR FEEDERS WITH STARTERS:-
1. Upto 10 HP / 7.5 KW Motor
o 3P MPCB – TH + MG (Thermal Magnetic Release with adjustable O/L trip class).
o MPCB’S upto 63A shall be Thermal-Magnetic type with adjustable O/L trip setting and above 63A shall be with Microprocessor based release.
o DOL
2. From 12.5 HP / 9.3 KW to 40 HP / 30 KW Motors
o 3P MPCB – TH + MG (Thermal Magnetic Release with adjustable O/L trip class).
o MPCB’S upto 63A shall be Thermal-Magnetic type with adjustable O/L trip setting and above 63A shall be with Microprocessor based release.
o Star Delta
3. From 50 HP / 37 KW to 150 HP / 110 KW
o 3P MCCB – M (F) (Motor Duty – Fixed Release)
o Star Delta
o External Electronic O/L Relay with SPP
4. Above 150 HP / 110 KW Motors
o 3P MCCB – MP (Motor Duty – Micro Processor Base Release)
o Star Delta
o External Electronic O/L Relay with SPP
B. MOTOR FEEDERS WITH VFD’s
1. Upto 40 HP / 30 KW Motors
o 3P MPCB –MG (Magnetic Release)
o MPCB’S upto 63A shall be Magnetic release and above 63A shall be with Microprocessor based release.
o VFD
2. From 50 HP / 37 KW to 150 HP / 110 KW Motors
o 3P MCCB –M(F) (Motor Duty - Fixed Release)
o VFD
3. Above 150 HP / 110 KW Motors
o 3P MCCB – M (MP) (Motor Duty – Micro Processor Base Release)
o VFD
C. MOTOR FEEDERS WITH SOFT STARTERS
1. Upto 40 HP / 30 KW Motor
o 3P MPCB – MG (Magnetic Release)
o MPCB’S upto 63A shall be Magnetic release and above 63A shall be with Microprocessor based release.
o Soft Starter with inbuilt Bypass Contactor
2. From 50 HP/ 37 KW to 150 HP / 110 KW Motor
o 3P MCCB – M(F) (Motor Duty - Fixed Release)
o Soft Starter with inbuilt Bypass Contactor
3. Above 150 HP / 110 KW Motor
o 3P MCCB – M (MP) (Motor Duty – Micro Processor Base Release)
o Soft Starter with inbuilt Bypass Contactor
4. Soft starters for fire pumps shall be with programmable auxilary contacts for BMS connectivity.
D. JET FAN 2 STAGE STARTER
o 3P MPCB – MG (Magnetic Release)
o 2 Stage Starter
o Overload Relay & SPP
Note: Cost shall inculde Elastomer mat 1000 mm. wide, 2mm thick, for upto 3.3kV grade as per Latest BIS Codes (IS: 15652/2006). (Vendor to check the thickness of the mat as per latest IS code & Quoe accordingly and also mention the thickness provided) for all the floor mount panel. Vendor to include the same required quantity
Following Panels as per attached Electrical Single Line Diagram:
1 | MR | LT PANEL | Set |  | 1
2 | MR | AHU PANEL | Set |  | 1
3 | MR | TERRACE CHILLER PANEL | Set |  | 1
4 | MR | EV CAR CHARGING PANEL | Set |  | 1
5 | MR | EV FAST CAR CHARGING PANEL-2 | Set |  | 1
6 | MR | 4 WAY PPI TPN EV CHARGING DB | Set |  | 10
7 | MR | EV FAST CAR CHARGING PANEL-1 | Set |  | 1
8 | MR | WS UPS INPUT PANEL | Set |  | 1
9 | MR | WS UPS OUTPUT PANEL | Set |  | 1
10 | MR | MDB-9F LHS UPS | Set |  | 1
11 | MR | MDB-8F LHS UPS | Set |  | 1
12 | MR | MDB-7F LHS UPS | Set |  | 1
13 | MR | MDB-6F LHS UPS | Set |  | 1
14 | MR | MDB-5F LHS UPS | Set |  | 1
15 | MR | MDB-4F LHS UPS | Set |  | 1
16 | MR | MDB-3F LHS UPS | Set |  | 1
17 | MR | MDB-2F LHS UPS | Set |  | 1
18 | MR | MDB-1F LHS UPS | Set |  | 1
19 | MR | MDB-GF LHS UPS | Set |  | 1
20 | MR | IT UPS INPUT PANEL-1 (W) | Set |  | 1
21 | MR | IT UPS INPUT PANEL-2 (S) | Set |  | 1
22 | MR | IT UPS OUTPUT PANEL-1 (W) | Set |  | 1
23 | MR | IT UPS OUTPUT PANEL-2 (S) | Set |  | 1
24 | MR | PDU-1 (W) 9F | Set |  | 1
25 | MR | PDU-1 (S) 9F | Set |  | 1
26 | MR | PDU-1 (W) 8F | Set |  | 1
27 | MR | PDU-1 (S) 8F | Set |  | 1
28 | MR | PDU-1 (W) 6F | Set |  | 1
29 | MR | PDU-1 (S) 6F | Set |  | 1
30 | MR | PDU-1 (W) 5F | Set |  | 1
31 | MR | PDU-1 (S) 5F | Set |  | 1
32 | MR | PDU-1 (W) 4F | Set |  | 1
33 | MR | PDU-1 (S) 4F | Set |  | 1
34 | MR | PDU-1 (W) 3F | Set |  | 1
35 | MR | PDU-1 (S) 3F | Set |  | 1
36 | MR | PDU-1 (W) 2F | Set |  | 1
37 | MR | PDU-1 (S) 2F | Set |  | 1
38 | MR | PDU-1 (W) 1F | Set |  | 1
39 | MR | PDU-1 (S) 1F | Set |  | 1
40 | MR | PDU-1 (W) 1F SERVER ROOM | Set |  | 1
41 | MR | PDU-1 (S) 1F SERVER ROOM | Set |  | 1
42 | MR | PDU-1 (W) GF | Set |  | 1
43 | MR | PDU-1 (S) GF | Set |  | 1
44 | MR | SDB L+P PANEL 9F | Set |  | 1
45 | MR | AHU PANEL-1 (9F-LHS) | Set |  | 1
46 | MR | AHU PANEL-2 (9F-RHS) | Set |  | 1
47 | MR | SDB L+P PANEL 8F | Set |  | 1
48 | MR | AHU PANEL-1 (8F-LHS) | Set |  | 1
49 | MR | AHU PANEL-2 (8F-RHS) | Set |  | 1
50 | MR | 100A, 4P MCCB-7F | Set |  | 1
51 | MR | SDB L+P PANEL-1 (7F) | Set |  | 1
52 | MR | SDB L+P PANEL-2 (7F) | Set |  | 1
53 | MR | STARTER PANEL-1 VENT -7F | Set |  | 1
54 | MR | STARTER PANEL-2 VENT -7F | Set |  | 1
55 | MR | AHU PANEL-1 (7F-LHS) | Set |  | 1
56 | MR | AHU PANEL-2 (7F-RHS) | Set |  | 1
57 | MR | SDB L+P PANEL 6F | Set |  | 1
58 | MR | AHU PANEL-1 (6F-LHS) | Set |  | 1
59 | MR | AHU PANEL-2 (6F-RHS) | Set |  | 1
60 | MR | SDB L+P PANEL 5F | Set |  | 1
61 | MR | AHU PANEL-1 (5F-LHS) | Set |  | 1
62 | MR | AHU PANEL-2 (5F-RHS) | Set |  | 1
63 | MR | SDB L+P PANEL 4F | Set |  | 1
64 | MR | AHU PANEL-1 (4F-LHS) | Set |  | 1
65 | MR | AHU PANEL-2 (4F-RHS) | Set |  | 1
66 | MR | SDB L+P PANEL 3F | Set |  | 1
67 | MR | AHU PANEL-1 (3F-LHS) | Set |  | 1
68 | MR | AHU PANEL-2 (3F-RHS) | Set |  | 1
69 | MR | SDB L+P PANEL 2F | Set |  | 1
70 | MR | AHU PANEL-1 (2F-LHS) | Set |  | 1
71 | MR | AHU PANEL-2 (2F-RHS) | Set |  | 1
72 | MR | 100A, 4P MCCB-FF | Set |  | 1
73 | MR | SDB L+P PANEL FF | Set |  | 1
74 | MR | AHU PANEL-1 (FF-LHS) | Set |  | 1
75 | MR | AHU PANEL-2 (FF-RHS) | Set |  | 1
76 | MR | STARTER PANEL-1 VENT -FF | Set |  | 1
77 | MR | STARTER PANEL-2 VENT -FF | Set |  | 1
78 | MR | SDB L+P PANEL GF | Set |  | 1
79 | MR | AHU PANEL-1 (GF-LHS) | Set |  | 1
80 | MR | AHU PANEL-2 (GF-RHS) | Set |  | 1
81 | MR | SDB L+P PANEL UPS ROOM | Set |  | 1
TOTAL CARRIED OVER TO SUMMARY
SUB HEAD J |  | UPS
1 | MR | UPS FOR WORK STATIONS - 300KW
Digital Signal Processor (DSP) based 1 Nos. x 300KW in 400KVA/KW frame (5x60kVA/KW or 6X50kW )Modular UPS , IGBT based rectifier to achieve input THDI < 5% and input power factor 1.0 at 100% loading. True Online Double Conversion (VFI as per IEC 62040-3) UPS using PWM IGBT technology, 3 Phase input and 3 phase 415V output UPS system; and each comprising of the following: Each UPS module with integrated 100% rectifier + inverter.Each UPS to have external paralleling feature for minimum 5 units along with inbuilt phase sequence corrector and Backfeed contactor Fully rated, unity power factor designed hot scalable & hot swappable power module and hot swappable static switch.Power Module to be integrated inside a single frame to achieve 400KW rating. It should possible to add or replace power modules and static switch without switching the load to bypass source i.e both power modules and static switch needs to be hot swappable(Documentary proof to be shared). Notification should be provided on the UPS intergrated display for add or removal of Power module.UPS to have sleep mode feature for energy saving and module awakening time to be less 2msec.Each Modular Chassis to have inbuilt input,output, bypass and mnaitenance bypass isolators as a mandatory requirement .
RS 485 BACnet / Modbus protocol with each UPS System for BMS Connectivity. All the information to be provided to the BMS vendor at one point. UPS Efficiency to be greater than 97.5% @ 25%, 50% and 75% Load and to be greater than 96.5% @ 100% Load(.Type test report of UPS to be shared along with bid in accordance with IEC62040-3-2021 standard only from NABL accrediated body/lab) Interconnecting Control Cabling between UPS, Battery breaker & Batteries, UPS to transformer (DC Cable Cu.) of required length and size. Each UPS shall have a SNMP card for LAN/WEB connectivity. The SNMP card shall have an inbuilt memory for event logging and should be inlined with UL2900 and must be VAPT tested by CERT-IN(TEST CERTIFICATE TO BE SUBMITTED) Suitable MS stand as per false floor depth/Condition at site for each UPS and Battery duly painted for each UPS. Self-Synchronization in the event of control module failure, full control logic at the power module level allows the system to self-synchronize for assured continuous operation. RAM Module/Relay card with each UPS and Cat 5 cable for RAM connectivity. Necessary Top Covered racks, Linksets and DC cable
1.1 |  | Chassis Only for Modular UPS having hot swappable static switch with all accessories | Set |  | 3
1.2 |  | Hot Swappable UPS Power Modules: 50KW/60KW for 300KVA/300KW in 400KW Chassis Note: The quantity of modules required for the 50 kW Power Module is 18 units. Bidders are requested to update the quantity accordingly while submitting their bids. | Set |  | 18
1.3 |  | UL9540A certified Lithium Ion batteries at Cell Level, module level and at rack level (A mandatory certificate/Reports needs to be shared along with bid for verification along with ) with NMC/NMC+LMO Chemistry for 300 kW load at Unity PF with 15 Mins backup time for each UPS shall be provided) with interconnectors, Cabinet and Accessories. Battery monitoring system of lithium ion batteries to be connected with existing BMS system ,Each Strings should have its own breaker and its own BMS.. Offered batetries to have mandatory UL 991 applies to controls using solid-state devices used in LIB and UL 1998 pertains to software in programmable components ,UL1973 applicable for BMS thermal , electrical and mechanical safety and UL1642 for safe design, construction, and performance of lithium battery cells . Inbuilt Rack based Battery Monitoring System: Monitor + Control along with balance charging. Individual Module Level, Rack Level & System Level shall be provided with each UPS with LIB system. The BMS shall provide SOC (State of Charge), SOH (State of Health), Voltage and Temperature for each Cell and Module within the LIB rack. The PC based external BMS is not acceptable.All accesories related to lithium ion batteries to be considered to ensure complete installation such as power supply ,MCB,cabling, JB etc.
|  | Lithium-ion batteries should be supplied according to the OEM standard model, complete with a Battery Management System (BMS) and rack provided by the OEM of the lithium-ion batteries. This ensures the highest quality and maintains all applicable safety certifications at the rack level. The quoted model should also be listed on the global OEM website or available on the UPS OEM website.A proper User manual of offered and product brichure Lithium ion battery can be downloaded from OEM Website -A Link to be provided along with the bid NOTE: Only original certificates/reports will be accepted, and each report must clearly mention the correct model number. | Set |  | 9
1.4 |  | External Galvanic Isolation transformer K-13-Copper, at the input of each UPS, capacity same as of Full chassis rating as per OEM. All Isolation Transformers shall have same impedance should be haing input breaker, Auto soft starter and Top and Bottom Cable Entry and RAL Code to be matched UPS RAL code | Set |  | 3
2 | MR | CRITICAL LOADS - SERVER /HUB ROOM - 240KW
Digital Signal Processor (DSP) based 1 Nos. x 240KW+ 1 Extra Module for redundancy in 300KVA/KW frame (5x60kVA/KW or 6X50kW )Modular UPS , IGBT based rectifier to achieve input THDI < 5% and input power factor 1.0 at 100% loading. True Online Double Conversion (VFI as per IEC 62040-3) UPS using PWM IGBT technology, 3 Phase input and 3 phase 415V output UPS system; and each comprising of the following: Each UPS module with integrated 100% rectifier + inverter.Each UPS to have external paralleling feature for minimum 5 units along with inbuilt phase sequence corrector and Backfeed contactor Fully rated, unity power factor designed hot scalable & hot swappable power module and hot swappable static switch.Power Module to be integrated inside a single frame to achieve 400KW rating. It should possible to add or replace power modules and static switch without switching the load to bypass source i.e both power modules and static switch needs to be hot swappable(Documentary proof to be shared). Notification should be provided on the UPS intergrated display for add or removal of Power module.UPS to have sleep mode feature for energy saving and module awakening time to be less 2msec.Each Modular Chassis to have inbuilt input,output, bypass and mnaitenance bypass isolators as a mandatory requirement .
RS 485 BACnet / Modbus protocol with each UPS System for BMS Connectivity. All the information to be provided to the BMS vendor at one point. UPS Efficiency to be greater than 97.5% @ 25%, 50% and 75% Load and to be greater than 96.5% @ 100% Load(.Type test report of UPS to be shared along with bid in accordance with IEC62040-3-2021 standard only from NABL accrediated body/lab) Interconnecting Control Cabling between UPS, Battery breaker & Batteries, UPS to transformer (DC Cable Cu.) of required length and size. Each UPS shall have a SNMP card for LAN/WEB connectivity. The SNMP card shall have an inbuilt memory for event logging and should be inlined with UL2900 and must be VAPT tested by CERT-IN(TEST CERTIFICATE TO BE SUBMITTED) Suitable MS stand as per false floor depth/Condition at site for each UPS and Battery duly painted for each UPS. Self-Synchronization in the event of control module failure, full control logic at the power module level allows the system to self-synchronize for assured continuous operation. RAM Module/Relay card with each UPS and Cat 5 cable for RAM connectivity. Necessary Top Covered racks, Linksets and DC cable .
2.1 |  | Chassis Only for Modular UPS having hot swappable static switch with all accessories | Set |  | 2
2.2 |  | Hot Swappable UPS Power Modules: 50KW/60KW for 240KW/250KW in 300KW Chassis Note: The quantity of modules required for the 50 kW Power Module is 12 units. Bidders are requested to update the quantity accordingly while submitting their bids. | Set |  | 10
2.3 |  | UL9540A certified Lithium Ion batteries at Cell Level, module level and at rack level (A mandatory certificate/Reports needs to be shared along with bid for verification along with ) with NMC/NMC+LMO Chemistry for 200 KVA load at unity PF with 90 Mins backup time for each UPS shall be provided(Battery Calculation sheet to be shared considering all mentioned parameters) with interconnectors, Cabinet and Accessories. Battery monitoring system of lithium ion batteries to be connected with existing BMS system ,Each Strings should have its own breaker and its own BMS.. Offered batetries to have mandatory UL 991 applies to controls using solid-state devices used in LIB and UL 1998 pertains to software in programmable components ,UL1973 applicable for BMS thermal , electrical and mechanical safety and UL1642 for safe design, construction, and performance of lithium battery cells . Inbuilt Rack based Battery Monitoring System: Monitor + Control along with balance charging. Individual Module Level, Rack Level & System Level shall be provided with each UPS with LIB system. The BMS shall provide SOC (State of Charge), SOH (State of Health), Voltage and Temperature for each Cell and Module within the LIB rack. The PC based external BMS is not acceptable.All accesories related to lithium ion batteries to be considered to ensure complete installation such as power supply ,MCB,cabling, JB etc.
|  | Lithium-ion batteries should be supplied according to the OEM standard model, complete with a Battery Management System (BMS) and rack provided by the OEM of the lithium-ion batteries. This ensures the highest quality and maintains all applicable safety certifications at the rack level. The quoted model should also be listed on the global OEM website or available on the UPS OEM website.A proper User manual of offered and product brichure Lithium ion battery can be downloaded from OEM Website -A Link to be provided along with the bid NOTE :- Only original certificates/reports will be accepted, and each report must clearly mention the correct model number. | Set |  | 18
2.4 |  | External Galvanic Isolation transformer K-13-Copper, at the input of each UPS, capacity same as of Full chassis rating as per OEM. All Isolation Transformers shall have same impedance should be haing input breaker , Auto soft starter and Top and Bottom Cable Entry and RAL Code to be matched UPS RAL code | Set |  | 2
Notes: Base frames for UPS and batteries up to the height of the raised floor to be considered. All necessary coordination with the Electrical contractor, AC contractor and BMS vendor for complete integration. Quoted prices to include cost of equipment including Packing, Forwarding charges, Transport Charges, Transit insurance, loading etc. Quoted price to include cost of supervision of installation and commissioning of above UPS systems. All UPS Systems shall have 3 year Warranty. All 12 V Batteries shall have 2 years Warranty. All Complete LIB shall have 10 years Warranty Full load test at factory-Factory Acceptance Test to be Conducted and report to be shared for each UPS. Cost to include visit to OEM factory before delivery of materials at site for a FAT, process and quality inspection of the proposed materials in the tender under this head for 3 persons from user / project manager / designer firm. Note: Cost shall inculde Elastomer mat 1000 mm. wide, 2mm thick, for upto 3.3kV grade as per Latest BIS Codes (IS: 15652/2006). (Vendor to check the thickness of the mat as per latest IS code & Quoe accordingly and also mention the thickness provided) for UPS, Batteries & Isolation Transformers. Vendor to include the same required quantity.
TOTAL CARRIED OVER TO SUMMARY
SUB HEAD K1 |  | FIRE DETECTION AND ALARM SYSTEM
Design, Supply, installation, testing & commissioning of UL Listed & FM Approved Fire Detection & Alarm system as per local fire norms & NBC / NFPA Codes:
1 | MR | Fire Panel & Annunciators
1.1 | MR | 10-loop - With Digital Voice Command Center | Nos. |  | 1
1.2 | MR | 8-loop - Without Digital Voice Command Center | Nos. |  | 2
Supplying, installing, testing and commissioning approved make Microprocessor based Multi- loop, Networkable Addressable Fire Alarm Control Panel with minimum 10 inch 1024x600 resolution LCD with touch capability, including audible and visible feedback, backlit by a long life, solid-state LCD. It shall also include a full QWERTY-style keypad on the color, touchscreen display. The display shall have the ability to scroll events by type (i.e. Fire Alarm, Supervisory Alarm, Trouble, etc) using the touchscreen with customizable buttons, 10000 history events & autolearn feature for programming. The system can be supported upto 2000 generation zone & 2000 logic zone & 50 releasing zone. The panels in network having true peer to peer provision. The panel shall have provision to support up to 50 releasing zones to protect against 50 independent hazards.
The panel should be equipped with sufficient numbers of loops considering 20% spare capacity in each loop and shall be extendable upto 10 Loops. Each loop shall have a capacity of minimum 125 detectors & 125 other devices excluding 20% spare. The panel shall work in degrade mode in case of CPU failure, Products not having this feature may offer Redundant CPU. Four access levels, flash EPROM, 240 volts AC power supply, automatic battery charger, 24 volts sealed lead acid batteries sufficient for 24 hours normal working and 30 mins in alarm condition with the charging capacity of 210AH. The panel shall be capable of auto-learn programing feature without any dependency on dongle or programming software.. Quoted rate shall include supply of necessary software & hardware for programming the panel with all necessary license. Panel shall have Modbus/ Bacnet over IP protocol for future integration with BMS. However, for present arrangement FA system will be standalone with 24x7 monitoring. The panel shall have the provision for cloud connectivity for remote off site monitoring & control through a mobile app and shall be Cyber Security Compliant. Panel shall be UL Listed (864 10th edition) & FM Approved for both Fire & Gas detection (FM6320) and Evacuation.
The Fire Fighters Telephone System shall be capable of having minimum 30 Telephones in conference in multiple FFT Risers. The panel shall be capable of self programing without any dependancy on dongle or programming software. Quoted rate shall include supply of necessary software & hardware for progamming the panel with all necessary licence. Panel shall have Modbus/ Bacnet over IP protocol for future integration with BMS. However, for present arrangement FA system will be standalone with 24x7 monitoring.
All Product will be latest technology/version only. Designed to meet UL864, 10th Edition & FM Approved.
1.3 | DSR-2025 28.2.3 | Network Repeater Panel | Set |  | 2
Supplying, installing, testing and commissioning of Network Repeater Panel with minimum 10" Color Touch Screen display or 640 Character Display with QWERTY Keypad, mapping minimum 2,00,000 points on network. The NRP shall act as an independent node communicating on the peer to peer network and shall not be dependant on the Fire Panel CPU for operation. Failure of Fire Panel CPU shall not result in failure of NRP operation. UL & FM Approved
2 |  | Software & Gateways
2.1 | DSR-2025 28.2.2 | Graphics User Interface for Monitoring & Control | Sets |  | 1
Supplying, installing, testing and commissioning of Graphics User Interface for Monitoring & Control of complete Fire, Voice Evacuation & Telephone Talkback System. The GUI based main network software shall network with other panels on True Peer-to-Peer network. It shall be capable of graphically representing each facility being monitored with floor plans and icons depicting the actual locations of the various systems, and / or sensors’ locations. It shall have the facility to change the sensitivity of any detector. The software shall be capable of monitoring 200 Nodes with 100 Mbps Transmission rate on Fibre Optics Network and 12 Mbps Transmission on cable and 2,50,000 network points. The software shall be capable to Monitor & Control all the Digital Voice Evactuation as well as 2 way communication from main control room using voice signals over Fire Network along with the Fire detection signal.
The Graphic workstation shall act as an independent node communicating on the peer to peer network and shall not be dependant on the Fire Panel CPU for operation. Failure of Fire Panel CPU shall not result in failure of GUI. Important to Note: GUI should be able to display all Fire Damper Status on single screen.
2.2 | MR | PC - 4th Generation Intel Core i5 processor | Sets |  | 1
Supply, installing, testing and commissioning of 4th Generation Intel Core i5 processor, 1 TB HDD, 4 GB DDR3 RAM, DVD Drive (Reads and Writes DVD), 1 GB Graphic Card, Network: 100/1000 Mb Ethernet network card, PC with 18" TFT monitor, key board & mouse for loading all the CAD fire detection drawings of the buildings / floors WITH Fire Graphics Software & Network card for loading on to "Fire PC" through a dongle.
2.3 | DSR-2025 28.2.18 | MODbus Interface Gateway for communication with BMS / Other Utilities | No. |  | 1
Supplying, installing, testing and commissioning of MODbus Interface Gateway for communication with BMS / Other Utilities. MODbus shall support minimum 14000 data points. MODbus Gateway shall act as an independent node communicating on the peer to peer network and shall not be dependant on the Fire Panel CPU for operation. Failure of Fire Panel CPU shall not result in failure of MODbus Gateway. UL & FM Approved
3 |  | Detectors
3.1 | MR | MULTI-CRITERIA with Inbuilt Isolators (PHOTO-THERMAL) DETECTOR | Nos. |  | 1657
Supply, installing, testing and commissioning of UL 268 listed 7th Edition addressable intelligent Multi-Criteria (Photo-Thermal) detector with sensitivity range of 0.5 to 4.0% obs/ft with mounting base, dual LED, complete with base as required with inbuilt isolators. The intelligent multi criteria detection device shall include the ability to combine the signal of the thermal sensor with the signal of the photoelectric signal in an effort to react hastily in the event of a fire situation. It shall also include the inherent ability to distinguish between a fire condition and a false alarm condition by examining the characteristics of the thermal and smoke sensing chambers and comparing them to a database of actual fire and deceptive phenomena. Addressing shall be with user friendly rotary /decade switches. The supplied product shall be fully compliant with the European Union's Restriction of Hazardous Substances (RoHS) Directive (2011/65/EU, including amendment 2015/863/EU) and shall be supported by a signed Declaration of Conformity (DoC).
3.2 | MR | MULTI-CRITERIA with Inbuilt Isolators (PHOTO-THERMAL) DETECTOR | Nos. |  | 1540
Supply, installing, testing and commissioning of UL 268 listed 7th Edition addressable intelligent Multi-Criteria (Photo-Thermal) detector with sensitivity range of 0.5 to 4.0% obs/ft with mounting base, dual LED, complete with base as required with inbuilt isolators. The intelligent multi criteria detection device shall include the ability to combine the signal of the thermal sensor with the signal of the photoelectric signal in an effort to react hastily in the event of a fire situation. It shall also include the inherent ability to distinguish between a fire condition and a false alarm condition by examining the characteristics of the thermal and smoke sensing chambers and comparing them to a database of actual fire and deceptive phenomena. Addressing shall be with user friendly rotary /decade switches. The supplied product shall be fully compliant with the European Union's Restriction of Hazardous Substances (RoHS) Directive (2011/65/EU, including amendment 2015/863/EU) and shall be supported by a signed Declaration of Conformity (DoC).
3.3 | MR | HEAT DETECTOR with Inbuilt Isolators | Nos. |  | 45
Supply, installing, testing and commissioning of UL 521 listed addressable intelligent Rate of Rise Heat Detector rated at 8.3°C/min with Inbuilt Isolators with mounting base, dual LED, complete with base as required. Addressing shall be with user friendly rotary /decade switches. The supplied product shall be fully compliant with the European Union's Restriction of Hazardous Substances (RoHS) Directive (2011/65/EU, including amendment 2015/863/EU) and shall be supported by a signed Declaration of Conformity (DoC).
3.4 | DSR-2025 28.2.5 | Response indicator | Nos. |  | 1540
Supplying, installing, testing and commissioning of Response indicator for all detectors located above false ceiling
3.5 | MR | Multisensor (Smoke + Heat + CO + IR) Detector (UPS, Battery and Server Room) | Nos. |  | 2
Supplying, installing, testing and commissioning of Addressable Multisensor (Smoke + Heat + CO + IR) Detector. The detector shall have four sensing elements viz. Photo electric smoke, Heat, Carbon Monoxide & Infra Red Flame detection combined in a single detector. The detector shall have twin bi-colour LED for 360 deg viewing. Addressing shall be with user friendly rotary decimal switches. The internal CO Sensor should be replaceable upon EOL. It should be possible to generate 2 distinctive tones if the CO concentration reaches 2 definite user defined levels. UL Approved
3.6 | MR | LPG/PNG SENSOR | Nos. |  | 2
Supplying, installing, testing and commissioning of Supply, installing, testing and commissioning of UL listed LPG Leakage detector with mounting base as required.. UL & FM Approved
4 | MR | Modules
4.1 | 2017-02-28 | Addressable Double Action Manual Pull Station (Manual Call Point) | Nos. |  | 30
Supplying, installing, testing and commissioning of Addressable Double Action Manual Pull Station (Manual Call Point). The device shall have an LED which shall blink in normal state & get steady on activation to monitor the heath status of the device. UL & FM Approved
4.2 | DSR-2025 28.2.10 | Addressable Control Module
Supplying, installing, testing and commissioning of Addressable Control Module for Sounders / Strobes / Sounder cum Strobes. The control module shall provide supervised NAC output rated at 24v DC, 2A. The device shall have an LED which shall blink in normal state & get steady on activation to monitor the heath status of the device. Addressing shall be with user friendly rotary decimal switches. Module shall be supplied with mounting plate from OEM for ease of installation & maintenance. UL & FM Approved
a. | DSR-2025 28.2.10 | Addressable Control Module - Fireman's Telephone jack circuits (Fireman's module) | Nos. |  | 12
b. | DSR-2025 28.2.10 | Addressable Control Module - Speakers Circuit | Nos. |  | 21
c. | DSR-2025 28.2.10 | Addressable Control Module - Hooters for Pull cord Alarm Circuit | Nos. |  | 33
4.3 | MR | Addressable Relay Module
Supplying, installing, testing and commissioning of Addressable Relay Module for AHU, Access Control, Lifts, Staircase Pressurization, Fire Suppression & other Third Party Outputs. The relay module shall provide contact rated at 24v DC, 2A. The device shall have an LED which shall blink in normal state & get steady on activation to monitor the heath status of the device. Addressing shall be with user friendly rotary decimal switches. Module shall be supplied with mounting plate from OEM for ease of installation & maintenance. UL & FM Approved
a. |  | Addressable Relay Module - Sending tripping signal to AHU's, Fire & Smoke Dampers (One for each AHU room) | Nos. |  | 20
d. |  | Addressable Relay Module - Sending fire signal to Existing Base Builder Panel. | Nos. |  | 2
e. |  | Addressable Relay Module - Sending signal to Access control system to de-energise locks | Nos. |  | 2
f. |  | Addressable Relay Module - Sending tripping signal to each Pr. AC's unit & Ceiling suspended AHU's (One for each unit) of server room/Hub Room | Nos. |  | 22
4.4 |  | Addressable Monitor Module
Supplying, installing, testing and commissioning of Addressable Monitor Module for Sprinklers, Panic Bars & other Third Party Inputs. The monitor module shall monitor potential free contacts. The device shall have an LED which shall blink in normal state & get steady on activation to monitor the heath status of the device. Addressing shall be with user friendly rotary decimal switches. Module shall be supplied with mounting plate from OEM for ease of installation & maintenance. UL & FM Approved
a. |  | Addressable Monitor Module - Receiving signal from Water leak detection & WLD panel | Nos. |  | 26
c. |  | Addressable Monitor Module - To get Fire Damper Status New and existing base builder. | Nos. |  | 22
d. |  | Addressable Monitor Module - Receiving signal from Existing Panel from Base Buillder. | Nos. |  | 2
4.5 | DSR-2025 28.2.7 | Isolator Module | Nos. |  | 129
Supplying, installing, testing and commissioning of Isolator Module for Isolating short / dewired / loose circuits with automatic resetting arrangement. Isolator Base can also be proposed, however in that case needs to be considered with each detector & module. The device shall have an LED which shall blink in normal state & get steady on activation to monitor the heath status of the device. Module shall be supplied with mounting plate from OEM for ease of installation & maintenance.
5 |  | Notification Devices
5.1 | DSR-2025 28.2.15 | Sounder cum Strobe | Nos. |  | 30
Supplying, installing, testing and commissioning of Sounder cum Strobe rated at 80 dBA @ 3m for Audible annunciation and 115cd flashintg at 1 Hz for visual indication. UL Listed
6 | MR | Addressable Power Supply Unit | Nos. |  | 3
Supplying, installing, testing and commissioning of Addressable Power Supply Unit: 24V DC for Notification Appliances.
7 |  | Telephone Talkback
7.1 | DSR-2025 28.2.17 | Addressable Fire Fighter's Telephone Jack | Nos. |  | 11
Supplying, installing, testing and commissioning of Addressable Fire Fighter's Telephone Jack with suitable supervised module for two way communication between Remote Fire Fighter & Fire Command Center. UL Listed
7.2 | DSR-2025 28.2.19 | Portable type Fire Telephone Handset | Nos. |  | 4
Supplying, installing, testing and commissioning of Portable type Fire Telephone Handset for two way communication between Remote Fire Fighter & Fire Command Center. UL Listed
7.3 |  | Pull cord Alarm system suitable for Handicap Toilets | Nos. |  | 26
Supplying, installing, testing and commissioning of Pull cord Alarm system suitable for Handicap Toilets for Initiating Emergancy Alarm.
8 |  | Public address and Voice alarm systems
8.1 | DSR-2025 28.3.2 | 1.5/3/6W Ceiling Mount Speakers | Nos. |  | 1306
Supplying, installing, testing and commissioning of 6W Ceiling Mount Speakers with 1.5W/3W/6W tapping's and required accessories. They shall be compatible with supplied Amplifiers and shall work on 100V.
8.2 | DSR-2025 28.3.4 | 1.5/3/6W Wall Mount Speakers | Nos. |  | 84
Supplying, installing, testing and commissioning of 6W metal box ceiling/wall mount speakers with 1.5W/3W/6W tapping's and required accessories. They shall be compatible with supplied Amplifiers and shall work on 100V.
8.3 | MR | 7.5/15W Horn Speakers | Nos. |  | 28
Supplying, installing, testing and commissioning of 15W horn speakers with 7.5W/15W tapping's and required accessories. They shall be compatible with supplied Amplifiers and shall work on 100V.
8.4 | MR | EN-54-16 certified IP based digital voice alarm network controller | Nos. |  | 1
Supply, installation, testing & commissioning of Master EN-54-16 certified 16 Zone IP based digital voice alarm network controller with built in SIP Intercom, redundant IP connection, redundant power supply unit built with following features: Voice alarm controller should be able to connect directly over Ethernet & LCD display for displaying troubles, events. It should have functions like audio playing, zone control, fault monitoring, log recording, volume control and amplifier switchover. Network controller shall also have following functions. - Able to handle 16 simultaneous audio channels in the controller and upto 96 loudspeakers lines - Built in DSP with 10 band parametric EQ for each output - In-built digital message storage with minimum 16GB capacity - in Built 16 relay contact input and 6 relay contact output -Automatic fault diagnostic & reporting at central location from call station till amplifiers, loudspeaker circuits. -Matrix controller shall have analog audio input lines for music Sources, Fire Alarm Signals - Integration with External systems, like PIDS or Scada, can get full control of the PA by opening a TCP socket to the mainframe. More than one client is allowed. - Connection with external equipment by VOIP,XML Commands, DLL -Graphic display integrated controller. Automatic backlight with LED - Automatic fault diagnostic & reporting at central location from call station till amplifiers, loudspeaker circuits.
8.5 | MR | Class-D digital Power amplifiers | Nos. |  | 18
Supply, installation, testing & commissioning of 1000W Class-D digital amplifiers. Unit shall have following features & shall comply to technical specifications. 1. Amplifier should have dual power supply 2. Protected against overload, short circuits and over-heating 3. Built-in fan with temperature-controlled rotation speed control, with airflow from front to back of device.
8.6 | MR | IP TOUCH SCREEN CALL STATION | Nos. |  | 1
Supply, installation, testing & commssioning of 7INCH TOUCH SCREEN CALL STATION OVER IP with graphic display Allows broadcasting announcements through an IP network in streaming as well as unit control and configuration parameters with followings: - Ethernet connection -Minimum 46 Zone capacity - Runs the PA Manager control software and Graphic display with configurable position of buttons and background images to facilitate the user operation. - IP control of all the situations in the installation: - Zones and groups buttons for selection. - Live or pre-recorded messages activation. - PA system surveillance. - Modification of zones volume or equalization. - Zone status indication. - Announcements with or without a pre-announcement tone (Gong). - Gong that can be personalised.
8.7 | MR | Supply, installation, testing & commssioning of 6W volume controller with override relay and required accessories | Nos. |  | 182
8.8 | MR | Rack for PA System | Nos. |  | 1
Supply, Installation, Testing & commissioning of 42U floor standing Rack with all required accessories as per the Tender specification and as directed by engineer in charge
9 | DSR-2025- 28.5.1 | Supplying & laying of 2x1.5 sqmm fire survival armoured cable, 600/1000V rated with annealed copper conductor having glass mica fire barrier tape covered by an extruded layer of Cross Linkable Ethylene Propylene Rubber (EPR) insulation and LSZH inner bedding, steel wire armouring & LSZH outer sheath complete as required
9.1 |  | For FDA | RM |  | 32300
9.2 |  | For Speakers | RM |  | 15350
Notes:
a. All hooters / strobes shall also be power wired directly from the fire control panel will 2x1.5 sq.mm in separate conduits in a loop.
b. Necessary interlocking, relays, power supplies and wiring etc. that may be required to automatically start smoke exhaust fans and staricase / lift well pressurization fans and to stop automatically air-conditioning plant and indoor air supply units and fire dampers on the detection of a fire signal through the fire alarm panel to be included in the scope of work and costs quoted above. It should also ensure automatic opening of all access controlled doors on fire signal.
c. It will be an absolute responsibility of the contractor to ensure design of fire safety system / sequence as per NFPA / NBC / Indian standards.
d. Contractor shall submit the fire life safety sequence of operation of various exhaust and pressurization fans and AC plants for approval to client / architect / consultant before implementation.
e. Contractor to submit fire detection schematic.
f. Project Specific MAF (Manufacturer's Authorization Form) Certificate required from OEM to ensure the System Integrator is authorized & that the OEM will support the System Integrator before execution & during execution of the project.
TOTAL CARRIED OVER TO SUMMARY
SUB HEAD K2 |  | VESDA (ASPIRATION) SYSTEM (FOR SERVER, UPS & BATTERY ROOMS)
For Server Room Battery & UPS Rooms
1 | MR | Loop based addressable type Short wavelength, laser based ultra high sensitive aspiration smoke detector | Nos. |  | 3
SITC of Loop based addressable type Short wavelength, laser based ultra high sensitive aspiration smoke detector with sensitivity range of 0.005 % OBS / m TO 20 % OBS / M, having 1 pipe inlets, shall support minimum 100 meters pipe length per pipe, inlet Area Coverage 700 Sq.M to 1,000 Sq.M by one pipe single detector, 4 alarm levels, auto cleaning mechanism for detection chamber, on-board dual stage filter with memory, built-in event memory of 20000 events, pipe wise 4 stage flow monitoring, LED indications for alarm and fault conditions . Detector shall have an IP66 rated enclosure and shall be suitable for Harsh environment applications, also detector shall support installation of additional displays & relay cards at remote location over 2 core wire for remote monitoring / alarm. It Should be of Same Make of FAS. Proposed aspiration detector shall be UL, FM, EN, LPCB & VDS approved.
2 | MR | Power Supply Unit for above Detector | Nos. |  | 3
Supply, Installation, Testing and commissioning of Power Supply Unit for above Detector 220VAC to 24VDC 2 Amp Power Supply,FM approved with 24 hour battery back up
3 | MR | Caplliary Tube - For below False ceiling Area | Nos. |  | 11
Supply, Installation, Testing and commissioning of Caplliary Tube as per required. (For below False ceiling Area )
4 | MR | End cap or Nozle Termination | Nos. |  | 7
Supply, Installation, Testing and commissioning of End cap or Nozle Termination as per required.
5 | MR | CPVC PIPE 21 mm internal dia | Nos. |  | 150
Supply, Installation, Testing and commissioning of CPVC PIPE 21 mm internal dia complete in all respect as required.
6 | MR | Dual tone hooters with 93 db | Nos. |  | 3
Supply, installation, testing and commissioning of Dual tone hooters with 93 db complete as required.
Note: Project Specific MAF (Manufacturer's Authorization Form) Certificate required from OEM to ensure the System Integrator is authorized & that the OEM will support the System Integrator before execution & during execution of the project.
TOTAL CARRIED OVER TO SUMMARY
SUB HEAD L |  | ACCESS CONTROL SYSTEM
Design, Supply, installation, testing & commissioning of following Access Control System:
1 |  | Access Control Software
1.1 | DSR-2025- 41.5 | Software for Web based Access Control System Supplying, Installation, Testing and Commissioning of Web based Access Control Enrolment and Device Configuration Software, Should be independent of OS (Windows), Unified Management of Biometric, Card, and Controllers, Import Functionality for bulk user details, Biometric Template Retrieval for Data Recovery, User Management, Logs and Terminal Management, Support for IP-based and USB Biometric Devices, User-specific Access Policies, Different User Policies on the Same Terminal, Assignment of Specific Access Schedules, Pushing Users to Terminals or Groups, Admin Authority Management to define rights of each user to perform, Blacklist User Management, Access Schedule Creation, Real-Time Log Retrieval, Real- Time User Identification, Secure Storage of Biometric/Users Data,Capable to integrate with 3rd party applications over Web API's, MQTT protocol support. | Each |  | 1
2 | MR | VMS
|  | Visitor Management Software (including all necessary HW and sofware(cloud hosting etc for atleast 1 year) | Nos. |  | 1
3 |  | Access Control System with Face recognition
3.1 | DSR-2025- 41.1 | Supplying, Installation, Testing and Commissioning of Access Control System comprising of Face and fingerprint Recognition, Smart Card, QR Code, NFC & PIN Code based Reader, following sizes of 5” IPS TFT Touch Screens, 1GB RAM, 8 GB ROM, Live Face Detection with anti- spoofing against 2D photograph, mobile selfie & video, Fake Fingerprint and face Detection Technology, 30,000 Face storage (1:N) /, 3,000 fingerprint (1:N), QR code 30,000, 30,000 card storage (1:N), 2 lakh transaction storage, 20,000 image logs, onboard dual camera (colour & IR) Primary camera min 2MP, Support Face authentication & verification from up to 1 meters, Communication protocols WiFi, TCP/IP, Wiegand Out, Wiegand IN, USB, MQTT protocol, Blacklist Employee Management, User wise authentication modes; Built in Lock Control, Mask Detection & Alert (configurable), 40 to 30,000 lux illumination, IP65 for Ingress Protection, Certification: CE, FCC, BIS, ROHS, etc. Metal Enclosure with battery backup, suitable for mounting on metal surface/metal frames/ wooden frames/wall/flap barriers including all mounting bracket & accessories complete etc. as required
| DSR-2025- 41.1.1 | 5" IPS TFT Touch Screen | Each |  | 28
4 | MR | Multi Lane Flap Barrier
|  | Supply Installation Testing Commissioning of 8 Lane (7 Normal + 1 Wide Lane) retractable Flap Barrier, Supply Installation Testing Commissioning of 8 Lane (7 Normal + 1 Wide Lane) retractable Flap Barrier Electrical shape design, SS304 Material, 1.5 mm thickness, BLDC Motor with direct drive mechanism for minimum 10 Mil MCBF , L: 1400 mm, W: 300 mm, H: 1000 mm, Bi-Directional, Pass Width 550-600 mm for Normal lane and 900mm for Wide Lane using telescopic flap, 20 Pairs of IR Sensors with separate logic control and main PCB Board to be integrate with any 3rd Party Access Control System. Certified: CE, ISO 13849-1:2023, EN60204- 1:2006/A1:2010, EN 61000‒6‒2:2005, EN 61000-6-4:2007/ A1:2011, EN ISO 12100:2010, ISO 9001 : 2015, ISO 45001 : 2018, ISO 14001 : 2015 complete as per tender specifications. Dimensions shall be as required at site. Vendor to visit site before quoting the same. | Nos. |  | 2
5 | MR | Dual Lane Flap Barrier
|  | Supply Installation Testing Commissioning of 2 Lane Flap Barrier, SS304 Material, 1.5 mm thickness, BLDC Motor for 8 Mil Cycles, Bi-Directional, Pass Width 600 mm LED Lights on Flaps, 5-6 Pairs of IR Sensors with separate logic control and main PCB Board to be integrate with any 3rd Party Access Control System. Certified: CE, ISO 13849-1:2023, EN60204-1:2006/A1:2010, EN 61000‒6‒2:2005, EN 61000-6-4:2007/ A1:2011, EN ISO 12100:2010, ISO 9001 : 2015, ISO 45001 : 2018, ISO 14001 : 2015 complete as per tender specifications. Dimensions shall be as required at site. Vendor to visit site before quoting the same. | Nos. |  | 6
6 | MR | Smart card Reader
|  | Supply of card readers with Typical Read Range miCLASS Seos: upto 5 cm iCLASS: upto 9 cm MIFARE Classic: upto 5 cm MIFARE DESFire EV1/EV2: upto 5 cm, Ideally suited for mullionmounted door installations or any flat surface, • Intelligent Power Management (IPM) – Reduces reader power consumption. Certifications CE (EU) , Cryto Processor Hardware Common Criteria Rating EAL5+ | Nos. |  | 91
7 | MR | Master Controller
|  | Supply, Installation, Testing, Commissioning of 2 reader inputs with 4 inputs and 3 controllable relays. These readers can be used for relaxed and full anti-pass (APB) access on a single door, or single entry on two doors. All inputs are also secure with end of line sensing (EOL). Legacy Wiegand readers are also supported.Support for the RF transmitter and receivers has been maintained. The two independent 10A single-pole, double throw (SPDT) relays allow for interfacing to door strikes, magnetic locks, and other 3rd party device such as alarm panels or lighting. An Auxiliary 3rd relay has been added for additional control and is currently reserved for future use on Access Portal software.operating temperature -25° to +60°C or -13° to +140°F. | Nos. |  | 2
8 | MR | Slave Controller
|  | Supply, Installation, Testing & Commissioing of Controller having 2 reader inputs with 4 inputs and 3 controllable relays. These readers can be used for relaxed and full anti-pass (APB) access on a single door, or single entry on two doors. All inputs are also secure with end of line sensing (EOL). Legacy Wiegand readers are also supported.Support for the RF transmitter and receivers has been maintained. The two independent 10A single-pole, double throw (SPDT) relays allow for interfacing to door strikes, magnetic locks, and other 3rd party device such as alarm panels or lighting. An Auxiliary 3rd relay has been added for additional control and is currently reserved for future use on Access Portal software.operating temperature -25° to +60°C or -13° to +140°F | Nos. |  | 47
9 | MR | EM lock
|  | Holding Force: Minimum 600 lbs (280 kg) Voltage: 12V DC / 24V DC (selectable), UL Listed with magnatic contact & Door position sensor Current Draw: ≤ 500 mA at 12V DC, ≤ 250 mA at 24V DC | Nos. |  | 23
10 | DSR-2025- 41.6 | Electromagnetic locks
Supplying, Installation, Testing and Commissioning of Electromagnetic locks (fail safe type) for following type of Doors suitable for operation on 12 V DC having holding force 600 lbs for Single Leaf Door and 1200lbs for Double leaf door with suitable feedback i/c connection complete etc. as required.
10.1 | DSR-2025- 41.6.2 | Double leaf door (Each leaf 600lbs & Total 1200 lbs) | Each |  | 68
11 | DSR-2025- 41.7 | Exit Push Button Supplying, Installation, Testing and Commissioning of Heavy Duty SS Finish Exit Push Button for releasing access doors with all necessary installation accessories i/c connection complete etc. as required | Nos. |  | 91
12 | MR | Power Supply
|  | 12 V 5 AMP Power Supply | Nos. |  | 43
13 | MR | Network Switch
|  | 8 Port POE Network Switch with 2 NOS Giga Port | Nos. |  | 13
14 | MR | Access Control Cards
|  | HID Smart Card | Nos. |  | 1010
16 | DSR-2025- 39.23 | Supplying and fixing of following size Wall Mount Rack having Fixed Structure with 0.8mm CRCA Sheet, completely knocked-down condition (CKD) Shape, Vertical Mounting Rail 1.6 mm with 'U'Marking, Minimum 2 cable entry/exit provision at Top and bottom with rubber protection, Front 5mm Toughened Glass with lock, wall mounting kit, Powder coated Color- RAL- 7035, complied with UL & RoHS, 2 x 6 sockets 16A power distribution units, 3 numbers closed cable organizer, Hardware mounting screws packet of 20 x 1 number, etc. complete as required
| DSR-2025- 39.23.2 | 9U Rack | Nos. |  | 13
17 |  | RJ45 Connectors
| DSR-2025- 39.16 | Supplying, Installation, Testing and commissioning of RJ45 Connector for CAT 6A Cables. RJ45 modular plug supports 4 twisted pairs, 8 positions, 8 connectors. Housing: PC, UL94V-2, transparent color, Use for 24- 26 AWG stranded wires etc. complete as required. | Nos. |  | 188
Magnetic door Sensor
18 | DSR-2025- 41.8 | Supplying, Installation Insta, Testing and Commissioning of Door Position Sensor i/e connection complete etc. as required | Nos. |  | 159
19 | MR | Server for Access control System
|  | Processor: Intel Xeon Silver/Gold (8-core+, 2.4 GHz+) RAM: 32 GB DDR4 ECC (expandable to 64 GB) Storage: 1 × 512 GB NVMe SSD (OS + BioStar application) 2 × 2 TB HDD (Database & logs – RAID 1 or RAID 5) OS: Windows Server 2022 Standard Database: MS SQL Standard / Enterprise Network: Dual 1 Gbps NICs or 10 Gbps (for large systems) Other: Redundant PSU Hardware RAID controller With 32" Display | Nos. |  | 1
20 | MR | Client Workstation for Visitor Management
|  | Processor: Intel® Core™ i7 13th Gen Operating System: Windows 11 Pro 64-bit (licensed) RAM: 16 GB DDR4 (expandable to 32 GB) Storage: 512 GB NVMe SSD (primary) + 6 TB HDD (secondary) Graphics: 2 GB Graphic Card Monitor: 23.8” LED, Full HD (1920×1080) | Nos. |  | 1
20 | MR | Tablet with stand for Registration of visitors | Nos. |  | 1
26 | MR | Integration of Access Control with Visitor Management Software | Nos. |  | 1
24 | DSR-2025- 42.4 | LED Display Supplying, Installation, Testing and Commissioning of following size LED display (LED monitor) industrial grade with 3840x2160 resolution or better, USB playback, bluetooth and miracast connectivity, 4X HDMI 2.0, DP 1.2, HDR 10/10+, brightness: 500-nits or better, Video wall mode should be available, contrast ratio: 1200:1, OPS slot, viewing angle (H/V): 170°/ 170°, response time less than 12ms, Display control shall be on monitor screen and programmable with remote (remote shall be supplied with system), Key Board, Optical Mouse, etc. as required.
24.1 | DSR-2025- 42.4.2 | 42 inch or larger | Nos. |  | 2
15 | DSR-2025- 39.18 | Supplying, drawing, Testing and commissioning of Cat6A UTP 4 pair, 23 AWG solid copper cable in existing conduit/ on surface, U/FTP, LSZH, Non- Plenum, Horizontal (solid) Cable suitable for high speed data networking application supporting upto 10Gbps over a 100 meter channel. The 4 Unshielded Twisted Pairs (UTP) cable with color coded insulation for easy indentification should have FLAME PROPERTIES i.e. Flammability Test - IEC 60332-1, Smoke Density - IEC 61034, LSZH standards compliance: ANSI/TIA-568 C.2, ISO/IEC 11801, IEEE 802.3an, RoHS. Delay Skew should be < 45NS. The outer Cable Diameter should be 7.5 + 2 mm. Cable should have been tested and verified by UL/ ETL etc. complete as required
15.1 | DSR-2025- 39.18.1 | 1 RUM of Cable | Meter |  | 650
21 |  | Fiber Optic Cable
| DSR-2025- 39.19 | Supplying and drawing following core Fiber Optic Cable having corrugated steel armoring. The Fiber should be SM Fiber Central -loose tube filled with Thixotropic jelly, duly following Standards: ISO 11801, IEC 60793-1/60794-1-2, ITU-T-REC G.652D and Telecordia GR-20-core, High quality Electro Chromium Coated Corrugated Steel tape (ECCS ) and HDPE- Sheath, Operating ambient Temperature should be – 5 0C to +50 0C and Storage Temperature shall be – 5 0C to +50 0C, Max Attenuation ± 0.36 (db / km) at Operational Wavelength 1310 nm and ± 0.22 db / km at Operational Wavelength 1550 nm. type of fiber should be 9/125 / G.652D & Refractive Index should be 1.4670/1.4675. The value for Mode-filed, Cladding Diameter 9.2 ± 0.4 μm and 125 ± 0.7 μm correspondingly. The Dispersion value < 3.5 < 18 ps/nm-km and PMD value < 0.2 ps/km and Cable Cutoff wavelength < 1260 nm i/c splicing & marking etc. complete as required
21.1 | DSR-2025- 39.19.1 | Single Mode 6 Core Optical fiber cable | Meter |  | 800
22 | DSR-2025- 1.17 | Supplying and drawing following sizes of FRLS/HFFR PVC insulated copper conductor, single core cable in the existing surface/ recessed steel/ PVC conduit as required.
22.1 | DSR-2025- 1.17.3 | 3C x 1.5 sq. mm | Meter |  | 1200
23 | DSR-2025- 15.15 | Supplying and laying of following size DWC HDPE pipe ISI marked along with all accessories like socket, bend, couplers etc. conforming to IS 14930, Part II complete with fitting and cutting, jointing etc. in the existing trench, complete as required.
23.1 | DSR-2025- 15.15.1 | 63 mm dia (OD-63 mm & ID-51 mm nominal) | Meter |  | 100
25 | DSR-2025- 1.2 | Supplying and fixing of following sizes of steel conduit along with accessories in surface/recess including painting in case of surface conduit, or cutting the wall and making good the same in case of recessed conduit as required.
25.1 | DSR-2025- 1.20.2 | 25mm | Meter |  | 9375
27 |  | Control Cables
27.1 | MR | Supplying, drawing, Installation, Testing and commissioning of 8 Core 1 sq. mm cable | Meter |  | 6050
27.2 | MR | Supplying, drawing, Installation, Testing and commissioning of 4 Core 1 sq. Mm cable | Meter |  | 6050
27.3 | MR | Supplying, drawing, Installation, Testing and commissioning of 2 Core 1 sq. mm cable | Meter |  | 6050
Note: Project Specific MAF (Manufacturer's Authorization Form) Certificate required from OEM to ensure the System Integrator is authorized & that the OEM will support the System Integrator before execution & during execution of the project.
TOTAL CARRIED OVER TO SUMMARY
SUB HEAD M |  | CCTV SYSTEM
Design, Supply, installation, testing & commissioning of following CCTV System (STQC and BIS certified):
2 MP IP IR Dome Camera
1 | DSR-2025- 40.1 | Supplying Installation Testing and Commissioning of 2 MP IP IR Dome Camera having following specifications, type of lens and features etc :- 1) Signal System: PAL/NTSC, Signal to Noise Ratio: >50 dB, Camera should display Camera title, Date & Time in live & recorded video 2)Image Sensor: 1/2.8" or better progressive Scan CMOS to get color image even at night condition(Minimum Illumination: 0.006 Lux@ F1.4, AGC ON, 0 lux with IR or better) True Day & Night High Performance Mechanical IR cut filter with auto switch, Integrated IR Source (Auto, Manual)- Inbuilt IR LED's with effective distance upto 50 meter or better and 30 meter for colour view in night, Imaging: 1/3s to 1/30000s electronic shutter support, Auto Gain Control , White Balance- Auto, Back Light Compensation, Multi zone Privacy Masking, HLC, Digital Watermarking. 3) Compression (Minimum):-Video:- H.265 or better, H.264H, H.264, Audio:- G.711U/A, G.711Mu, G.726, AAC, G.723 4) Wide Dynamic Range:- WDR (120db or more) 5) Digital Noise Reduction:- DNR (3D) On/Off 6) Video Streaming & Frame Rates :- Triple streaming , configurable (Main stream: 2MP (1920 ×1080)@25/30 fps,Sub streams minimum: 720P@25/30 fps). 7) Image Setting: Rotate Mode, saturation, brightness, contrast, sharpness adjustable through client software or web browser, Edge Analytics: Tripwire, Intrusion, Motion Detection 8) Cyber Security: AES 256-bit Encryption, Configuration encryption, trusted execution, Digest, security logs, account lockout, syslog, video encryption, IP/MAC filtering, HTTPS, trusted
1.1 | DSR-2025- 40.1.1 | 2MP (@ 25/30fps@1080P (1920×1080)) IP IR Dome Camera with 2.8/ 3.6mm fixed lens | Each |  | 375
2 MP IP IR Outdoor Bullet Camera
2 | DSR-2025- 40.2 | Supplying Installation Testing and Commissioning of 2MP Fixed Lens IP IR Outdoor Bullet Camera having following specifications and features etc :- 1) Signal System: PAL/NTSC, Signal to Noise Ratio: >50 dB,Camera should display Camera title, Date & Time in live & recorded video 2)Image Sensor: 1/2.8" or better progressive Scan CMOS to get color image even at night condition(Minimum Illumination: 0.006 Lux@ F1.4, AGC ON, 0 lux with IR or better) True Day & Night High Performance Mechanical IR cut filter with auto switch, Integrated IR Source (Auto, Manual)- Inbuilt Smart IR LED's with effective distance upto 50 meter or better and 30 meter for colour view in night, Imaging: 1/3s to 1/30000s electronic shutter support, Auto Gain Control , White Balance- Auto, Back Light Compensation, Multi zone Privacy Masking, HLC, Digital Watermarking. 3) Compression (Minimum):-Video:- H.265 or better, H.264H, H.264, Audio:- G.711U/A, G.711Mu, G.726, AAC, G.723 4) Wide Dynamic Range:- WDR (120db or more) 5) Digital Noise Reduction:- DNR (3D) On/Off 6) Video Streaming & Frame Rates :- Triple streaming , configurable(Main stream: 2MP (1920 × 1080)@25/30 fps Sub streams minimum: 720P@25/30 fps). 7) Image Setting: Rotate Mode, saturation, brightness, contrast, sharpness adjustable through client software or web browser, Edge Analytics: Tripwire, Intrusion, Motion Detection 8) Cyber Security: AES 256-bit Encryption, Configuration encryption, trusted execution, Digest, security logs, account lockout, syslog, video encryption, IP/MAC filtering, HTTPS, trusted upgrade, trusted boot.
2.1 | DSR-2025- 40.2.1 | 2MP @ 25/30fps@1080P (1920×1080) Outdoor Bullet Camera with 2.8/ 3.6mm fixed lens | Each |  | 18
3 |  | 24 Port POE Switch
|  | 24 Port POE Switch 24 × 10/100/1000 Mbps RJ45 (PoE / PoE+) All ports Gigabit, auto■negotiation, auto MDIX Uplink / SFP Ports 2 × RJ45 Gigabit uplinks + 2 × SFP (mini■GBIC) Vendor to confirm interface types PoE Support / Standard IEEE 802.3af / IEEE 802.3at (PoE+) Vendor to state exact standards supported Total PoE Power Budget 400 W Confirm actual usable budget Per Port Max PoE Output~30 W per port (PoE+) For high■power cameras, check if supported Switching / Backplane Capacity ≥ 56 Gbps non■blocking Vendor to confirm Forwarding Rate ~41.7 Mpps Vendor to confirm MAC Address Table Size≥ 16,000 entries Vendor to specify Jumbo Frame Support Up to 9,000 bytes Useful for video traffic VLAN / Layer 2 Features802.1Q VLANs, trunking, Q-in-Q, private VLAN Vendor to confirm Link Aggregation / Redundancy LACP (802.3ad), STP/RSTP/MSTP For link redundancy QoS / Traffic Prioritization8 queues, 802.1p, DSCP, rate limiting Ensure video traffic priority Multicast / IGMP FeaturesIGMP snooping, querier support Important for multicast cameras Security / Access ControlACLs, 802.1X, port security, DHCP snooping Vendor to confirm Management & MonitoringWeb GUI, CLI, SNMP v1/v2c/v3, syslog, RMON Firmware upgrade & backup supported Redundancy / Reliability Dual firmware, optional RPS For mission■critical deployment Power Supply Internal AC 100■240 V, 50/60 Hz Vendor to confirm input range Operating Temperature 0 to 40■°C (typical), humidity non■condensing Vendor to specify exact range Physical / Mechanical 1U rackmount, fans/ventilation, LED indicators Vendor to confirm Certifications & StandardsCE, FCC, RoHS, EMC, safety Vendor to confirm compliance Warranty & Support 3 years or more Vendor to clarify SLA Optional / Extra Modules SFP modules | Nos. |  | 27
24-Port L3 PoE Managed Switch
4 | DSR-2025- 39.3 | Supplying, installation, Testing and commissioning of following capacity 24 port Layer 2 indoor Network Switch having features and specifications etc. as mentioned here under: At least 24 X RJ-45 Gigabit Ethernet Ports and additional 2 X 10G Base -T with 4 X SFP Ports with non- blocking architecture by having Switching capacity of min. 168Gbps and packet forwarding rate of 125Mpps or higher, 16K MAC table. Console Port, USB port, Stacking support of min. 8 units per stack. Internal dual AC Power supply, STP, RSTP, MSTP, BPDU Filter, BPDU Restriction, Min. 9K Jumbo Frame, LBD, IGMP Snooping V1/V2/V3, MLD Snopping V1/V2. IGMP /MLD Groups 1K or more, IPv4/IPv6 Loopback Interface, 16 L3 IP Interface, Ipv6 ND, VRRPv3, UDP Helper, ECMP. VLAN: 802.1Ǫ, Port based, Ǫ-in-Ǫ, Multicast VLAN, Protocol VLAN, VLAN Trunking, DHCP Snopping, Server, server Screening. RADIUS , TACACS+ Authentication, ǪoS: 802.1P, 8 queues per port, ǪoS : WRR, Strict+WRR, WRED, 802.1p. ACL: MAC based, IPv4C IPv6, TCP/UDP Port number, time based ACL, TFTP Client, SNMP V1, v2c, v3, SNMP traps, RMON, DHCP server, relay, client, LLDP, LLDP-MED, OAM, Dying Gasp, 802.3ah, sflow, RIP, OSPF v2/v3, policy based route, SSL, SSH. 6 kV surge protection on all Gigabit Ethernet ports and on all GE RJ-45 access ports. Certifications: UL, CE, FCC, RoHS, MTCTE, OEM/Product must be on Trusted Telecom Portal of Department of Telecommunication, Government of India etc. complete as required.
4.1 | DSR-2025- 39.3.1 | 24 port PoE Layer 2 Network Switch with PoE Support of 370W or higher with each copper port supporting 802.3at PoE+ min. | Each |  | 1
5 | MR | 24 Port Patch Panel | Nos. |  | 28
6 | DSR-2025- 42.4 | LED Display Supplying, Installation, Testing and Commissioning of following size LED display (LED monitor) industrial grade with 3840x2160 resolution or better, USB playback, bluetooth and miracast connectivity, 4X HDMI 2.0, DP 1.2, HDR 10/10+, brightness: 500-nits or better, Video wall mode should be available, contrast ratio: 1200:1, OPS slot, viewing angle (H/V): 170°/ 170°, response time less than 12ms, Display control shall be on monitor screen and programmable with remote (remote shall be supplied with system), Key Board, Optical Mouse, etc. as required.
6.1 | DSR-2025- 42.4.3 | 55 inch or larger | Each |  | 7
7 |  | 64 Channel NVR (STQC and BIS certified):
|  | SITC of 64 channels Network Video Recorder with 80 TB HD. Should support 8 SATA hard disk slot and each should support 10TB HDD. This shall be support RAID 0, 1, 5, 6, 10. Image and Video specification, H.265, H.264 compression. Video Input – 32 IP camera minimum. Video Resolution support Up to 8 MP (4K) IP CameraF. Adjustable Image Quality. VBR and CBR support. Each channel should support multi-level motion detection. Matrix Display: 1/4/9/16/32/64. Physical Ports. Video Output: HDMI 1 (4K Max), HDMI 2 (1080P), VGA x1 (1080P). Audio Interface: 1ch In & 1ch Out. Serial Interfaces: 1# RS232, 2# RS485. Network: 2 RJ45, 10M/100M/1000M LAN port. Alarm Interface: 16ch In & 6ch Out. USB Port: Front x 2, USB 2.0, Back x 1, USB 3.0 ports. Recording and playback. Should support schedule, motion and alarm-based recording. Incoming /Outgoing Bandwidth should be 400 Mbps. Synchronous Playback. Time/Date based search mode. Alarm based search. VCA detection alarm should be supported. Should Supports data transfer via USB, e-SATA & Network for easy and fast backup of data. Support megapixel HD network video preview, storage and playback. Digital Zoom support on any user specified area in live screen. Should support digital zoom in both Live and Playback. Should support Playback and backup based on event search. Should support Crome / Edge / Safari or later. Multiple Language GUI. Compatable for smart phone. Humidity: 10% to 90% (non-condensing) Certifications - UL, CE, FCC, BIS. | Nos. |  | 7
| DSR-2025- 40.12 | Supplying, Installation, Testing and Commissioning following capacity Serveillance grade Hard Disk with upto 256MB/s Transfer Rate, 256 MB Cache, 7200 RPM Disk Speed, 3.5 inch form factor, SATA Interface, BSMI, ICES-003/NNB-003, CE, FCC, KC, Maghreb, RCM, UKCA, VCCI, CB- Scheme, TUV, UL Certifications.
8 | DSR-2025- 40.12.4 | 10TB (Terabytes) | Each |  | 56
10 |  | Rack Type□Wall-mounted / 19” standard
| DSR-2025- 39.26 | Supplying and fixing Outdoor Pole/ Wall mount 6U Rack, IP55, Front Door with Filter, Louver & Unique key Lock. 3 Socket PDU 5Amp - 1 No. Self adhesive thermal foam from inside. Hood For Air Inlet at front side.1U Cantilever Tray 250mmDepth, Gasket. etc complete as required | Each |  | 27
11 |  | 42U Rack-19” standard
| DSR-2025- 39.25 | Supplying and fixing 42U Rack with 6 inch Castor wheels and front brake Floor Standing Rack with Main Frame Pillar of 1.6mm CRCA Sheet with removable side panels, L- Shape adjustable Vertical Mounting Rail of 2mm with 'U'Marking completely knocked-down condition (CKD) Shape, fitted with 4 number cooling fans, minimum 8nos two line cable entry/exit provision at top and bottom with rubber protection, Front door 5mm Toughened Glass with MS frame or MS perforated with lock, Rear MS vented or perforated door, Powder coated Color- RAL- 7035 or black, complied with UL & RoHS, 2 x 6 sockets 16A power distribution units, 3 numbers closed cable organizer, Hardware mounting screws packet of 20 x 1 number, etc. complete as required. | Each |  | 1
12 | DSR-2025- 39.19 | Supplying and drawing following core Fiber Optic Cable having corrugated steel armoring. The Fiber should be SM Fiber Central -loose tube filled with Thixotropic jelly, duly following Standards: ISO 11801, IEC 60793-1/60794-1-2, ITU-T-REC G.652D and Telecordia GR-20-core, High quality Electro Chromium Coated Corrugated Steel tape (ECCS ) and HDPE- Sheath, Operating ambient Temperature should be – 5 0C to +50 0C and Storage Temperature shall be – 5 0C to +50 0C, Max Attenuation ± 0.36 (db / km) at Operational Wavelength 1310 nm and ± 0.22 db / km at Operational Wavelength 1550 nm. type of fiber should be 9/125 / G.652D & Refractive Index should be 1.4670/1.4675. The value for Mode-filed, Cladding Diameter 9.2 ± 0.4 μm and 125 ± 0.7 μm correspondingly. The Dispersion value < 3.5 < 18 ps/nm-km and PMD value < 0.2 ps/km and Cable Cutoff wavelength < 1260 nm i/c splicing & marking etc complete as required.
12.1 | DSR-2025- 39.19.1 | Single Mode 6 Core Optical fiber cable | Meter |  | 1400
| DSR-2025- 39.21 | Supply and fixing following port Rack Mount loaded LIU with pigtail, Front-mounted cable saddles for jumper management, suitable to manage both splices and terminations, Pre- assembled shelves in multiple configurations, Rubber fiber slotted bracket built-in, metal splice shelf to protect the fibers, 2 fiber spools built-in for 900μm tight buffered fiber storing, Capable of storing up to 3 meters of 900μm tight buffered fiber per adapter, Removable front and rear covers for better access to interior of LIU, Should be Single / Multi mode LC Type fully loaded. Accessory kit consists of cable ties, mounting ear screws, and spiral wrap tube etc complete as required.
| DSR-2025- 39.21.1 | 6 Port LIU | Each |  | 14
| DSR-2025- 39.21.2 | 12 Port LIU | Each |  | 14
13 | DSR-2025- 39.18 | Supplying, drawing, Testing and commissioning of Cat6A UTP 4 pair, 23 AWG solid copper cable in existing conduit/ on surface, U/FTP, LSZH, Non- Plenum, Horizontal (solid) Cable suitable for high speed data networking application supporting upto 10Gbps over a 100 meter channel. The 4 Unshielded Twisted Pairs (UTP) cable with color coded insulation for easy indentification should have FLAME PROPERTIES i.e. Flammability Test - IEC 60332-1, Smoke Density - IEC 61034, LSZH standards compliance: ANSI/TIA-568 C.2, ISO/IEC 11801, IEEE 802.3an, RoHS. Delay Skew should be < 45NS. The outer Cable Diameter should be 7.5 + 2 mm. Cable should have been tested and verified by UL/ ETL etc. complete as required
13.1 | DSR-2025- 39.18.1 | 1 RUM of Cable | Meter |  | 26640
14 | MR | SFP Module for Connectivy of Netwrok switches
|  | SFP Module for Connectivy of Netwrok switches,Supply, installation, testing, and commissioning of SFP (Small Form-factor Pluggable) transceiver module suitable for Gigabit Ethernet network switch, supporting 1.25 Gbps data rate, with LC duplex connector, compatible with single-mode fiber, and providing transmission distance up to 10 km at 1310 nm wavelength, compliant with IEEE 802.3z and MSA standards, complete in all respects as required. | Nos. |  | 28
15 | DSR-2025- 39.16 | Supplying, Installation, Testing and commissioning of RJ45 Connector for CAT 6A Cables. RJ45 modular plug supports 4 twisted pairs, 8 positions, 8 connectors. Housing: PC, UL94V-2, transparent color, Use for 24- 26 AWG stranded wires etc. complete as required. | Nos. |  | 786
16 | DSR-2025- 1.17 | Supplying and drawing following sizes of FRLS/HFFR PVC insulated copper conductor, single core cable in the existing surface/ recessed steel/ PVC conduit as required.
16.1 | DSR-2025- 1.17.3 | 3C x 1.5 sq. mm | Meter |  | 1400
17 | DSR-2025- 39.13 | Supplying, Installation, Testing and commissioning of following CAT6A Patch Cord should have ETL/UL verification program certificate for compliance with ANSI/TIA-568.2-D etc. complete as required
| DSR-2025- 39.13.1 | Copper Patch Cords of length 1m (3ft) | Each |  | 28
18 | DSR-2025- 1.2 | Supplying and fixing of following sizes of steel conduit along with accessories in surface/recess including painting in case of surface conduit, or cutting the wall and making good the same in case of recessed conduit as required.
18.1 | DSR-2025- 1.20.2 | 25mm | Nos. |  | 8315
19 | MR | Heavy Duty PVC Box for Cameras | Nos |  | 442
20 | DSR-2025- 42.2 | PC System Supplying Installation Testing Commissioning of Client PC System comprising of PC Hardware with minimum11th Gen Intel® I7 processor CPU E5-2640x64 (or better), compatible with dual and quad core processors minimum 3.1 Ghz and 8GB or higher RAM, Hard Drive Space of 256 GB SSD or better, Video card and monitor capable of 1920 x 1080 pixel resolution or better with Ethernet adapter (10/100/1000 Mbps with RJ-45 connector) with 2 GB or higher Graphics card suitable complete etc. as required. | Nos. |  | 1
Note: Project Specific MAF (Manufacturer's Authorization Form) Certificate required from OEM to ensure the System Integrator is authorized & that the OEM will support the System Integrator before execution & during execution of the project.
TOTAL CARRIED OVER TO SUMMARY
SUB HEAD N |  | ADDRESSABLE WATER LEAK DETECTION SYSTEM
Design, Supply, installation, testing & commissioning of following Water Leak Detection System: for Server Room, UPS Room, Battery Room, HUB Rooms (1 No. per floor), Electrical rooms (2 Nos. per floor)
1 | MR | Addressable Main Water Leak Detection Panel with 10.1inch Touch Screen display
|  | Addressable Main Water Leak Detection Panel with 10.1inch Touch Screen display networkable on RS 485 with Water Leak Detection Modules. It will give point of leak distance in Meters and cable fault conditions of each networked modules. It shall have event log with date and time.It shall also have Modbus/Bacnet output for BMS monitoring with 230 VAC input. Main Panel to be enclosed in NEMA 4X enclosure. | Set |  | 2
2 | MR | 4 Wire Quick Dry Addressable Type Water Leak Sensing Cable
|  | 4 Wire Quick Dry Addressable Type Water Leak Sensing Cable.Water leak sensing cable shall be twisted, mechanically strong, resistant to corrosion and abrasion. The cable shall be constructed with two sensing wires, an alarm signaling wire and a continuity wire.The Sensing Cable shall have over braided Synthetic Robe Jacket to avoid false alarms in case of metal touching the sensing cable.The Sensing cable should be made from flouro polymer with minimum diameter of 6.5mm. | Mtrs. |  | 640
3 | MR | Sensor Interface Module ( SIM ), with LCD display
|  | Sensor Interface Module ( SIM ), with LCD display showing point of leak in meters and cable fault condition. It shall have capability to extend one sounder output and connect upto 150 mts of sensing Cable with 32 such Modules connectivity to the Main Panel. It shall have fail safe loop back system wherein if there is a cable break.the sensing cable which is still in connection with interface module. shall continue to detect leak ( if any ) . This fail safe loop back . system ( Class A wiring ) shall be incorporated as necessity to enhance. the system capability and redundancy. SIM Module to be enclosed in NEMA 4X enclosure. | Nos. |  | 32
4 | MR | Leader cable 3mtrs. | Nos. |  | 32
5 | MR | Cable Securing Clip with Tie Fixing Base (recommended to secure cable very 3-4 ft) (Qty.50 in 1 pack) | Nos. |  | 32
6 | MR | High-visibility Yellow Tags to identify sensing cable and record mapped distance- bag of 50 | Sets |  | 4
7 | MR | Belden Jumper cable for connecting two digital sensing cables or between control panel & sensing cable | Sets |  | 4
8 | MR | End Termination Plugs for terminating each circuit of sensing cable | Sets |  | 32
9 | MR | Hooter with strobe | Sets |  | 32
Note: Project Specific MAF (Manufacturer's Authorization Form) Certificate required from OEM to ensure the System Integrator is authorized & that the OEM will support the System Integrator before execution & during execution of the project.
TOTAL CARRIED OVER TO SUMMARY
SUB HEAD O |  | ADDRESSABLE DIGITAL RODENT REPELLENT SYSTEM
DESIGN, SUPPLY, INSTALLATION,TESTING & COMMISSIONING OF ADDRESSABLE DIGITAL RODENT REPELLENT SYSTEM
for Office floors, All Shafts, Technical rooms i.e. UPS, Battery, Server & Hub Rooms
1 | MR | SITC of Microprocessor based Master Controller with 128X64 Graphic LCD DISPLAY capable of operating in 5 ultrasonic frequency band spectrums. The LCD should display oscillation between these freqency bands in a graphical format. The controller should also support upto 20 transducers @ minimum 500 sq.ft each and networkable on RS 485 having facility to support Hardwired Third Party BMS integration via Modbus & potential free NO-NC contacts.And, also Ultrasound output verification with the help of software capable of documenting the same via a pdf report. | Nos. |  | 15
2 | MR | Each transducer should cover an area upto 500 sq.ft in all voids. No Looping permitted. | Nos. |  | 212
3 | MR | Supply, installation, Testing, Commissioning & Verification Kit comprising of Ultrasound Wave Analyzer (Software and Hardware) that can do the following: a. Capture,Record and Report (in pdf format) One Third Octave Ultrasound Band Frequencies emitted from the transducers thereby ensuring HUMAN SAFETY as per IRPA (International Radiation Protection Association, Geneva) Guidelines. b. Capture,Record and Report (in pdf format) ultrasound output from each transducer depicting individual frequency peaks along with corresponding sound pressure levels, current operating band and the Controller Name for verifying the product. | Nos. |  | 1
4 | MR | SITC of GUI Software capable of supporting: • Real Time Graphical Representation of the ultrasonic frequency band spectrum depicting the frequency oscillations within the current band. • Facility to generate a consolidated pdf summary report of all controllers or detailed pdf report of individual controller in real time or in a pre defined schedule. • Parameter Configuration of the controller. • PCB view of each controller. | Nos. |  | 1
5 | MR | 2C x 14/40 SWG Copper Cable of 0.5 sq.mm-275 Mtrs Roll (will be billed as per actual) | Nos. |  | 30
6 | MR | Powder Coated MS Bracket | Nos. |  | 165
7 | 1.2 | Supplying and fixing of following sizes of steel conduit along with accessories in surface/recess including painting in case of surface conduit, or cutting the wall and making good the same in case of recessed conduit as required.
| 1.20.2 | 25mm | RM |  | 430
8 | MR | Supplying and drawing following sizes of FRLS/HFFR PVC insulated copper conductor, single core cable in the existing surface/ recessed steel/ PVC conduit as required.
8.1 | MR | 3C x 1.5 sq. mm | Meter |  | 2810
Note: Project Specific MAF (Manufacturer's Authorization Form) Certificate required from OEM to ensure the System Integrator is authorized & that the OEM will support the System Integrator before execution & during execution of the project.
TOTAL CARRIED OVER TO SUMMARY
SUB HEAD P |  | EMERGENCY LIGHTING SYSTEMS - WITH CENTRAL BATTERY SYSTEM
Design, Supply, installation, testing & commissioning of following Energency Lighting System with Central Battery System:
1 | MR | EMERGENCY LUMINAIRES
1.1 | MR | Fully recessed LED luminaire - suitable for Offices/ Corridor addressable emergency luminaires as per specification: • Recessed Mounted luminaire with metal body • Lux level below light should be 45 lux and 15 lux average along evacuation path @ 3 meter mounting height • Ingress protection IP20 • Supply Voltage 220-240 V, 50/60 Hz AC, DC • Fully compliant with requirements of the fire and safety code of practice & the respective EN 60598-2-22 and the system designed in compliance with EN50171, EN50272-2, EN50172, and EN1838 standards • With Backup for 90 Minutes operation via Central Battery System. | Nos. |  | 770
1.2 | MR | Surface Mount LED luminaire - suitable for AHU Rooms/ Electrical Rooms luminaires as per specification: • Wall / Ceiling and Surface mount - 20 W Batten Light • Ingress protection IP65 • Polycarbonate body and diffuser • Supply Voltage 220V/ 240V AC/DC • Fully compliant with requirements of the fire and safety code of practice & the respective NBC 2016 standards • With Backup for 90 Minutes operation via Central Battery System | Nos. |  | 111
1.3 | MR | ADDRESS MODULE for converting THIRD PARTY LIGHT FITTING to EMERGENCY LIGHT of upto 60VA for Small Rooms / Cabins: * The address modules should comply to EN 61347-2-11:2001 in conjunction with EN 61347- 1:2001. * The luminaries must be fitted with electronic ballast/ drivers with the following features: * It must be able to operate with both AC and DC voltage. * It must shut itself off in an event of a lamp failure, input current in shut off mode must be less than 10mA * It must have Constant power output high frequency electronic control gear/ transformer. * The electronic ballast/ driver should be ‘CE’ marked and should comply to EN 60925. | Nos. |  | 552
1.4 | MR | ADDRESS MODULE for converting THIRD PARTY LIGHT FITTING to EMERGENCY LIGHT of upto 60VA for Toilet areas: * The address modules should comply to EN 61347-2-11:2001 in conjunction with EN 61347- 1:2001. * The luminaries must be fitted with electronic ballast/ drivers with the following features: * It must be able to operate with both AC and DC voltage. * It must shut itself off in an event of a lamp failure, input current in shut off mode must be less than 10mA * It must have Constant power output high frequency electronic control gear/ transformer. * The electronic ballast/ driver should be ‘CE’ marked and should comply to EN 60925. | Nos. |  | 80
2 |  | EXIT LUMINAIRES
2.1 | MR | SINGLE SIDED/ DOUBLE SIDED WALL/SURFACE mounting EXIT Luminaire, High power LED 230VAC/DC Addressable luminaire: • Viewing distance up to 25m • Ingress protection IP43 • Supply Voltage 220V/ 240V AC/DC • Fully compliant with requirements of the fire and safety code of practice & the respective EN 60598-2-22 and the system designed in compliance with EN50171, EN50272-2, EN50172, and EN1838 standards • With Backup for 90 Minutes operation via Central Battery System | Nos. |  | 229
2.2 | MR | EXIT LUMINAIRES - SINGLE SIDED WALL/ CEILING MOUNT addressable Adaptive EXIT Luminaire, LED luminaire: • Viewing distance up to 25m • Ingress protection IP43 • The adaptive emergency exit light adapts, to warn about dangerous escape routes. Under normal conditions, the exit light works like any normal exit light but in case the path is dangerous it should illuminate a red cross across the signage. • Supply Voltage 220-240 V, 50/60 Hz AC, DC • Fully compliant with requirements of the fire and safety code of practice & the respective EN 60598-2-22 and the system designed in compliance with EN50171, EN50272-2, EN50172, and EN1838 standards • With Backup for 90 Minutes operation via Central Battery System. | Nos. |  | 92
2.3 | MR | Route Controller for Adaptive Exit Lights Route Controller control unit, TST6901, for TWT8051WKX adaptive emergency exit lights. To integrate with Fire Alarm system-TST6901 | Nos. |  | 4
3 | MR | CENTRAL BATTERY SYSTEM PANEL
Emergency System Panel with own LED indicator for each luminaire in the same circuit providing simultaneous status information of the luminaires by a single view with corresponding group (circuit) number indicating on the segment display. -Liquid Crystal Display (LCD) for the simultaneous display of the system status, faults and Luminaire status. The control module must have following features: -Monitor and control all test cycles and functions. -Indicate every status of the system and the connected luminaire -Communicate with the addressable electronic ballast on every slave luminaire -With volt free contacts for internal fault, battery mode operation & external fault. - The emergency supply panel shall supervise the battery status such as Battery Over voltage / Battery Under voltage. Charging failure shall be indicated as an Internal fault by an indicator
|  | - The emergency supply panel should be capable of continuously monitoring the circuits by means of current measurement thus making the system a continuously fully addressable system. - The unit shall be fitted with a deep discharge protection circuit, which has two operation phases: When in battery mode the battery voltage decreases to 195V, a preliminary deep discharge alarm shall be given. When the battery voltage decreases to 175V, the load shall be disconnected. The circuit shall allow the battery to increase its voltage without switching the load ON again, thus avoiding detrimental full discharge. The panel shall automatically return to normal operation, once the mains supply recovers. Fully compliant with requirements of designed and installed to meet the fire and safety code of practice & the respective EN 60598-2-22 and the system designed in compliance with EN50171, EN50272-2, EN50172, and EN1838 standards EN Standards | Sets |  | 3
4 | MR | BATTERIES - The batteries shall be maintenance free VRLA sealed lead acid gas recombination type with a minimum design life of 10 years at prevailing ambient temperature. - They shall have extremely low gas generation, low self-discharge and have permanently sealed pressure release vents. - The batteries shall be sized to power complete system for 90 minutes following mains failure at 100% light output of all emergency lamps. | Sets |  | 3
5 | MR | Intelligent Control Module The non-maintained luminaires at sub distribution panel area shall be lit during a local supply failure. However the emergency supply panel shall not switch to battery use as long as its own mains supply is available. All necessary data transfer shall take place through the standard power supply cabling of the luminaires Continuous monitoring of the lighting sub distribution panels shall be made by Local Controller units, each having 3-phase monitoring input. Each circuit shall have its own Local Controller so that a possible failure of a single controller does not affect the other circuits.The same functionality can be met by using intelligent controllers by routing 8 sub circuit monitoring contacts to one IC or 8 switching contacts per IC IC shall be on a dedicated RS485 bus topology and it should be possible to connect a total of 32 IC’s per bus The Local Controllers should comply to EN 61347-2-11:2001 in conjunction with EN 61347- 1:2001. | Sets |  | 9
6 | MR | BACNET/IP and MODBUS/IP Interface with inbuilt web server The Gateway shall have the following specifications: • Shall be capable of integrating CBS Panel (Should be capable of integrating 7 Nos networked panels) • Inbuilt Web Server with 10 simultaneous user logins • Monitor each CBS Panel parameters, emergency and exit light in the BMS • Capable of scheduling the on/ off function of the emergency light and also provide switch control to all emergency light via connectivity to the Intelligent Controller • Integrates with 3rd party BMS over BACNET/IP or MODBUS/IP • Processor Speed: 1GHz • Memory: 1GB DDR3 SDRAM to store logs in case of communication failure between gateway and BMS • 2 Nos. of 10/100MB Ethernet ports • 24VAC/DC power supply • BTL Listed • No dedicated PC should be needed. Failure of PC should not cause the integration with BMS to fail or disconnect. | Set |  | 1
7 | MR | Supply, laying and termination along with Halogen free glands of 3C x 1.5 sq.mm Fire Survival Armoured cable with Class-2 Copper conductor with glass mica tape, as per BS 7846, Fire Test as per BS 6387 CWZ, BSEN 8434-2, LPCB / TUV / BRE Global Certified. Fire Survival cable shall be suitable 950°C rating for three hours for fire alarm system. | Meters |  | 25600
Note: Project Specific MAF (Manufacturer's Authorization Form) Certificate required from OEM to ensure the System Integrator is authorized & that the OEM will support the System Integrator before execution & during execution of the project.
TOTAL CARRIED OVER TO SUMMARY
HIGH SIDE - ELECTRICAL WORKS
SUB HEAD S |  | SECURITY EQUIPMENTS
1 | MR | DFMD for Entrance/reception
Supply, Installation, testing and commissioning of FULL-HEIGHT, 360° DETECTION DFMD Single pole Type. Detection of all cell phones and other contraband ,concealed on the person or in body cavities (including keyfob cell phones) with or without batteries , Multi-Zone targeting indication identifi es location ,of contraband on the body, Fully weather proof for outdoor use (IP65 certifi ed), minimum 90 minutes continuous use on embedded battery operation, Unmatched detection in all environments without adjustment, Extremely durable design, No assembly required: 10 second set-up, Detection of all cell phones and other contraband concealed on the person or in body cavities (including keyfob cell phones) with or without batteries, Detection of magnets and ferromagnetic metals.
|  | Full-height, 360° detection (horizontal & vertical),5 individual zones for pinpointing locations of contraband on the body, Covert operation through use of Bluetooth headset (included), Fully weather proof for outdoor use, Up to minimum 90 minutes continuous battery operation, One- piece and lightweight design easily transportable by one person, Unmatched detection in all environments without adjustment, Extremely durable design using stainless steel and high impact reinforced plastics, Anti-tip suction cups for securing to smooth fl oor surfaces (included, Non-emitting device: safe for use for pace-makers and other medical implants. | Nos. |  | 5
2 | MR | HHMD
|  | Supply, Installation, Testing & Commissioning of Hand Held Metal Detector (HHMD), Garrett Super Wand or equivalent Operating Frequency 95 KHz Audio Frequency 2 KHz Operating Temperature -37 deg.C to 70 deg.C Humidity 95% noncondensing Dimensions: 48.3 cm(L) x 8.3cm(W) x 3.2cm(T) 9V cadmium free NiMH Rechargeable batteries, The batteries shall provide up to 20 hours of charge for 12-hours recharge. HHMD shall have audible speaker. Controls: 3-Way switch i.e. On (Speaker/LED Light), Off and On (Vibrating/LED Light) Individual Suitable Charger shall be supplied for each HHMD. | Nos. |  | 10
3 | MR | Baggage Scanner
|  | Supply, installation, testing and commissioning of Baggage Scanner, Tunnel Opening - minimum (W x H)606mm x 420mm) or better, Conveyor Speed (m/sec)0, 24@60Hz / 0,20@50Hz, Generator Voltage (Operating) 180kV operating at 170kV, Conveyor minimum Load 150kg or better, Wire Resolution (ASTM F792) 40 AWG7, Weight 750kg, Dimensions (L,W,H) 1980mm, 1147mm, 1240mm,Color Imaging (No black / white) 3 Color Imaging, Contrast Sensitivity 65.000 Grey levels, Geometric Image Dist. Correction Yes,Image Separation (mm) 1.0 Horizontal / 1.0 Vertical, Image Size 270 lines/sec, ZoomUp to 128x, Display resolution 1360 X 768 / 24 bit,Reports format PDF, ODT, XLS, TXT or direct print, Image Archiving Automatic (200,000 images), TCP/IP. | Nos. |  | 5
4 | MR | Supply, installation, testing and commissioning of i-7 PC, Latest Generation, 2 TB SSD, 64 GB RAM, 4GB Graphic Card with Window 11 & 22 inch Monitor | Nos |  | 1
Note: Project Specific MAF (Manufacturer's Authorization Form) Certificate required from OEM to ensure the System Integrator is authorized & that the OEM will support the System Integrator before execution & during execution of the project.
TOTAL CARRIED OVER TO SUMMARY
SUB HEAD T | CHAPTER 18 | ELECTRICAL VEHICLE CHARGER
| DSR-2025- 18.1 | Supplying Installation, Testing and Commissioning of EV charging station As per specifications and in Compliance to relevant IS codes etc.
1 | DSR-2025- 18.1.1 | Light EV AC Charger (Mode-3) Power : 7 kW, Input power supply: 1phase 230 +10% Volt, output supply: 230 Volt AC, Frequency:50 Hz +/-3%, Operational temperature range : -25 to 55 0C (outdoor), -5 to 550C (Indoor)., RH upto 95%, Charging Device as per IS-17017-22-1 EV- EVSE Communication: as per relevant IS Codes, Bluetooth Low Energy, one Charge Point Plug/ Socket as per IS-60309 and IS-17017-2, Vehicle Inlet/ Connector As per EV manufacturer, suitable for 2 Wheelers and 4 wheelers. Indoor use: at least IP42; Outdoor use: at least IP54. Mechanical Strength: protection of the external enclosure against mechanical impact shall be IK08 according to IEC 62262.O/L,S/C protection. Insulation Resistance > 1 MΩ. Cable Length: 7.5 m. RCD having a rated residual operating current not exceeding 30 mA; Separate RCD for multiple outputs. Telecommunication port of the EV supply equipment according to IS 13252 (Part1): 2010. OCPP(Open charge point protocol) 1.6J upgradable to ocpp 2.0. Device Should follow 17017 series of IS codes in general and the installation of the system shall comply with relevant IS Codes. | Each |  | 50
2 | DSR-2025- 18.1.3 | Parkbay AC Charger (Mode -3) Power Level 2: Normal Power ~11kW/ 22 kW, 3 phase 415VAC(- 40% to+20%), Frequency:50 Hz +/-5%, output supply: 240 Volt AC, Operational temperature range : -25 to 55 0C (outdoor), -5 to 55 0C (Indoor), RH upto 95%, Charging Device as per IS- 17017-1 EV-EVSE ISO- 15118 for Smart Charging, Infrastructure Socket as per IS-17017-2-2, Vehicle Connector as per IS- 17017-2-2 Vehicle Inlet/ Connector As per EV manufacturer, suitable for 4 wheelers. Indoor use: at least IP42; Outdoor use: at least IP 54. Mechanical Strength : protection of the external enclosure against mechanical impact shall be IK08 according to IEC 62262. O/L,S/C protection. Insulation Resistance > 1M Ω. Cable Length: 7.5 . RCD having a rated residual operating current not exceeding 30 mA; Separate RCD for multiple outputs. Telecommunication port of the EV supply equipment according to IS 13252 (Part1): 2010. OCPP(Open charge point protocol) 1.6J upgradable to ocpp 2.0. Device Should follow 17017 series of IS codes in general and the installation of the system shall comply with relevant IS Codes. | Each |  | 5
3 | MR | The 60 kW DC Charger is designed for three-phase input supply supporting a voltage range from 285 - 475 V AC. The output voltage range of 150–1000 V DC and a frequency range of 45–55 Hz. It operates at a rated current of approximately 120 A, while standby power consumption remains below 10 W. The charger features a single Type 2 DC outlet with an IEC- 62196 Type 2 connector, delivering an output power of 60 kW and a maximum current of 200 A through a cable of 5 meters or more. Suitable for both Indoor and outdoor installation, it is wall- mounted/stand mounted and offers IP55 protection, natural air cooling, and dimensions of 717 × 939 × 409 mm, constructed from durable plastic. It operates reliably in ambient temperatures from -30°C to +55°C. Safety and protection mechanisms include input-side overcurrent and short-circuit protection, overvoltage and undervoltage protection, ground fault detection, overtemperature protection with derating or shutdown, internal residual current detection, surge protection, stuck actuator protection, earth leakage detection, smoke sensors for system shutdown, Insulation/Isolation resistance monitoring (IMD alarm). Troubleshooting is supported through diagnostic functions, over-the-air software updates, and monitoring via OCPP v1.6 or later and capable for billing and transaction with diffrent modes of payment. Communication options include Ethernet, Wi-Fi, GSM 4G/LTE, and Bluetooth, complemented by backlit LED indicators for charging states. The charger complies with EMI/EMC and safety standards IEC61851 and IS17017. | Each |  | 5
TOTAL CARRIED OVER TO SUMMARY
SUB HEAD U |  | PARKING MANAGEMENT / GUIDANCE SYSTEM
Design, Supply, installation, testing and commissioning of following Automatin System for Parking Management System / Guidance:
1 | MR | Supply, installation and commissioning of long range RFID UHF Reader, 12 mtr reading range,Communication Interface -RJ 45, RS 232, RS 485, Wiegand, Trigger,Protocol-EPC C1 GEN2/ISO 18000-6C ,12dBi circular polarization Built-in antenna,26 dBm power (adjustable by 1dBm step),operating power 9V/3A , RJ45 rate - 10 Mbps Frequency range 865.1-869.7 Mhz Dimensions- 445mm x 445mm x 55mm Material- ABS+PVC, complete with Pole mounting accessories. ISO, CE, FCC Certified. | Nos. |  | 2
2 | MR | Supply, installation and commissioning of Controller for RFID readers, PVC enclosure box,Processor-Broadcom BCM2837B0, Cortex-A53 64 bit SoC @ 1.4 GHz,1 GB LPDDR2 SDRAM Memory,GPIO Access with Extended 40-pin GPIO header, Connectivity- 2.4 GHz and 5 Ghz IEEE 802.11.b/g/m/ac wireless LAN, Bluetooth 4.2, BLE, Gigabit Ethernet over USB 2.0 (maximum throughput 300 Mbps), 4 x USB 2.0 ports Micro SD card supported for loading operating system and data storage, operating temperature-0-60° C, Complete with pole/wall mounting accessories | Nos. |  | 2
3 | MR | Supply, installation and commissioning of user information full color matrix LED display of size 160*600 mm | Nos. |  | 2
4 | MR | Supply, installation and commissioning of Server for parking management and Guidance system with the Intel Xeon E5 Series (4 core, 1.8 GHz), 32 GB RAM, 2 TB SSD ,4 Hot Pluggable SFF drive, RAID enabled, with (OS window server 2012 R2 or higher version &SQL) , 18.5” / 19” TFT Color monitor,Key board Mouse | Nos. |  | 1
5 | MR | Supply, installation and commissioning of 8 Port PoE Network switch with 10/100/1000 Ethernet, power port for AC adapter or power cord port,Devices supporting 802.3 Ethernet, 802.u Faster Ethernet, or 802.3ab Gigabit Ethernet Cat6A or better Ethernet cable | Nos. |  | 1
#REF! | MR | Supply, installation, testing and commissioning of Ultrasonic Sensors to sense the vehicle occupancy with automatic detection. Ultrasonic detection sensing with RS485 as communication protocol, detectable range of 0.3m to 4.5m, Scope of detection: 15 deg, Operating temp:-20 to +60 Deg C. ISO-9001:2015, 14001:2015, CE, ROHS, FCC Certified,IP 67 certified from Govt accredited lab. The unit should have with all required mounting connectors & Accessories. (For Covering all the three basements for PFC Parking) | Nos. |  | 750
#REF! | MR | Supply, installation, testing and commissioning of Space LED Indicator (RG) to show the occupancy or vacant bay status with Red/ Green Clour. The unit should have with all required mounting connectors & Accessories. (For Covering all the three basements for PFC Parking) | Nos. |  | 750
#REF! | MR | Supply, installation, testing and commissioning of PFC Reflective Sign boards for Car Park Indication (10" x 6") at each parking slot. The unit should have with all required mounting connectors & Accessories. (For Covering all the three basements for PFC Parking) | Nos. |  | 750
#REF! | MR | Supply, installation, testing and commissioning of ZONE CONTROLLER: Equipped with communication protocol: RS485, with Standard Baud rate, Maximum load quantity 28 loads. Minimum Communication distance: 400 mtrs, Working temp range: 5 deg C to 50 deg C. The above shall be housed in a vandal proof, lockable & secure PVC Cabinets to be supplied along with the Controllers and its necessary accessories. | Nos. |  | 30
#REF! | MR | Supply, installation, testing and commissioning of Master Controller for getting informations from the zonal controller,Operating voltage :AC220V± 10%, Communication protocol : TCP/IP | Nos. |  | 1
#REF! | MR | Supply, installation, testing and commissioning of Parking Availability Display (1 Row, 1 column, 3 Character, 4" characterHeight, indoor) - Directional Display | Nos. |  | 42
#REF! | MR | Supply, installation, testing and commissioning of Parking Availability Display (1 Row, 1 column, 3 Character, 4" characterHeight, Outdoor) - Floor Display | Nos. |  | 3
#REF! | MR | Supply, installation, testing and commissioning of Parking Availability Display (3 Row, 2 column, 3 Character, 4" characterHeight, Outdoor) - Main Gate | Nos. |  | 1
CABLES, CONDUITS & ACCESSORIES
15 | DSR-2025- 39.18 | Supplying, drawing, Testing and commissioning of Cat6A UTP 4 pair, 23 AWG solid copper cable in existing conduit/ on surface, U/FTP, LSZH, Non- Plenum, Horizontal (solid) Cable suitable for high speed data networking application supporting upto 10Gbps over a 100 meter channel. The 4 Unshielded Twisted Pairs (UTP) cable with color coded insulation for easy indentification should have FLAME PROPERTIES i.e. Flammability Test - IEC 60332-1, Smoke Density - IEC 61034, LSZH standards compliance: ANSI/TIA-568 C.2, ISO/IEC 11801, IEEE 802.3an, RoHS. Delay Skew should be < 45NS. The outer Cable Diameter should be 7.5 + 2 mm. Cable should have been tested and verified by UL/ ETL etc. complete as required.
| DSR-2025- | 1 run of cable | RM |  | 1150
16 | MR | Supply & laying of 4C x 1.0 sq mm Flexible Multistrand cable for signal / power as per specification. (from Sensor & Devices to Controller) on cable tray surface . As per system requirement to cover all the floors and parking slots. | RM |  | 7350
17 | MR | Supply & laying of 3C x 1.5 sq mm Power Cables Flexible Multistrand cable for signal / power as per specification in PVC Conduits on surface . As per system requirement to cover all the floors and parking slots. | RM |  | 2400
18 | DSr-2025- 1.2 | Supplying and fixing of following sizes of steel conduit along with accessories in surface/recess including painting in case of surface conduit, or cutting the wall and making good the same in case of recessed conduit as required.
| DSr-2025- 1.20.2 | 25mm | RM |  | 7200
Note: Project Specific MAF (Manufacturer's Authorization Form) Certificate required from OEM to ensure the System Integrator is authorized & that the OEM will support the System Integrator before execution & during execution of the project.
TOTAL CARRIED OVER TO SUMMARY
SUB HEAD V |  | SOLAR PV (12KW) SYSTEM - DISMANTILING & RE-INSTALLATION
|  | Dismantling, shifting, installation, testing and commissioning of EXISTING 12KW solar plant at terrace. (Shifting to be done approx. 20 meter away from existing location, shifting shall include complete installation as per site as reqiured. Contractor need to visit site for asses the volumn of work and understand the complete scope and the use of the exisng modules and structure, canling etc.) | Lot |  | 1
TOTAL CARRIED OVER TO SUMMARY

## LIGHT FIXTURES
ITEM NO. | DSR / NDSR (MR) | ITEM DESCRIPTIONS | Unit | QTY. | Rate |  | Amount (In Rs.)
[5 empty] | Supply | Installation | Supply | Installation
SUB HEAD Q |  | LIGHT FIXTURES
Important Notes: 1. Base specifications are given for 4000 -6000 Kelvin. However, all fixtures shall be considered with tunable White Operations for consideration of well being Norms. 2. CRI value of all the fixtures shall be greater than 90. 3. UGR value shall be considered as per the given details in the specifications. All product shall be with UGR less than 19 and specific areas given in the detail specification with UGR 16 shall be considered as given in specifications. 4. DALI Type 2 Drivers shall be considered for all the fixtures (non dim considered for BOH & certain other areas) and all Drivers shall be Tunable white. (there is no tuneable light fixture in the BoQ) 5. Drivers shall be flicker free in operations. 6. LED Life time shall be Minimum L90 50,000 Working Hours 7. All LED fixtures shall have warranty as per OEM or atleast 6 years whichever is higher.
1 | MR | Supply,Installation,Testing and Commissioning of LED strip for mounting in Cove SDCM 3 bin rolls, Color temperature 4000K, CRI≥90, efficacy 100-120lm/w, IP20, working temperature -20°C to +35°C, SUpply & Fixing volatage 24V DC. The strip shall have a cutting pitch of 6.25 mm, a minimum bend radius of 50 mm, and be supplied with 3MM backing for mounting, compatible with aluminum U/L-channel profiles for better heat dissipation. The luminaire shall have an IP20 protection rating, suitable for operation in ambient temperatures between –25 °C and +40 °C, and a rated service life of at least 50,000 hours (L70 @ 25 °C) tested per LM-79 and LM-80 standards. The system shall be dimmable. The LED strips shall be supplied in standard 5-meter reels, complete with all mounting accessories necessary for a complete installation. The bidder shall submit the NABL accreditation of LED luminaire manufacturer along with technical bid. The bidder shall submit the Type test of luminaires & LM79 test reports issued by NABL accredited lab before SUpply & Fixing of material. DALI 2 BALLAST | RM | 2030 |  | 50 | 0 | 101500
2 | MR | Supply,Installation,Testing and Commissioning of LED strip for mounting in Cove SDCM 3 bin rolls, Color temperature 4000K, CRI≥90, efficacy 100-120lm/w, IP20, working temperature -20°C to +35°C, SUpply & Fixing volatage 24V DC. The strip shall have a cutting pitch of 6.25 mm, a minimum bend radius of 50 mm, and be supplied with 3MM backing for mounting, compatible with aluminum U/L-channel profiles for better heat dissipation. The luminaire shall have an IP20 protection rating, suitable for operation in ambient temperatures between –25 °C and +40 °C, and a rated service life of at least 50,000 hours (L70 @ 25 °C) tested per LM-79 and LM-80 standards. The system shall be dimmable. The LED strips shall be supplied in standard 5-meter reels, complete with all mounting accessories necessary for a complete installation. The bidder shall submit the NABL accreditation of LED luminaire manufacturer along with technical bid. The bidder shall submit the Type test of luminaires & LM79 test reports issued by NABL accredited lab before SUpply & Fixing of material. The bidder shall submit the NABL accreditation of LED luminaire manufacturer along with technical bid. The bidder shall submit the Type test of luminaires & LM79 test reports issued by NABL accredited lab before SUpply & Fixing of material. DALI 2 BALLAST | RM | 865 |  | 50 | 0 | 43250
3 | MR | Supply,Installation,Testing and Commissioning of recessed mounted deep recessed Round Shape Fixed spot light, made up of pressure die-cast aluminium housing and white trim with diffuser,The luminaire shall deliver minimum of 1200-1400lumens with system efficacy of >90 to 120lm/w.. Powered by electronic LED driver with Output Short-circuit protection, Surge protection 4KV. Color temperature 4000K. Dimensions: Cut out Dia-90mm. The Luminaire shall be IP20 complaint.CRI 90 & RA≥70, SDCM<3. Beam Angle option of >50 deg. The driver of the LED downlighter shall be isolated driver and shall have minimum operating voltage of 140V to 270V, PF≥0.90 & THD≤10%, . The luminaire shall have Class B serviceability and the life of luminaire shall be 50000hrs @ L70B50. Manufacturer shall have inhouse lab approved by NABL or ministry of science of govt of India. LM 79 and LM80 reports need to be submitted from a NABL/UL accredited lab to verify above parameters. Both the fixture and Driver should have separate BIS approval. (Non Dim driver) | Nos. | 1381 |  | 250 | 0 | 345250
4 | MR | Supply,Installation,Testing and Commissioning of recessed mounted deep recessed Round Shape Adjustable spot light, made up of pressure die-cast aluminium housing and white trim with diffuser, The luminaire shall deliver minimum of 1000-1200lumens with system efficacy of>90 to 120lm/w.. Powered by electronic LED driver with Output Short-circuit protection, Surge protection 4KV. Color temperature Tunable. Dimensions: Cut out Dia-75mm. The Luminaire shall be IP20 complaint. CRI 90 & RA≥70, SDCM<3. Beam Angle option of >50 deg. The driver of the LED downlighter shall be isolated driver and shall have minimum operating voltage of 140V to 270V, PF≥0.90 & THD≤10%, . The luminaire shall have Class B serviceability and the life of luminaire shall be 50000hrs @ L70B50. Manufacturer shall have inhouse lab approved by NABL or ministry of science of govt of India. LM 79 and LM80 reports need to be submitted from a NABL/UL accredited lab to verify above parameters. Both the fixture and Driver should have separate BIS approval. Fixture price to include dimmable driver. | Nos. | 4113 |  | 250 | 0 | 1028250
5 | MR | Supply,Installation,Testing and Commissioning of 20W Recessed mounted deep recessed round shape fixed spot COB high efficacy downlighter, made up of pressure die-cast aluminium housing and white trim with reflector options of both white and Aluminium reflector finish with minimum system lumen output of 2000lm with =<130lm/W system efficacy, with beam angle of 80 deg and 60 deg respectively. The luminaire shall have life of 50000hrs @L70B50, CRI ≥90, SDCM 5, THD ≤10%, pf ≥0.9, CCT-4000k. Dimensions: Cut out Dia-150mm. The Luminaire shall be IP20 complaint. The product shall have internal surge protection of 3.5kV, with operating temperature range of 0 to 45 deg C and operating voltage range of 140-270V. Manufacturer shall have inhouse lab approved by NABL or ministry of science of govt of India. LM 79 and LM80 reports need to be submitted from a NABL/UL accredited lab to verify above parameters. Both the fixture and Driver should have separate BIS approval. Fixture price to include dimmable driver. | Nos. | 88 |  | 250 | 0 | 22000
6 | MR | Supply,Installation,Testing and Commissioning of Suspended/Surface mounted Cylinderical Downlight with Micro Prismatic diffuser better UGR rating, 1500-1600 lm, CCT 4000k, SDCM<5, CRI 90, Efficacy ≥100lm/W, Surge 2.5KV internal, THD ≤10% (At Full Load), pf ≥0.9. The luminaire housing shall be Extruded aluminum housing, white finish, Product Dia 75mm, Height 150mm, Life L70B50 @ 50K Hrs.@ 45 Degree Ambient temp. The product should be with current ripple factor <5%. The product should have beam angle option of >50° beam angles to choose from as per the application. The operating temperature should be -10° to +45°; operating volateg range shall be 140-270V. The product shall be Class B serviceability. Manufacturer shall have inhouse lab approved by NABL or ministry of science of govt of India. LM 79 and LM80 reports need to be submitted from a NABL/UL accredited lab to verify above parameters. Both the fixture and Driver should have separate BIS approval. Fixture price to include dimmable driver. | Nos. | 1273 |  | 300 | 0 | 381900
7 | MR | Supply,Installation,Testing and Commissioning of of Suspended Up-Down W 35MMxH 35MM x L 2400 MM linear 65mm wide Continuous LED luminaire made of extruded aluminum, with special lens of dew drop facet design(housed in antiglare shield) & sunflower tessellation to have Delta wing distribution. The luminaire shall have system efficacy of =<130lm/W with 5400Lumen & beam angle of 65-70 degree, UGR<16, The LED shall be with CRI≥90 SDCM<3, CCT option of 4000K. Luminance ≤ 6,000 cd/m2 at any angle between 45 and 90 degrees from nadir, Operating temperature of the luminaire shall be 0°C to +45°C and driver shall comply to the minimum electronic parameters of THD<10%, PF ≥0.95, internal surge protection of 3.5KV, The life shall be 50K Hrs. at L70B50 @ 45deg C. , operating voltage range of 140V - 270V having Class - I protection & serviceability of Class B. The luminaire shall be IP20 & IK02 compliance. The driver shall be of the same make as that of LED luminaire. Luminaire manufacturer must have IN-house NABL accredited lab to conduct LM79, Type test as per IS10322. The successful bidder must submit the NABL accreditation certificate for Luminaire manufacturer. The LED Luminaire & it's driver both should be BIS registered. The luminaire shall be supplied with adjustable suspension wires. The manufacturer shall submit the following reports before SUpply & Fixing of material for approvals LM79 issued by NABL accredited lab, LM80 issued by LED manufacturer. Luminaire should be ROHS/REACH/EPD/LEED & Well Compliant. DALI 2 BALLAST | Nos. | 4 |  | 300 | 0 | 1200
8 | MR | Supply,Installation,Testing and Commissioning of Suspended Up-Down 35mm x 35mm x 3000mm linear 65mm wide Continuous LED luminaire made of extruded aluminum, with special lens of dew drop facet design(housed in antiglare shield) & sunflower tessellation to have Delta wing distribution. The luminaire shall have system efficacy of =<120lm/W with 1200- 1500Lumen/Meter with 70:30 Ratio & beam angle of 65-70 degree, UGR<16, The LED shall be with CRI≥90 SDCM<3, CCT option of 4000K. Luminance ≤ 6,000 cd/m2 at any angle between 45 and 90 degrees from nadir, Operating temperature of the luminaire shall be 0°C to +45°C and driver shall comply to the minimum electronic parameters of THD<10%, PF ≥0.95, internal surge protection of 3.5KV, The life shall be 50K Hrs. at L70B50 @ 45deg C. , operating voltage range of 140V - 270V having Class - I protection & serviceability of Class B. The luminaire shall be IP20 & IK02 compliance. The driver shall be of the same make as that of LED luminaire. Luminaire manufacturer must have IN-house NABL accredited lab to conduct LM79, Type test as per IS10322. The successful bidder must submit the NABL accreditation certificate for Luminaire manufacturer. The LED Luminaire & it's driver both should be BIS registered. The luminaire shall be supplied with adjustable suspension wires. The manufacturer shall submit the following reports before SUpply & Fixing of material for approvals LM79 issued by NABL accredited lab, LM80 issued by LED manufacturer. Luminaire should be ROHS/REACH/EPD/LEED & Well Compliant. DALI 2 BALLAST | Nos. | 1 |  | 300 | 0 | 300
9 | MR | Supply,Installation,Testing and Commissioning of Suspended Down W35mm x H35mm x L 1600mm linear 65mm wide Continuous LED luminaire made of extruded aluminum, with special lens of dew drop facet design(housed in antiglare shield) & sunflower tessellation to have Delta wing distribution. The luminaire shall have system efficacy of =<130lm/W with 1200- 1500Lumen/meter & beam angle of 65-70 degree, UGR<16, The LED shall be with CRI≥90 SDCM<3, CCT option of 4000K. Luminance ≤ 6,000 cd/m2 at any angle between 45 and 90 degrees from nadir, Operating temperature of the luminaire shall be 0°C to +45°C and driver shall comply to the minimum electronic parameters of THD<10%, PF ≥0.95, internal surge protection of 3.5KV, The life shall be 50K Hrs. at L70B50 @ 45deg C. , operating voltage range of 140V - 270V having Class - I protection & serviceability of Class B. The luminaire shall be IP20 & IK02 compliance. The driver shall be of the same make as that of LED luminaire. Luminaire manufacturer must have IN-house NABL accredited lab to conduct LM79, Type test as per IS10322. The successful bidder must submit the NABL accreditation certificate for Luminaire manufacturer. The LED Luminaire & it's driver both should be BIS registered. The luminaire shall be supplied with adjustable suspension wires. The manufacturer shall submit the following reports before SUpply & Fixing of material for approvals LM79 issued by NABL accredited lab, LM80 issued by LED manufacturer. Luminaire should be ROHS/REACH/EPD/LEED & Well Compliant. DALI 2 BALLAST | Nos. | 4 |  | 300 | 0 | 1200
10 | MR | Supply,Installation,Testing and Commissioning of Suspended Down W35mm x H35mm x L1800mm Continuous LED luminaire made of extruded aluminum, with special lens of dew drop facet design(housed in antiglare shield) & sunflower tessellation to have Delta wing distribution. The luminaire shall have system efficacy of =<130lm/W with 1200-1500Lumen/meter with beam angle of 65-70 degree, UGR<16, The LED shall be with CRI≥90 SDCM<3, CCT option of 4000K. Luminance ≤ 6,000 cd/m2 at any angle between 45 and 90 degrees from nadir, Operating temperature of the luminaire shall be 0°C to +45°C and driver shall comply to the minimum electronic parameters of THD<10%, PF ≥0.95, internal surge protection of 3.5KV, The life shall be 50K Hrs. at L70B50 @ 45deg C. , operating voltage range of 140V - 270V having Class - I protection & serviceability of Class B. The luminaire shall be IP20 & IK02 compliance. The driver shall be of the same make as that of LED luminaire. Luminaire manufacturer must have IN-house NABL accredited lab to conduct LM79, Type test as per IS10322. The successful bidder must submit the NABL accreditation certificate for Luminaire manufacturer. The LED Luminaire & it's driver both should be BIS registered. The luminaire shall be supplied with adjustable suspension wires. The manufacturer shall submit the following reports before SUpply & Fixing of material for approvals LM79 issued by NABL accredited lab, LM80 issued by LED manufacturer. Luminaire should be ROHS/REACH/EPD/LEED & Well Compliant. DALI 2 BALLAST | Nos. | 5 |  | 300 | 0 | 1500
11 | MR | Supply,Installation,Testing and Commissioning of Suspended Down 5ft linear 65mm wide Continuous LED luminaire made of extruded aluminum, with special lens of dew drop facet design(housed in antiglare shield) & sunflower tessellation to have Delta wing distribution. The luminaire shall have system efficacy of =<130lm/W with 1200-1500Lumen/meter & beam angle of 65-70 degree, UGR<16, The LED shall be with CRI≥90 SDCM<3, CCT option of 4000K. Luminance ≤ 6,000 cd/m2 at any angle between 45 and 90 degrees from nadir, Operating temperature of the luminaire shall be 0°C to +45°C and driver shall comply to the minimum electronic parameters of THD<10%, PF ≥0.95, internal surge protection of 3.5KV, The life shall be 50K Hrs. at L70B50 @ 45deg C. , operating voltage range of 140V - 270V having Class - I protection & serviceability of Class B. The luminaire shall be IP20 & IK02 compliance. The driver shall be of the same make as that of LED luminaire. Luminaire manufacturer must have IN-house NABL accredited lab to conduct LM79, Type test as per IS10322. The successful bidder must submit the NABL accreditation certificate for Luminaire manufacturer. The LED Luminaire & it's driver both should be BIS registered. The luminaire shall be supplied with adjustable suspension wires. The manufacturer shall submit the following reports before SUpply & Fixing of material for approvals LM79 issued by NABL accredited lab, LM80 issued by LED manufacturer. Luminaire should be ROHS/REACH/EPD/LEED & Well Compliant. DALI 2 BALLAST | Nos. | 4 |  | 350 | 0 | 1400
12 | MR | Supply,Installation,Testing and Commissioning of Suspended Down W35mm x H35mm x L3300- 3400mm Continuous LED luminaire made of extruded aluminum, with special lens of dew drop facet design(housed in antiglare shield) & sunflower tessellation to have Delta wing distribution. The luminaire shall have system efficacy of =<130lm/W with 1200-1500Lumen/meter & beam angle of 65-70 degree, UGR<16, The LED shall be with CRI≥90 SDCM<3, CCT option of 4000K. Luminance ≤ 6,000 cd/m2 at any angle between 45 and 90 degrees from nadir, Operating temperature of the luminaire shall be 0°C to +45°C and driver shall comply to the minimum electronic parameters of THD<10%, PF ≥0.95, internal surge protection of 3.5KV, The life shall be 50K Hrs. at L70B50 @ 45deg C. , operating voltage range of 140V - 270V having Class - I protection & serviceability of Class B. The luminaire shall be IP20 & IK02 compliance. The driver shall be of the same make as that of LED luminaire. Luminaire manufacturer must have IN-house NABL accredited lab to conduct LM79, Type test as per IS10322. The successful bidder must submit the NABL accreditation certificate for Luminaire manufacturer. The LED Luminaire & it's driver both should be BIS registered. The luminaire shall be supplied with adjustable suspension wires. The manufacturer shall submit the following reports before SUpply & Fixing of material for approvals LM79 issued by NABL accredited lab, LM80 issued by LED manufacturer. Luminaire should be ROHS/REACH/EPD/LEED & Well Compliant. DALI 2 BALLAST | Nos. | 5 |  | 350 | 0 | 1750
13 | MR | Supply,Installation,Testing and Commissioning of Suspended Down W35mm x H35mm x L3200- 3300mm Continuous LED luminaire made of extruded aluminum, with special lens of dew drop facet design(housed in antiglare shield) & sunflower tessellation to have Delta wing distribution. The luminaire shall have system efficacy of =<130lm/W with 1200-1500Lumen/meter & beam angle of 65-70 degree, UGR<16, The LED shall be with CRI≥90 SDCM<3, CCT option of 4000K. Luminance ≤ 6,000 cd/m2 at any angle between 45 and 90 degrees from nadir, Operating temperature of the luminaire shall be 0°C to +45°C and driver shall comply to the minimum electronic parameters of THD<10%, PF ≥0.95, internal surge protection of 3.5KV, The life shall be 50K Hrs. at L70B50 @ 45deg C. , operating voltage range of 140V - 270V having Class - I protection & serviceability of Class B. The luminaire shall be IP20 & IK02 compliance. The driver shall be of the same make as that of LED luminaire. Luminaire manufacturer must have IN-house NABL accredited lab to conduct LM79, Type test as per IS10322. The successful bidder must submit the NABL accreditation certificate for Luminaire manufacturer. The LED Luminaire & it's driver both should be BIS registered. The luminaire shall be supplied with adjustable suspension wires. The manufacturer shall submit the following reports before SUpply & Fixing of material for approvals LM79 issued by NABL accredited lab, LM80 issued by LED manufacturer. Luminaire should be ROHS/REACH/EPD/LEED & Well Compliant. DALI 2 BALLAST | Nos. | 14 |  | 350 | 0 | 4900
14 | MR | Supply,Installation,Testing and Commissioning of Suspended Down W35mm x H35mm x L900- 1000mm Continuous LED luminaire made of extruded aluminum, with special lens of dew drop facet design(housed in antiglare shield) & sunflower tessellation to have Delta wing distribution. The luminaire shall have system efficacy of =<130lm/W with 1200-1500Lumen/meter & beam angle of 65-70 degree, UGR<16, The LED shall be with CRI≥90 SDCM<3, CCT option of 4000K. Luminance ≤ 6,000 cd/m2 at any angle between 45 and 90 degrees from nadir, Operating temperature of the luminaire shall be 0°C to +45°C and driver shall comply to the minimum electronic parameters of THD<10%, PF ≥0.95, internal surge protection of 3.5KV, The life shall be 50K Hrs. at L70B50 @ 45deg C. , operating voltage range of 140V - 270V having Class - I protection & serviceability of Class B. The luminaire shall be IP20 & IK02 compliance. The driver shall be of the same make as that of LED luminaire. Luminaire manufacturer must have IN-house NABL accredited lab to conduct LM79, Type test as per IS10322. The successful bidder must submit the NABL accreditation certificate for Luminaire manufacturer. The LED Luminaire & it's driver both should be BIS registered. The luminaire shall be supplied with adjustable suspension wires. The manufacturer shall submit the following reports before SUpply & Fixing of material for approvals LM79 issued by NABL accredited lab, LM80 issued by LED manufacturer. Luminaire should be ROHS/REACH/EPD/LEED & Well Compliant. DALI 2 BALLAST | Nos. | 2 |  | 350 | 0 | 700
15 | MR | Supply,Installation,Testing and Commissioning of stanalone Suspended slim Linear LED made of extruded Aluminium with white/black powder coaed finish with high efficiency drop down polycarbonate/PS diffuser to have volumetric light distribution and wide angle illumination. The luminaire shall have a W35mm x H35mm x L2000mm. LED Used shall be SMD type with approx system Lumens 4800 & efficacy =>120lm/W,1200-1500Lm/Meter, Life of fixture : 50000 burning Hrs. @ L70B50 Lumen maintenance, CCT of 4000K (SDCM<=5), CRI Ra ≥80, PF ≥0.95, THD≤10%, an Operating working temp range - 0°C < Ta < 45°C & operating Voltage Range of 140-270 V AC. Minimum Internal Surge Protection 3.5kV. Luminaire with Ingress & IK protection Rating of of IP20 & IK02.The driver shall be compliant to IEC61347-2-13, IEC62384 & IEC6100-3 2. The driver & Luminaire shall be BIS registered. The driver shall be designed for continuous operation of minimum 12-15Hrs a day. The luminaire driver shall be of the same make/manufacturer as that of LED luminaires. Luminaire manufacturer must have In-house NABL accredited lab in India to conduct LM79, Type test as per IS10322, "FAT" before dispatch as per IS 10322 & IK Test. The successful bidder must submit the NABL accreditation certificate for Luminaire manufacturer. The manufacturer shall submit the following reports before SUpply & Fixing of material for approvals LM79 issued by NABL accredited lab, LM80 issued by LED manufacturer. DALI 2 BALLAST | Nos. | 4 |  | 350 | 0 | 1400
16 | MR | Supply,Installation,Testing and Commissioning of Suspended Down W35mm x H35mm x L4500- 4600mm Continuous LED luminaire made of extruded aluminum, with special lens of dew drop facet design(housed in antiglare shield) & sunflower tessellation to have Delta wing distribution. The luminaire shall have system efficacy of =<130lm/W with 1200-1500Lumen/meter & beam angle of 65-70 degree, UGR<16, The LED shall be with CRI≥90 SDCM<3, CCT option of 4000K. Luminance ≤ 6,000 cd/m2 at any angle between 45 and 90 degrees from nadir, Operating temperature of the luminaire shall be 0°C to +45°C and driver shall comply to the minimum electronic parameters of THD<10%, PF ≥0.95, internal surge protection of 3.5KV, The life shall be 50K Hrs. at L70B50 @ 45deg C. , operating voltage range of 140V - 270V having Class - I protection & serviceability of Class B. The luminaire shall be IP20 & IK02 compliance. The driver shall be of the same make as that of LED luminaire. Luminaire manufacturer must have IN-house NABL accredited lab to conduct LM79, Type test as per IS10322. The successful bidder must submit the NABL accreditation certificate for Luminaire manufacturer. The LED Luminaire & it's driver both should be BIS registered. The luminaire shall be supplied with adjustable suspension wires. The manufacturer shall submit the following reports before SUpply & Fixing of material for approvals LM79 issued by NABL accredited lab, LM80 issued by LED manufacturer. Luminaire should be ROHS/REACH/EPD/LEED & Well Compliant. DALI 2 BALLAST | Nos. | 28 |  | 350 | 0 | 9800
17 | MR | Supply,Installation,Testing and Commissioning of rectangal W35mm x H45mm profile and fixture size is 1200mm x 3900 mm Continuos linear with deep recessed Diffuser with Up & down distribution, made up of extruded Al housing with tapered external reflector options downward of Rose Gold with Al silver housing/High gloss gold with Matt black housing/High gloss Silver with matt black housing, and with customisable finish to enhance/match interiors. The luminaire shall be of 65mm widthX100mm height, with minimum system lumen of 1200-1500lm/meter and with system efficacy of >=120lm/W. The life of fixture shall be 50000 burning hours @L70B50 lumen maintenance, CCT 4000K, SDCM<5, CRI≥90, PF≥0.95,THD≤10%, an Operating working temp range : 0°C < Ta < 45°C & operating Voltage Range of 140-270 V AC. Minimum Internal Surge Protection 3.5KV. , Power factor 0.99%, efficiency of ≥ 91% Output current ripple LF<4%, The fixture design should comply to IEC61000-3-2 ed.3.2, 2009 for Harmonics, IEC61347 -2 -13, 2006 in Conjunction with IEC61347-1 ed.2.0, 2007 for Electrical Safety, IEC62384 ed.1.1, 2011 for performance and IEC61547 ed.2.0, 2009. The luminaire shall be Class B Serviceability.The luminaire driver shall be of the same make/manufacturer as that of LED luminaires. Manufacturer shall have inhouse lab approved by NABL or ministry of science of govt of India. LM 79 and LM80 reports need to be submitted from a NABL/UL accredited lab to verify above parameters. Both the fixture and Driver should have separate BIS approval DALI 2 BALLAST | Nos. | 2 |  | 300 | 0 | 600
18 | MR | Supply,Installation,Testing and Commissioning of Standalone/Continues Recessed linear LED luminaire made of extruded aluminimum with White/Black Powder Coated finish, With Lenses and UGR reflector, with reflector color Gun-metal/black. UGR<16.The luminaire having Multiple Lumen Output Options Varying from 1200-1500 Lumens/meter to choose from,with system efficacy of ≥120lm/w. COD Dimenions W35mm x H35mm x L7550mm . Optics option of Square 50deg,Round 24deg and wallwasher.The luminaire shall have a width of not more than 55mm(± 2mm), height 64mm (± 2mm) and shall be available in multiple lengths. The life shall be 50K Hrs. at L70B50. Operating temperature of the luminaire shall be 0°C to +45°C and driver shall comply to the minimum electronic paramtere like THD≤ 10%, PF ≥0.9, internal surge protection of 4KV, operating voltage range of 140V - 270V having Class - I protection & serviceability of Class B. The luminaire shall be IP20 & IK02 compliance.The driver shall be of the same make as that of LED luminaire and must be EMI/EMC compliant.. The LEDs used shall have CCT option of 4000K having CRI≥80, & SDCM≤5. Luminaire manufacturer must have IN-house NABL accredited lab to conduct LM79, Type test as per IS10322 & "FAT". The the successful bidder must submit the NABL accreditation certificate for Luminaire manufacturer. The LED Luminaire & it's driver both should be BIS registered. The luminaire shall be supplied with adjustable suspension wires. The manufacturer shall submit the following reports before SUpply & Fixing of material for approvals LM79 issued by NABL accrediated lab, LM80 issued by LED manufacturer. DALI 2 BALLAST | Nos. | 2 |  | 300 | 0 | 600
19 | MR | Supply,Installation,Testing and Commissioning of Standalone/Continues recessed linear LED luminaire made of extruded aluminimum with White/Black Powder Coated finish, With Lenses and UGR reflector, with reflector color Gun-metal/black. UGR<16.The luminaire having Multiple Lumen Output Options Varying from 1200-1500 Lumen/meter to choose from,with system efficacy of ≥100lm/w & system wattage option 16W-44W (±5%). W35mm x H35mm x L2900-3000mmm. Optics option of Square 50deg,Round 24deg and wallwasher.The luminaire shall have a width of not more than 55mm(± 2mm), height 64mm (± 2mm) and shall be available in multiple lengths. The life shall be 50K Hrs. Operating temperature of the luminaire shall be 0°C to +45°C and driver shall comply to the minimum electronic paramtere like THD≤ 10%, PF ≥0.9, internal surge protection of 4KV, operating voltage range of 140V - 270V having Class - I protection & serviceability of Class B. The luminaire shall be IP20 & IK02 compliance.The driver shall be of the same make as that of LED luminaire and must be EMI/EMC compliant.. The LEDs used shall have CCT option of 4000K having CRI≥80, & SDCM≤5. Luminaire manufacturer must have IN-house NABL accredited lab to conduct LM79, Type test as per IS10322 & "FAT". The the successful bidder must submit the NABL accreditation certificate for Luminaire manufacturer. The LED Luminaire & it's driver both should be BIS registered. The luminaire shall be supplied with adjustable suspension wires. The manufacturer shall submit the following reports before SUpply & Fixing of material for approvals LM79 issued by NABL accrediated lab, LM80 issued by LED manufacturer. DALI 2 BALLAST | Nos. | 2 |  | 300 | 0 | 600
20 | MR | Supply,Installation,Testing and Commissioning of stanalone Suspended slim Linear LED made of extruded Aluminium with white/black powder coaed finish with high efficiency drop down polycarbonate/PS diffuser to have volumetric light distribution and wide angle illumination. The luminaire shall have a W35mm x H35mm x L1200mm. LED Used shall be SMD type with approx system Lumens 2800 & efficacy >=120-150lm/W,Life of fixture : 50000 burning Hrs. @ L70B50 Lumen maintenance, CCT of 4000K (SDCM<=5), CRI Ra ≥80, PF ≥0.95, THD≤10%, an Operating working temp range - 0°C < Ta < 45°C & operating Voltage Range of 140-270 V AC. Minimum Internal Surge Protection 3.5kV. Luminaire with Ingress & IK protection Rating of of IP20 & IK02.The driver shall be compliant to IEC61347-2-13, IEC62384 & IEC6100-3-2. The driver & Luminaire shall be BIS registered. The driver shall be designed for continuous operation of minimum 12-15Hrs a day. The luminaire driver shall be of the same make/manufacturer as that of LED luminaires. Luminaire manufacturer must have In-house NABL accredited lab in India to conduct LM79, Type test as per IS10322, "FAT" before dispatch as per IS 10322 & IK Test. The successful bidder must submit the NABL accreditation certificate for Luminaire manufacturer. The manufacturer shall submit the following reports before SUpply & Fixing of material for approvals LM79 issued by NABL accredited lab, LM80 issued by LED manufacturer. DALI 2 BALLAST | Nos. | 7 |  | 300 | 0 | 2100
21 | MR | Supply,Installation,Testing and Commissioning of rectangal 1200mmx7495mm Formed standalone/Continuos linear with deep recessed Diffuser with Up & down distribution, made up of extruded Al housing with tapered external reflector options downward of Rose Gold with Al silver housing/High gloss gold with Matt black housing/High gloss Silver with matt black housing, and with customisable finish to enhance/match interiors. The luminaire shall be of 65mm widthX100mm height, with minimum system lumen of 1200-2000lm/meter and with system efficacy of >=120lm/W. The life of fixture shall be 50000 burning hours @L70B50 lumen maintenance, CCT 4000K, SDCM<5, CRI≥90, PF≥0.95,THD≤10%, an Operating working temp range : 0°C < Ta < 45°C & operating Voltage Range of 140-270 V AC. Minimum Internal Surge Protection 3.5KV. , Power factor 0.99%, efficiency of ≥ 91% Output current ripple LF<4%, The fixture design should comply to IEC61000-3-2 ed.3.2, 2009 for Harmonics, IEC61347 -2 -13, 2006 in Conjunction with IEC61347-1 ed.2.0, 2007 for Electrical Safety, IEC62384 ed.1.1, 2011 for performance and IEC61547 ed.2.0, 2009. The luminaire shall be Class B Serviceability.The luminaire driver shall be of the same make/manufacturer as that of LED luminaires. Manufacturer shall have inhouse lab approved by NABL or ministry of science of govt of India. LM 79 and LM80 reports need to be submitted from a NABL/UL accredited lab to verify above parameters. Both the fixture and Driver should have separate BIS approval DALI 2 BALLAST | Nos. | 1 |  | 300 | 0 | 300
22 | MR | Supply,Installation,Testing and Commissioning of Standalone/Continues rectangal 8300- 8400mm x 2000-2100mm suspended linear LED luminaire made of extruded aluminimum with White/Black Powder Coated finish, With Lenses and UGR reflector, with reflector color Gun- metal/black. UGR<16.The luminaire having Multiple Lumen Output Options Varying from 1800lm- 4400 Lumens to choose from,with system efficacy of ≥100lm/w & system wattage option 16W- 44W (±5%). COD Dimenions W 42MM x H 35MM. Optics option of Square 50deg,Round 24deg and wallwasher.The life shall be 50K Hrs. at L70B50. Operating temperature of the luminaire shall be 0°C to +45°C and driver shall comply to the minimum electronic paramtere like THD≤ 10%, PF ≥0.9, internal surge protection of 4KV, operating voltage range of 140V - 270V having Class - I protection & serviceability of Class B. The luminaire shall be IP20 & IK02 compliance.The driver shall be of the same make as that of LED luminaire and must be EMI/EMC compliant.. The LEDs used shall have CCT option of 4000K having CRI≥80, & SDCM≤5. Luminaire manufacturer must have IN-house NABL accredited lab to conduct LM79, Type test as per IS10322 & "FAT". The the successful bidder must submit the NABL accreditation certificate for Luminaire manufacturer. The LED Luminaire & it's driver both should be BIS registered. The luminaire shall be supplied with adjustable suspension wires. The manufacturer shall submit the following reports before SUpply & Fixing of material for approvals LM79 issued by NABL accrediated lab, LM80 issued by LED manufacturer. DALI 2 BALLAST | Nos. | 1 |  | 3000 | 0 | 3000
23 | MR | Supply,Installation,Testing and Commissioning of Standalone/Continues recessed linear LED luminaire made of extruded aluminimum with White/Black Powder Coated finish, With Lenses and UGR reflector, with reflector color Gun-metal/black. UGR<16.The luminaire having Multiple Lumen Output Options Varying from 1800lm- 4400 Lumens to choose from,with system efficacy of ≥120lm/w & 1200-1500lm/meter. COD Dimenions W 35MM x H 35MM X L 14000-15000 MM. Optics option of Square 50deg,Round 24deg and wallwasher.The luminaire shall have a width of not more than 55mm(± 2mm), height 64mm (± 2mm) and shall be available in multiple lengths. The life shall be 50K Hrs. at L70B50. Operating temperature of the luminaire shall be 0°C to +45°C and driver shall comply to the minimum electronic paramtere like THD≤ 10%, PF ≥0.9, internal surge protection of 4KV, operating voltage range of 140V - 270V having Class - I protection & serviceability of Class B. The luminaire shall be IP20 & IK02 compliance.The driver shall be of the same make as that of LED luminaire and must be EMI/EMC compliant.. The LEDs used shall have CCT option of 4000K having CRI≥80, & SDCM≤5. Luminaire manufacturer must have IN-house NABL accredited lab to conduct LM79, Type test as per IS10322 & "FAT". The the successful bidder must submit the NABL accreditation certificate for Luminaire manufacturer. The LED Luminaire & it's driver both should be BIS registered. The luminaire shall be supplied with adjustable suspension wires. The manufacturer shall submit the following reports before SUpply & Fixing of material for approvals LM79 issued by NABL accrediated lab, LM80 issued by LED manufacturer. DALI 2 BALLAST | Nos. | 2 |  | 4900 | 0 | 9800
24 | MR | Supply,Installation,Testing and Commissioning of Standalone/Continues rectangal 2690mmx4280mm recessed linear LED luminaire made of extruded aluminimum with White/Black Powder Coated finish, With Lenses and UGR reflector, with reflector color Gun- metal/black. UGR<16.The luminaire having Multiple Lumen Output Options Varying from 1200- 1500lm/meter,with system efficacy of ≥100lm/w & system.W35mm x H35mm x profile and fixture size is 2700mm x 4500mm. Optics option of Square 50deg,Round 24deg and wallwasher. The life shall be 50K Hrs. at L70B50. Operating temperature of the luminaire shall be 0°C to +45°C and driver shall comply to the minimum electronic paramtere like THD≤ 10%, PF ≥0.9, internal surge protection of 4KV, operating voltage range of 140V - 270V having Class - I protection & serviceability of Class B. The luminaire shall be IP20 & IK02 compliance.The driver shall be of the same make as that of LED luminaire and must be EMI/EMC compliant.. The LEDs used shall have CCT option of 4000K having CRI≥80, & SDCM≤5. Luminaire manufacturer must have IN-house NABL accredited lab to conduct LM79, Type test as per IS10322 & "FAT". The the successful bidder must submit the NABL accreditation certificate for Luminaire manufacturer. The LED Luminaire & it's driver both should be BIS registered. The luminaire shall be supplied with adjustable suspension wires. The manufacturer shall submit the following reports before SUpply & Fixing of material for approvals LM79 issued by NABL accrediated lab, LM80 issued by LED manufacturer. DALI 2 BALLAST | Nos. | 1 |  | 350 | 0 | 350
25 | MR | Supply,Installation,Testing and Commissioning of Standalone/Continues rectangal recessed linear LED luminaire made of extruded aluminimum with White/Black Powder Coated finish, With Lenses and UGR reflector, with reflector color Gun-metal/black. UGR<16.The luminaire having Multiple Lumen Output Options Varying from 1200-1500 Lumens/meter to choose from,with system efficacy of ≥100lm/w. W35mm x H45mm profile and fixture size is 5300-7100mm. Optics option of Square 50deg,Round 24deg and wallwasher.The luminaire shall have a width of not more than 55mm(± 2mm), height 64mm (± 2mm) and shall be available in multiple lengths. The life shall be 50K Hrs. at L70B50. Operating temperature of the luminaire shall be 0°C to +45°C and driver shall comply to the minimum electronic paramtere like THD≤ 10%, PF ≥0.9, internal surge protection of 4KV, operating voltage range of 140V - 270V having Class - I protection & serviceability of Class B. The luminaire shall be IP20 & IK02 compliance.The driver shall be of the same make as that of LED luminaire and must be EMI/EMC compliant.. The LEDs used shall have CCT option of 4000K having CRI≥80, & SDCM≤5. Luminaire manufacturer must have IN-house NABL accredited lab to conduct LM79, Type test as per IS10322 & "FAT". The the successful bidder must submit the NABL accreditation certificate for Luminaire manufacturer. The LED Luminaire & it's driver both should be BIS registered. The luminaire shall be supplied with adjustable suspension wires. The manufacturer shall submit the following reports before SUpply & Fixing of material for approvals LM79 issued by NABL accrediated lab, LM80 issued by LED manufacturer. DALI 2 BALLAST | Nos. | 1 |  | 350 | 0 | 350
26 | MR | Supply,Installation,Testing and Commissioning of Standalone/Continues rectangal recessed linear LED luminaire made of extruded aluminimum with White/Black Powder Coated finish, With Lenses and UGR reflector, with reflector color Gun-metal/black. UGR<16.The luminaire having Multiple Lumen Output Options Varying from 1200- 1500 Lumens/meter to choose from,with system efficacy of ≥100lm/w.W35mm x H45mm profile and fixture size is 4820mm x 8820mm. Optics option of Square 50deg,Round 24deg and wallwasher.The luminaire shall have a width of not more than 55mm(± 2mm), height 64mm (± 2mm) and shall be available in multiple lengths. The life shall be 50K Hrs. at L70B50. Operating temperature of the luminaire shall be 0°C to +45°C and driver shall comply to the minimum electronic paramtere like THD≤ 10%, PF ≥0.9, internal surge protection of 4KV, operating voltage range of 140V - 270V having Class - I protection & serviceability of Class B. The luminaire shall be IP20 & IK02 compliance.The driver shall be of the same make as that of LED luminaire and must be EMI/EMC compliant.. The LEDs used shall have CCT option of 4000K having CRI≥80, & SDCM≤5. Luminaire manufacturer must have IN-house NABL accredited lab to conduct LM79, Type test as per IS10322 & "FAT". The the successful bidder must submit the NABL accreditation certificate for Luminaire manufacturer. The LED Luminaire & it's driver both should be BIS registered. The luminaire shall be supplied with adjustable suspension wires. The manufacturer shall submit the following reports before SUpply & Fixing of material for approvals LM79 issued by NABL accrediated lab, LM80 issued by LED manufacturer. DALI 2 BALLAST | Nos. | 1 |  | 350 | 0 | 350
27 | MR | Supply,Installation,Testing and Commissioning of Standalone/Continues rectangal recessed linear LED luminaire made of extruded aluminimum with White/Black Powder Coated finish, With Lenses and UGR reflector, with reflector color Gun-metal/black. UGR<16.The luminaire having Multiple Lumen Output Options Varying from 1200- 1500 Lumens/meter to choose from,with system efficacy of ≥100lm/w.W35mm x H45mm profile and fixture size is 1400-1500mm x 5700- 5800mm. Optics option of Square 50deg,Round 24deg and wallwasher.The luminaire shall have a width of not more than 55mm(± 2mm), height 64mm (± 2mm) and shall be available in multiple lengths. The life shall be 50K Hrs. at L70B50. Operating temperature of the luminaire shall be 0°C to +45°C and driver shall comply to the minimum electronic paramtere like THD≤ 10%, PF ≥0.9, internal surge protection of 4KV, operating voltage range of 140V - 270V having Class - I protection & serviceability of Class B. The luminaire shall be IP20 & IK02 compliance.The driver shall be of the same make as that of LED luminaire and must be EMI/EMC compliant.. The LEDs used shall have CCT option of 4000K having CRI≥80, & SDCM≤5. Luminaire manufacturer must have IN-house NABL accredited lab to conduct LM79, Type test as per IS10322 & "FAT". The the successful bidder must submit the NABL accreditation certificate for Luminaire manufacturer. The LED Luminaire & it's driver both should be BIS registered. The luminaire shall be supplied with adjustable suspension wires. The manufacturer shall submit the following reports before SUpply & Fixing of material for approvals LM79 issued by NABL accrediated lab, LM80 issued by LED manufacturer. DALI 2 BALLAST | Nos. | 1 |  | 350 | 0 | 350
28 | MR | Supply,Installation,Testing and Commissioning of Standalone/Continues rectangal recessed linear LED luminaire made of extruded aluminimum with White/Black Powder Coated finish, With Lenses and UGR reflector, with reflector color Gun-metal/black. UGR<16.The luminaire having Multiple Lumen Output Options Varying from 1200-1500 Lumens/meter to choose from,with system efficacy of ≥100lm/w & system wattage option 16W-44W (±5%). COD Dimenions W 42MM x H 35MM. Optics option of Square 50deg,Round 24deg and wallwasher.W35mm x H45mm profile and fixture size is 9300mm x 7100mm . The life shall be 50K Hrs. at L70B50. Operating temperature of the luminaire shall be 0°C to +45°C and driver shall comply to the minimum electronic paramtere like THD≤ 10%, PF ≥0.9, internal surge protection of 4KV, operating voltage range of 140V - 270V having Class - I protection & serviceability of Class B. The luminaire shall be IP20 & IK02 compliance.The driver shall be of the same make as that of LED luminaire and must be EMI/EMC compliant.. The LEDs used shall have CCT option of 4000K having CRI≥80, & SDCM≤5. Luminaire manufacturer must have IN-house NABL accredited lab to conduct LM79, Type test as per IS10322 & "FAT". The the successful bidder must submit the NABL accreditation certificate for Luminaire manufacturer. The LED Luminaire & it's driver both should be BIS registered. The luminaire shall be supplied with adjustable suspension wires. The manufacturer shall submit the following reports before SUpply & Fixing of material for approvals LM79 issued by NABL accrediated lab, LM80 issued by LED manufacturer. DALI 2 BALLAST | Nos. | 1 |  | 350 | 0 | 350
29 | MR | Supply,Installation,Testing and Commissioning of Continues rectangal recessed linear LED luminaire made of extruded aluminimum with White/Black Powder Coated finish, With Lenses and UGR reflector, with reflector color Gun-metal/black. UGR<16.The luminaire having Multiple Lumen Output Options Varying from 1200-1500 Lumens/meter to choose from,with system efficacy of ≥100lm/w . W35mm x H45mmprofile and fixture size is 4900-5000mm x 7500-7600mm . Optics option of Square 50deg,Round 24deg and wallwasher.The luminaire shall have a width of not more than 55mm(± 2mm), height 64mm (± 2mm) and shall be available in multiple lengths. The life shall be 50K Hrs. at L70B50. Operating temperature of the luminaire shall be 0°C to +45°C and driver shall comply to the minimum electronic paramtere like THD≤ 10%, PF ≥0.9, internal surge protection of 4KV, operating voltage range of 140V - 270V having Class - I protection & serviceability of Class B. The luminaire shall be IP20 & IK02 compliance.The driver shall be of the same make as that of LED luminaire and must be EMI/EMC compliant.. The LEDs used shall have CCT option of 4000K having CRI≥80, & SDCM≤5. Luminaire manufacturer must have IN-house NABL accredited lab to conduct LM79, Type test as per IS10322 & "FAT". The the successful bidder must submit the NABL accreditation certificate for Luminaire manufacturer. The LED Luminaire & it's driver both should be BIS registered. The luminaire shall be supplied with adjustable suspension wires. The manufacturer shall submit the following reports before SUpply & Fixing of material for approvals LM79 issued by NABL accrediated lab, LM80 issued by LED manufacturer. DALI 2 BALLAST | Nos. | 1 |  | 350 | 0 | 350
30 | MR | Supply,Installation,Testing and Commissioning of Continues recessed linear LED luminaire made of extruded aluminimum with White/Black Powder Coated finish, With Lenses and UGR reflector, with reflector color Gun-metal/black. UGR<16. The luminaire having lumens 1200-1500lm/m to ,with system efficacy of ≥100lm/w,with system efficacy of ≥100lm/w. COD Dimenions W 35MM x H 35MM X L 3200-3300mm. Optics option of Square 50deg,Round 24deg and wallwasher.The luminaire shall have a width of not more than 55mm(± 2mm), height 64mm (± 2mm) and shall be available in multiple lengths. The life shall be 50K Hrs. at L70B50. Operating temperature of the luminaire shall be 0°C to +45°C and driver shall comply to the minimum electronic paramtere like THD≤ 10%, PF ≥0.9, internal surge protection of 4KV, operating voltage range of 140V - 270V having Class - I protection & serviceability of Class B. The luminaire shall be IP20 & IK02 compliance.The driver shall be of the same make as that of LED luminaire and must be EMI/EMC compliant.. The LEDs used shall have CCT option of 4000K having CRI≥80, & SDCM≤5. Luminaire manufacturer must have IN-house NABL accredited lab to conduct LM79, Type test as per IS10322 & "FAT". The the successful bidder must submit the NABL accreditation certificate for Luminaire manufacturer. The LED Luminaire & it's driver both should be BIS registered. The luminaire shall be supplied with adjustable suspension wires. The manufacturer shall submit the following reports before SUpply & Fixing of material for approvals LM79 issued by NABL accrediated lab, LM80 issued by LED manufacturer. DALI 2 BALLAST | Nos. | 18 |  | 350 | 0 | 6300
31 | MR | Supply,Installation,Testing and Commissioning of Continues recessed linear LED luminaire made of extruded aluminimum with White/Black Powder Coated finish, With Lenses and UGR reflector, with reflector color Gun-metal/black. UGR<16. The luminaire having lumens 1200-1500lm/meter to ,with system efficacy of ≥100lm/w,with system efficacy of ≥100lm/w. COD Dimenions W 35MM x H 35MM X L 3200-3300MM. Optics option of Square 50deg,Round 24deg and wallwasher.The luminaire shall have a width of not more than 55mm(± 2mm), height 64mm (± 2mm) and shall be available in multiple lengths. The life shall be 50K Hrs. at L70B50. Operating temperature of the luminaire shall be 0°C to +45°C and driver shall comply to the minimum electronic paramtere like THD≤ 10%, PF ≥0.9, internal surge protection of 4KV, operating voltage range of 140V - 270V having Class - I protection & serviceability of Class B. The luminaire shall be IP20 & IK02 compliance.The driver shall be of the same make as that of LED luminaire and must be EMI/EMC compliant.. The LEDs used shall have CCT option of 4000K having CRI≥80, & SDCM≤5. Luminaire manufacturer must have IN-house NABL accredited lab to conduct LM79, Type test as per IS10322 & "FAT". The the successful bidder must submit the NABL accreditation certificate for Luminaire manufacturer. The LED Luminaire & it's driver both should be BIS registered. The luminaire shall be supplied with adjustable suspension wires. The manufacturer shall submit the following reports before SUpply & Fixing of material for approvals LM79 issued by NABL accrediated lab, LM80 issued by LED manufacturer. DALI 2 BALLAST | Nos. | 7 |  | 350 | 0 | 2450
32 | MR | Supply,Installation,Testing and Commissioning of Continues recessed linear LED luminaire made of extruded aluminimum with White/Black Powder Coated finish, With Lenses and UGR reflector, with reflector color Gun-metal/black. UGR<16. The luminaire having lumens 1200-1500lm/meter to ,with system efficacy of ≥100lm/w,with system efficacy of ≥100lm/w. COD Dimenions W 35MM x H 35MM X L 3100-3200MM. Optics option of Square 50deg,Round 24deg and wallwasher.The luminaire shall have a width of not more than 55mm(± 2mm), height 64mm (± 2mm) and shall be available in multiple lengths. The life shall be 50K Hrs. at L70B50. Operating temperature of the luminaire shall be 0°C to +45°C and driver shall comply to the minimum electronic paramtere like THD≤ 10%, PF ≥0.9, internal surge protection of 4KV, operating voltage range of 140V - 270V having Class - I protection & serviceability of Class B. The luminaire shall be IP20 & IK02 compliance.The driver shall be of the same make as that of LED luminaire and must be EMI/EMC compliant.. The LEDs used shall have CCT option of 4000K having CRI≥80, & SDCM≤5. Luminaire manufacturer must have IN-house NABL accredited lab to conduct LM79, Type test as per IS10322 & "FAT". The the successful bidder must submit the NABL accreditation certificate for Luminaire manufacturer. The LED Luminaire & it's driver both should be BIS registered. The luminaire shall be supplied with adjustable suspension wires. The manufacturer shall submit the following reports before SUpply & Fixing of material for approvals LM79 issued by NABL accrediated lab, LM80 issued by LED manufacturer. DALI 2 BALLAST | Nos. | 10 |  | 350 | 0 | 3500
33 | MR | Supply,Installation,Testing and Commissioning of Continues recessed linear LED luminaire made of extruded aluminimum with White/Black Powder Coated finish, With Lenses and UGR reflector, with reflector color Gun-metal/black. UGR<16. The luminaire having lumens 1200-1500lm/m to ,with system efficacy of ≥100lm/w,with system efficacy of ≥100lm/w. COD Dimenions W 35MM x H 35MM X L 3100MM. Optics option of Square 50deg,Round 24deg and wallwasher.The luminaire shall have a width of not more than 55mm(± 2mm), height 64mm (± 2mm) and shall be available in multiple lengths. The life shall be 50K Hrs. at L70B50. Operating temperature of the luminaire shall be 0°C to +45°C and driver shall comply to the minimum electronic paramtere like THD≤ 10%, PF ≥0.9, internal surge protection of 4KV, operating voltage range of 140V - 270V having Class - I protection & serviceability of Class B. The luminaire shall be IP20 & IK02 compliance.The driver shall be of the same make as that of LED luminaire and must be EMI/EMC compliant.. The LEDs used shall have CCT option of 4000K having CRI≥80, & SDCM≤5. Luminaire manufacturer must have IN-house NABL accredited lab to conduct LM79, Type test as per IS10322 & "FAT". The the successful bidder must submit the NABL accreditation certificate for Luminaire manufacturer. The LED Luminaire & it's driver both should be BIS registered. The luminaire shall be supplied with adjustable suspension wires. The manufacturer shall submit the following reports before SUpply & Fixing of material for approvals LM79 issued by NABL accrediated lab, LM80 issued by LED manufacturer. DALI 2 BALLAST | Nos. | 10 |  | 350 | 0 | 3500
34 | MR | Supply,Installation,Testing and Commissioning of Continues recessed linear LED luminaire made of extruded aluminimum with White/Black Powder Coated finish, With Lenses and UGR reflector, with reflector color Gun-metal/black. UGR<16.The luminaire having lumens 1200-1500lm/m to ,with system efficacy of ≥100lm/w ,with system efficacy of ≥100lm/w. COD Dimenions W 35MM x H 35MM X L 2600-2800MM. Optics option of Square 50deg,Round 24deg and wallwasher.The luminaire shall have a width of not more than 55mm(± 2mm), height 64mm (± 2mm) and shall be available in multiple lengths. The life shall be 50K Hrs. at L70B50. Operating temperature of the luminaire shall be 0°C to +45°C and driver shall comply to the minimum electronic paramtere like THD≤ 10%, PF ≥0.9, internal surge protection of 4KV, operating voltage range of 140V - 270V having Class - I protection & serviceability of Class B. The luminaire shall be IP20 & IK02 compliance.The driver shall be of the same make as that of LED luminaire and must be EMI/EMC compliant.. The LEDs used shall have CCT option of 4000K having CRI≥80, & SDCM≤5. Luminaire manufacturer must have IN-house NABL accredited lab to conduct LM79, Type test as per IS10322 & "FAT". The the successful bidder must submit the NABL accreditation certificate for Luminaire manufacturer. The LED Luminaire & it's driver both should be BIS registered. The luminaire shall be supplied with adjustable suspension wires. The manufacturer shall submit the following reports before SUpply & Fixing of material for approvals LM79 issued by NABL accrediated lab, LM80 issued by LED manufacturer. DALI 2 BALLAST | Nos. | 2 |  | 350 | 0 | 700
35 | MR | Supply,Installation,Testing and Commissioning of Continues recessed linear LED luminaire made of extruded aluminimum with White/Black Powder Coated finish, With Lenses and UGR reflector, with reflector color Gun-metal/black. UGR<16.The luminaire having lumens 1200-1500lm/m to ,with system efficacy of ≥100lm/w, with system efficacy of ≥100lm/w. COD Dimenions W 35MM x H 35MM X L 2100-2200MM. Optics option of Square 50deg,Round 24deg and wallwasher.The luminaire shall have a width of not more than 55mm(± 2mm), height 64mm (± 2mm) and shall be available in multiple lengths. The life shall be 50K Hrs. at L70B50. Operating temperature of the luminaire shall be 0°C to +45°C and driver shall comply to the minimum electronic paramtere like THD≤ 10%, PF ≥0.9, internal surge protection of 4KV, operating voltage range of 140V - 270V having Class - I protection & serviceability of Class B. The luminaire shall be IP20 & IK02 compliance.The driver shall be of the same make as that of LED luminaire and must be EMI/EMC compliant.. The LEDs used shall have CCT option of 4000K having CRI≥80, & SDCM≤5. Luminaire manufacturer must have IN-house NABL accredited lab to conduct LM79, Type test as per IS10322 & "FAT". The the successful bidder must submit the NABL accreditation certificate for Luminaire manufacturer. The LED Luminaire & it's driver both should be BIS registered. The luminaire shall be supplied with adjustable suspension wires. The manufacturer shall submit the following reports before SUpply & Fixing of material for approvals LM79 issued by NABL accrediated lab, LM80 issued by LED manufacturer. DALI 2 BALLAST | Nos. | 2 |  | 350 | 0 | 700
36 | MR | Supply,Installation,Testing and Commissioning of Continues recessed linear LED luminaire made of extruded aluminimum with White/Black Powder Coated finish, With Lenses and UGR reflector, with reflector color Gun-metal/black. UGR<16.The luminaire having lumens 1200-1500lm/meter to ,with system efficacy of ≥100lm/w, with system efficacy of ≥100lm/w. COD DimenionsW35mm x H35mm x L1200-1300mm. Optics option of Square 50deg,Round 24deg and wallwasher.The luminaire shall have a width of not more than 55mm(± 2mm), height 64mm (± 2mm) and shall be available in multiple lengths. The life shall be 50K Hrs. at L70B50. Operating temperature of the luminaire shall be 0°C to +45°C and driver shall comply to the minimum electronic paramtere like THD≤ 10%, PF ≥0.9, internal surge protection of 4KV, operating voltage range of 140V - 270V having Class - I protection & serviceability of Class B. The luminaire shall be IP20 & IK02 compliance.The driver shall be of the same make as that of LED luminaire and must be EMI/EMC compliant.. The LEDs used shall have CCT option of 4000K having CRI≥80, & SDCM≤5. Luminaire manufacturer must have IN-house NABL accredited lab to conduct LM79, Type test as per IS10322 & "FAT". The the successful bidder must submit the NABL accreditation certificate for Luminaire manufacturer. The LED Luminaire & it's driver both should be BIS registered. The luminaire shall be supplied with adjustable suspension wires. The manufacturer shall submit the following reports before SUpply & Fixing of material for approvals LM79 issued by NABL accrediated lab, LM80 issued by LED manufacturer. DALI 2 BALLAST | Nos. | 2 |  | 350 | 0 | 700
37 | MR | Supply,Installation,Testing and Commissioning of Continues recessed linear LED luminaire made of extruded aluminimum with White/Black Powder Coated finish, With Lenses and UGR reflector, with reflector color Gun-metal/black. UGR<16. The luminaire having lumens 1200-1500lm/m ,with system efficacy of ≥100lm/w. COD Dimenions W35mm x H35mm x L2100mm. Optics option of Square 50deg,Round 24deg and wallwasher.The luminaire shall have a width of not more than 55mm(± 2mm), height 64mm (± 2mm) and shall be available in multiple lengths. The life shall be 50K Hrs. at L70B50. Operating temperature of the luminaire shall be 0°C to +45°C and driver shall comply to the minimum electronic paramtere like THD≤ 10%, PF ≥0.9, internal surge protection of 4KV, operating voltage range of 140V - 270V having Class - I protection & serviceability of Class B. The luminaire shall be IP20 & IK02 compliance.The driver shall be of the same make as that of LED luminaire and must be EMI/EMC compliant.. The LEDs used shall have CCT option of 4000K having CRI≥80, & SDCM≤5. Luminaire manufacturer must have IN-house NABL accredited lab to conduct LM79, Type test as per IS10322 & "FAT". The the successful bidder must submit the NABL accreditation certificate for Luminaire manufacturer. The LED Luminaire & it's driver both should be BIS registered. The luminaire shall be supplied with adjustable suspension wires. The manufacturer shall submit the following reports before SUpply & Fixing of material for approvals LM79 issued by NABL accrediated lab, LM80 issued by LED manufacturer. DALI 2 BALLAST | Nos. | 54 |  | 350 | 0 | 18900
38 | MR | Supply,Installation,Testing and Commissioning of continuous Suspended slim Linear LED made of extruded Aluminium with white/black powder coaed finish with high efficiency drop down polycarbonate/PS diffuser to have volumetric light distribution and wide angle illumination. The luminaire shall have a aluminium profile of 1000mm x 50mm x 80mm. LED Used shall be SMD type with approx system Lumens 1200-1500/m & efficacy >=150lm/W,Life of fixture : 50000 burning Hrs. @ L70B50 Lumen maintenance, CCT of 4000K (SDCM<=5), CRI Ra ≥80, PF ≥0.95, THD≤10%, an Operating working temp range - 0°C < Ta < 45°C & operating Voltage Range of 140-270 V AC. Minimum Internal Surge Protection 3.5kV. Driver should be DALI 2 Certified & compliant, Luminaire with Ingress & IK protection Rating of of IP20 & IK02.The driver shall be compliant to IEC61347-2-13, IEC62384 & IEC6100-3-2. The driver & Luminaire shall be BIS registered. The driver shall be designed for continuous operation of minimum 12-15Hrs a day. The luminaire driver shall be of the same make/manufacturer as that of LED luminaires. Luminaire manufacturer must have In-house NABL accredited lab in India to conduct LM79, Type test as per IS10322, "FAT" before dispatch as per IS 10322 & IK Test. The successful bidder must submit the NABL accreditation certificate for Luminaire manufacturer. The manufacturer shall submit the following reports before SUpply & Fixing of material for approvals LM79 issued by NABL accredited lab, LM80 issued by LED manufacturer. DALI 2 BALLAST | Nos. | 10 |  | 350 | 0 | 3500
39 | MR | Supply,Installation,Testing and Commissioning of stanalone/continues Recessed slim Linear LED made of extruded Aluminium with white/black powder coaed finish with high efficiency Micro Prismatic Diffuser.The luminaire shall have a 1200mm x 50mm x 80mm. LED Used shall be SMD type with approx system Lumens 2200-3000 (+-10%) & efficacy 115lm/W, UGR<19 Life of fixture : 50000 burning Hrs. @ L70B50 Lumen maintenance, Driver should be DALI2 Certified & compliant, Power factor 0.99%, efficiency of ≥ 91% Output current ripple LF<4%. CCT of Tunable (SDCM<=5), CRI 90, PF ≥0.95, THD≤ 10%, an Operating working temp range - 0°C < Ta < 45°C & operating Voltage Range of 140-270 V AC having Class - I protection & serviceability of Class B. Minimum Internal Surge Protection 3.5kV. The manufacturer shall submit the following reports before SUpply & Fixing of material for approvals LM79 issued by NABL accredited lab, LM80 issued by LED manufacturer. DALI 2 BALLAST | Nos. | 40 |  | 350 | 0 | 14000
40 | MR | Supply,Installation,Testing and Commissioning of continues Recessed slim Linear LED made of extruded Aluminium with white/black powder coaed finish with high efficiency Micro Prismatic Diffuser.The luminaire shall have a 1200mm x 50mm x 80mm. LED Used shall be SMD type with approx system Lumens 2200-3000 (+-10%) & efficacy 115lm/W, UGR<19 Life of fixture : 50000 burning Hrs. @ L70B50 Lumen maintenance, Driver should be DALI2 Certified & compliant, Power factor 0.99%, efficiency of ≥ 91% Output current ripple LF<4%. CCT of Tunable (SDCM<=5), CRI 90, PF ≥0.95, THD≤ 10%, an Operating working temp range - 0°C < Ta < 45°C & operating Voltage Range of 140-270 V AC having Class - I protection & serviceability of Class B. Minimum Internal Surge Protection 3.5kV. The manufacturer shall submit the following reports before SUpply & Fixing of material for approvals LM79 issued by NABL accredited lab, LM80 issued by LED manufacturer. DALI 2 BALLAST | Nos. | 85 |  | 350 | 0 | 29750
41 | MR | Supply,Installation,Testing and Commissioning of continuous Suspended slim Linear LED made of extruded Aluminium with white/black powder coaed finish with high efficiency drop down polycarbonate/PS diffuser to have volumetric light distribution and wide angle illumination. The luminaire shall have a 1400m x 50mm x 80mm. LED Used shall be SMD type with approx system Lumens 3500-4000 & efficacy <=150lm/W,Life of fixture : 50000 burning Hrs. @ L70B50 Lumen maintenance, CCT of 4000K (SDCM<=5), CRI Ra ≥80, PF ≥0.95, THD≤10%, an Operating working temp range - 0°C < Ta < 45°C & operating Voltage Range of 140-270 V AC. Minimum Internal Surge Protection 3.5kV. Driver should be DALI 2 Certified & compliant, Luminaire with Ingress & IK protection Rating of of IP20 & IK02.The driver shall be compliant to IEC61347-2-13, IEC62384 & IEC6100-3-2. The driver & Luminaire shall be BIS registered. The driver shall be designed for continuous operation of minimum 12-15Hrs a day. The luminaire driver shall be of the same make/manufacturer as that of LED luminaires. Luminaire manufacturer must have In- house NABL accredited lab in India to conduct LM79, Type test as per IS10322, "FAT" before dispatch as per IS 10322 & IK Test. The successful bidder must submit the NABL accreditation certificate for Luminaire manufacturer. The manufacturer shall submit the following reports before SUpply & Fixing of material for approvals LM79 issued by NABL accredited lab, LM80 issued by LED manufacturer. DALI 2 BALLAST | Nos. | 623 |  | 350 | 0 | 218050
42 | MR | Supply,Installation,Testing and Commissioning of stanalone/continuous Suspended slim Linear LED made of extruded Aluminium with white/black powder coaed finish with high efficiency drop down polycarbonate PS diffuser to have volumetric light distribution and wide angle illumination. The luminaire shall have a width of 1500mmx50mmx80mm. LED Used shall be SMD type with approx system Lumens 4000-5000 & efficacy <=150lm/W,Life of fixture : 50000 burning Hrs. @ L70B50 Lumen maintenance, CCT of 4000K (SDCM<=5), CRI Ra ≥80, PF ≥0.95, THD≤10%, an Operating working temp range - 0°C < Ta < 45°C & operating Voltage Range of 140-270 V AC. Minimum Internal Surge Protection 3.5kV. Driver should be DALI 2 Certified & compliant, Luminaire with Ingress & IK protection Rating of of IP20 & IK02.The driver shall be compliant to IEC61347-2-13, IEC62384 & IEC6100-3-2. The driver & Luminaire shall be BIS registered. The driver shall be designed for continuous operation of minimum 12-15Hrs a day. The luminaire driver shall be of the same make/manufacturer as that of LED luminaires. Luminaire manufacturer must have In-house NABL accredited lab in India to conduct LM79, Type test as per IS10322, "FAT" before dispatch as per IS 10322 & IK Test. The successful bidder must submit the NABL accreditation certificate for Luminaire manufacturer. The manufacturer shall submit the following reports before SUpply & Fixing of material for approvals LM79 issued by NABL accredited lab, LM80 issued by LED manufacturer. DALI 2 BALLAST | Nos. | 322 |  | 350 | 0 | 112700
43 | MR | Supply,Installation,Testing and Commissioning of continuous Suspended 5ft slim Linear LED made of extruded Aluminium with white/black powder coaed finish with high efficiency drop down polycarbonate/PS diffuser to have volumetric light distribution and wide angle illumination. The luminaire shall have an extruded aluminium profile of 1600mm x 50mm x 80mm. LED Used shall be SMD type with approx system Lumens 4000-5000 & efficacy <=150lm/W,Life of fixture : 50000 burning Hrs. @ L70B50 Lumen maintenance, CCT of 4000K (SDCM<=5), CRI Ra ≥80, PF ≥0.95, THD≤10%, an Operating working temp range - 0°C < Ta < 45°C & operating Voltage Range of 140-270 V AC. Minimum Internal Surge Protection 3.5kV. Driver should be DALI 2 Certified & compliant, Luminaire with Ingress & IK protection Rating of of IP20 & IK02.The driver shall be compliant to IEC61347-2-13, IEC62384 & IEC6100-3-2. The driver & Luminaire shall be BIS registered. The driver shall be designed for continuous operation of minimum 12-15Hrs a day. The luminaire driver shall be of the same make/manufacturer as that of LED luminaires. Luminaire manufacturer must have In-house NABL accredited lab in India to conduct LM79, Type test as per IS10322, "FAT" before dispatch as per IS 10322 & IK Test. The successful bidder must submit the NABL accreditation certificate for Luminaire manufacturer. The manufacturer shall submit the following reports before SUpply & Fixing of material for approvals LM79 issued by NABL accredited lab, LM80 issued by LED manufacturer. DALI 2 BALLAST | Nos. | 62 |  | 350 | 0 | 21700
44 | MR | Supply,Installation,Testing and Commissioning of continuous Suspended 6ft slim Linear LED made of extruded Aluminium with white/black powder coaed finish with high efficiency drop down polycarbonate/PS diffuser to have volumetric light distribution and wide angle illumination. The luminaire shall have a 2000mmx50mmx80mm. LED Used shall be SMD type with approx system Lumens 4000-5000 & efficacy <=150lm/W,Life of fixture : 50000 burning Hrs. @ L70B50 Lumen maintenance, CCT of 4000K (SDCM<=5), CRI Ra ≥80, PF ≥0.95, THD≤10%, an Operating working temp range - 0°C < Ta < 45°C & operating Voltage Range of 140-270 V AC. Minimum Internal Surge Protection 3.5kV. Driver should be DALI 2 Certified & compliant, Luminaire with Ingress & IK protection Rating of of IP20 & IK02.The driver shall be compliant to IEC61347-2-13, IEC62384 & IEC6100-3-2. The driver & Luminaire shall be BIS registered. The driver shall be designed for continuous operation of minimum 12-15Hrs a day. The luminaire driver shall be of the same make/manufacturer as that of LED luminaires. Luminaire manufacturer must have In- house NABL accredited lab in India to conduct LM79, Type test as per IS10322, "FAT" before dispatch as per IS 10322 & IK Test. The successful bidder must submit the NABL accreditation certificate for Luminaire manufacturer. The manufacturer shall submit the following reports before SUpply & Fixing of material for approvals LM79 issued by NABL accredited lab, LM80 issued by LED manufacturer. DALI 2 BALLAST | Nos. | 48 |  | 350 | 0 | 16800
45 | MR | Supply,Installation,Testing and Commissioning of stanalone/continuous Suspended slim Linear LED made of extruded Aluminium with white/black powder coaed finish with high efficiency drop down polycarbonate/PS diffuser to have volumetric light distribution and wide angle illumination. The luminaire shall have a 2400mm x 50mm x 80mm. LED Used shall be SMD type with approx system Lumens 5000-6000 & efficacy <=150lm/W,Life of fixture : 50000 burning Hrs. @ L70B50 Lumen maintenance, CCT of 4000K (SDCM<=5), CRI Ra ≥80, PF ≥0.95, THD≤10%, an Operating working temp range - 0°C < Ta < 45°C & operating Voltage Range of 140-270 V AC. Minimum Internal Surge Protection 3.5kV. Driver should be DALI 2 Certified & compliant, Luminaire with Ingress & IK protection Rating of of IP20 & IK02.The driver shall be compliant to IEC61347-2-13, IEC62384 & IEC6100-3-2. The driver & Luminaire shall be BIS registered. The driver shall be designed for continuous operation of minimum 12-15Hrs a day. The luminaire driver shall be of the same make/manufacturer as that of LED luminaires. Luminaire manufacturer must have In- house NABL accredited lab in India to conduct LM79, Type test as per IS10322, "FAT" before dispatch as per IS 10322 & IK Test. The successful bidder must submit the NABL accreditation certificate for Luminaire manufacturer. The manufacturer shall submit the following reports before SUpply & Fixing of material for approvals LM79 issued by NABL accredited lab, LM80 issued by LED manufacturer. DALI 2 BALLAST | Nos. | 2 |  | 350 | 0 | 700
46 | MR | Supply,Installation,Testing and Commissioning of rectangal 1200mmx2400mm an extruded aluminium profile of 50mm x 80mm Continuos linear with deep recessed Diffuser with down distribution, made up of extruded Al housing with tapered external reflector options downward of Rose Gold with Al silver housing/High gloss gold with Matt black housing/High gloss Silver with matt black housing, and with customisable finish to enhance/match interiors. The luminaire shall be with minimum system lumen of 5000-6000lm and with system efficacy of <=120lm/W. The life of fixture shall be 50000 burning hours @L70B50 lumen maintenance, CCT 4000K, SDCM<5, CRI≥90, PF≥0.95,THD≤10%, an Operating working temp range : 0°C < Ta < 45°C & operating Voltage Range of 140-270 V AC. Minimum Internal Surge Protection 3.5KV. , Driver should be DALI 2 Certified & compliant, Power factor 0.99%, efficiency of ≥ 91% Output current ripple LF<4%, The fixture design should comply to IEC61000-3-2 ed.3.2, 2009 for Harmonics, IEC61347 -2 -13, 2006 in Conjunction with IEC61347-1 ed.2.0, 2007 for Electrical Safety, IEC62384 ed.1.1, 2011 for performance and IEC61547 ed.2.0, 2009. The luminaire shall be Class B Serviceability.The luminaire driver shall be of the same make/manufacturer as that of LED luminaires. Manufacturer shall have inhouse lab approved by NABL or ministry of science of govt of India. LM 79 and LM80 reports need to be submitted from a NABL/UL accredited lab to verify above parameters. Both the fixture and Driver should have separate BIS approval DALI 2 BALLAST | Nos. | 14 |  | 350 | 0 | 4900
47 | MR | Supply,Installation,Testing and Commissioning of rectangal 1200mmx3600-3700mm, an extruded aluminium profile 50mm x 80mm formed standalone/Continuos linear with deep recessed Diffuser with down distribution, made up of extruded Al housing with tapered external reflector options downward of Rose Gold with Al silver housing/High gloss gold with Matt black housing/High gloss Silver with matt black housing, and with customisable finish to enhance/match interiors. The luminaire shall be system efficacy of >=120lm/W. The life of fixture shall be 50000 burning hours @L70B50 lumen maintenance, CCT 4000K, SDCM<5, CRI≥90, PF≥0.95,THD≤10%, an Operating working temp range : 0°C < Ta < 45°C & operating Voltage Range of 140-270 V AC. Minimum Internal Surge Protection 3.5KV. , Driver should be DALI 2 Certified & compliant, Power factor 0.99%, efficiency of ≥ 91% Output current ripple LF<4%, The fixture design should comply to IEC61000-3-2 ed.3.2, 2009 for Harmonics, IEC61347 -2 -13, 2006 in Conjunction with IEC61347-1 ed.2.0, 2007 for Electrical Safety, IEC62384 ed.1.1, 2011 for performance and IEC61547 ed.2.0, 2009. The luminaire shall be Class B Serviceability.The luminaire driver shall be of the same make/manufacturer as that of LED luminaires. Manufacturer shall have inhouse lab approved by NABL or ministry of science of govt of India. LM 79 and LM80 reports need to be submitted from a NABL/UL accredited lab to verify above parameters. Both the fixture and Driver should have separate BIS approval DALI 2 BALLAST | Nos. | 1 |  | 350 | 0 | 350
48 | MR | Supply,Installation,Testing and Commissioning of ractangle extruded aluminium profile of 50mm × 80mm and the fixture size is 5820mm X 1400mm, rectangular shapeContinuos linear with deep recessed Diffuser with down distribution, made up of extruded Al housing with tapered external reflector options downward of Rose Gold with Al silver housing/High gloss gold with Matt black housing/High gloss Silver with matt black housing, and with customisable finish to enhance/match interiors. The luminaire efficacy of >=120lm/W. The life of fixture shall be 50000 burning hours @L70B50 lumen maintenance, CCT 4000K, SDCM<5, CRI≥90, PF≥0.95,THD≤10%, an Operating working temp range : 0°C < Ta < 45°C & operating Voltage Range of 140-270 V AC. Minimum Internal Surge Protection 3.5KV. , Driver should be DALI 2 Certified & compliant, Power factor 0.99%, efficiency of ≥ 91% Output current ripple LF<4%, The fixture design should comply to IEC61000-3-2 ed.3.2, 2009 for Harmonics, IEC61347 -2 -13, 2006 in Conjunction with IEC61347- 1 ed.2.0, 2007 for Electrical Safety, IEC62384 ed.1.1, 2011 for performance and IEC61547 ed.2.0, 2009. The luminaire shall be Class B Serviceability.The luminaire driver shall be of the same make/manufacturer as that of LED luminaires. Manufacturer shall have inhouse lab approved by NABL or ministry of science of govt of India. LM 79 and LM80 reports need to be submitted from a NABL/UL accredited lab to verify above parameters. Both the fixture and Driver should have separate BIS approval DALI 2 BALLAST | Nos. | 2 |  | 350 | 0 | 700
49 | MR | Supply,Installation,Testing and Commissioning of rectangal 1200mmx5980mm formed standalone/Continuos linear with deep recessed Diffuser with down distribution, made up of extruded Al housing with tapered external reflector options downward of Rose Gold with Al silver housing/High gloss gold with Matt black housing/High gloss Silver with matt black housing, and with customisable finish to enhance/match interiors. The luminaire shall be of 65mm widthX100mm height, with minimum system lumen of 2000-2500lm/meter and with system efficacy of >=120lm/W. The life of fixture shall be 50000 burning hours @L70B50 lumen maintenance, CCT 4000K, SDCM<5, CRI≥90, PF≥0.95,THD≤10%, an Operating working temp range : 0°C < Ta < 45°C & operating Voltage Range of 140-270 V AC. Minimum Internal Surge Protection 3.5KV, Driver should be DALI 2 Certified & compliant, Power factor 0.99%, efficiency of ≥ 91% Output current ripple LF<4%, The fixture design should comply to IEC61000-3-2 ed.3.2, 2009 for Harmonics, IEC61347 -2 -13, 2006 in Conjunction with IEC61347-1 ed.2.0, 2007 for Electrical Safety, IEC62384 ed.1.1, 2011 for performance and IEC61547 ed.2.0, 2009. The luminaire shall be Class B Serviceability.The luminaire driver shall be of the same make/manufacturer as that of LED luminaires. Manufacturer shall have inhouse lab approved by NABL or ministry of science of govt of India. LM 79 and LM80 reports need to be submitted from a NABL/UL accredited lab to verify above parameters. Both the fixture and Driver should have separate BIS approval DALI 2 BALLAST | Nos. | 12 |  | 350 | 0 | 4200
50 | MR | Supply,Installation,Testing and Commissioning of rectangal Fixture size 900mmx2600-2700mm, profile of 50mm x 80mm formed standalone/Continuos linear with deep recessed Diffuser with down distribution, made up of extruded Al housing with tapered external reflector options downward of Rose Gold with Al silver housing/High gloss gold with Matt black housing/High gloss Silver with matt black housing, and with customisable finish to enhance/match interiors. The luminaire shall minimum system lumen of 2000-2500lm/m and with system efficacy of >=120lm/W. The life of fixture shall be 50000 burning hours @L70B50 lumen maintenance, CCT 4000K, SDCM<5, CRI≥90, PF≥0.95,THD≤10%, an Operating working temp range : 0°C < Ta < 45°C & operating Voltage Range of 140-270 V AC. Minimum Internal Surge Protection 3.5KV, Driver should be DALI 2 Certified & compliant, Power factor 0.99%, efficiency of ≥ 91% Output current ripple LF<4%, The fixture design should comply to IEC61000-3-2 ed.3.2, 2009 for Harmonics, IEC61347 -2 -13, 2006 in Conjunction with IEC61347-1 ed.2.0, 2007 for Electrical Safety, IEC62384 ed.1.1, 2011 for performance and IEC61547 ed.2.0, 2009. The luminaire shall be Class B Serviceability.The luminaire driver shall be of the same make/manufacturer as that of LED luminaires. Manufacturer shall have inhouse lab approved by NABL or ministry of science of govt of India. LM 79 and LM80 reports need to be submitted from a NABL/UL accredited lab to verify above parameters. Both the fixture and Driver should have separate BIS approval DALI 2 BALLAST | Nos. | 1 |  | 350 | 0 | 350
51 | MR | Supply,Installation,Testing and Commissioning of rectangal fixture size is 3100-3200mmx2100- 2200mm, profile of 50mm x 80mm formed standalone/Continuos linear with deep recessed Diffuser with down distribution, made up of extruded Al housing with tapered external reflector options downward of Rose Gold with Al silver housing/High gloss gold with Matt black housing/High gloss Silver with matt black housing, and with customisable finish to enhance/match interiors. The luminaire shall be minimum system lumen of 2000-2500lm/m and with system efficacy of >=120lm/W. The life of fixture shall be 50000 burning hours @L70B50 lumen maintenance, CCT 4000K, SDCM<5, CRI≥90, PF≥0.95,THD≤10%, an Operating working temp range : 0°C < Ta < 45°C & operating Voltage Range of 140-270 V AC. Minimum Internal Surge Protection 3.5KV, Driver should be DALI 2 Certified & compliant, Power factor 0.99%, efficiency of ≥ 91% Output current ripple LF<4%, The fixture design should comply to IEC61000-3-2 ed.3.2, 2009 for Harmonics, IEC61347 -2 -13, 2006 in Conjunction with IEC61347-1 ed.2.0, 2007 for Electrical Safety, IEC62384 ed.1.1, 2011 for performance and IEC61547 ed.2.0, 2009. The luminaire shall be Class B Serviceability.The luminaire driver shall be of the same make/manufacturer as that of LED luminaires. Manufacturer shall have inhouse lab approved by NABL or ministry of science of govt of India. LM 79 and LM80 reports need to be submitted from a NABL/UL accredited lab to verify above parameters. Both the fixture and Driver should have separate BIS approval DALI 2 BALLAST | Nos. | 1 |  | 350 | 0 | 350
52 | MR | Supply,Installation,Testing and Commissioning of rectangal 2700-2800mmx1300-1400mm, profile 50mm x 80mm formed standalone/Continuos linear with deep recessed Diffuser with down distribution, made up of extruded Al housing with tapered external reflector options downward of Rose Gold with Al silver housing/High gloss gold with Matt black housing/High gloss Silver with matt black housing, and with customisable finish to enhance/match interiors. The luminaire shall be with minimum system lumen of 2000-2500lm/m and with system efficacy of >=120lm/W. The life of fixture shall be 50000 burning hours @L70B50 lumen maintenance, CCT 4000K, SDCM<5, CRI≥90, PF≥0.95,THD≤10%, an Operating working temp range : 0°C < Ta < 45°C & operating Voltage Range of 140-270 V AC. Minimum Internal Surge Protection 3.5KV, Driver should be DALI 2 Certified & compliant, Power factor 0.99%, efficiency of ≥ 91% Output current ripple LF<4%, The fixture design should comply to IEC61000-3-2 ed.3.2, 2009 for Harmonics, IEC61347 -2 -13, 2006 in Conjunction with IEC61347-1 ed.2.0, 2007 for Electrical Safety, IEC62384 ed.1.1, 2011 for performance and IEC61547 ed.2.0, 2009. The luminaire shall be Class B Serviceability.The luminaire driver shall be of the same make/manufacturer as that of LED luminaires. Manufacturer shall have inhouse lab approved by NABL or ministry of science of govt of India. LM 79 and LM80 reports need to be submitted from a NABL/UL accredited lab to verify above parameters. Both the fixture and Driver should have separate BIS approval DALI 2 BALLAST | Nos. | 1 |  | 350 | 0 | 350
53 | MR | Supply,Installation,Testing and Commissioning of rectangal fixture size is 900mm x 1600- 1700mm, profile of 50mm x 80mm formed standalone/Continuos linear with deep recessed Diffuser with down distribution, made up of extruded Al housing with tapered external reflector options downward of Rose Gold with Al silver housing/High gloss gold with Matt black housing/High gloss Silver with matt black housing, and with customisable finish to enhance/match interiors. The luminaire shall be minimum system lumen of 2000-2500lm/m and with system efficacy of >=120lm/W. The life of fixture shall be 50000 burning hours @L70B50 lumen maintenance, CCT 4000K, SDCM<5, CRI≥90, PF≥0.95,THD≤10%, an Operating working temp range : 0°C < Ta < 45°C & operating Voltage Range of 140-270 V AC. Minimum Internal Surge Protection 3.5KV, Driver should be DALI 2 Certified & compliant, Power factor 0.99%, efficiency of ≥ 91% Output current ripple LF<4%, The fixture design should comply to IEC61000-3-2 ed.3.2, 2009 for Harmonics, IEC61347 -2 -13, 2006 in Conjunction with IEC61347-1 ed.2.0, 2007 for Electrical Safety, IEC62384 ed.1.1, 2011 for performance and IEC61547 ed.2.0, 2009. The luminaire shall be Class B Serviceability.The luminaire driver shall be of the same make/manufacturer as that of LED luminaires. Manufacturer shall have inhouse lab approved by NABL or ministry of science of govt of India. LM 79 and LM80 reports need to be submitted from a NABL/UL accredited lab to verify above parameters. Both the fixture and Driver should have separate BIS approval DALI 2 BALLAST | Nos. | 6 |  | 350 | 0 | 2100
54 | MR | Supply,Installation,Testing and Commissioning of rectangal fixture size is 900-1000mmx900- 1000mm formed standalone/Continuos linear with deep recessed Diffuser with down distribution, made up of extruded Al housing with tapered external reflector options downward of Rose Gold with Al silver housing/High gloss gold with Matt black housing/High gloss Silver with matt black housing, and with customisable finish to enhance/match interiors. The luminaire shall be minimum system lumen of 2000-2500lm/m and with system efficacy of <=120lm/W. The life of fixture shall be 50000 burning hours @L70B50 lumen maintenance, CCT 4000K, SDCM<5, CRI≥90, PF≥0.95,THD≤10%, an Operating working temp range : 0°C < Ta < 45°C & operating Voltage Range of 140-270 V AC. Minimum Internal Surge Protection 3.5KV, Driver should be DALI 2 Certified & compliant, Power factor 0.99%, efficiency of ≥ 91% Output current ripple LF<4%, The fixture design should comply to IEC61000-3-2 ed.3.2, 2009 for Harmonics, IEC61347 -2 -13, 2006 in Conjunction with IEC61347-1 ed.2.0, 2007 for Electrical Safety, IEC62384 ed.1.1, 2011 for performance and IEC61547 ed.2.0, 2009. The luminaire shall be Class B Serviceability.The luminaire driver shall be of the same make/manufacturer as that of LED luminaires. Manufacturer shall have inhouse lab approved by NABL or ministry of science of govt of India. LM 79 and LM80 reports need to be submitted from a NABL/UL accredited lab to verify above parameters. Both the fixture and Driver should have separate BIS approval DALI 2 BALLAST | Nos. | 6 |  | 350 | 0 | 2100
55 | MR | Supply,Installation,Testing and Commissioning of Recessed mounted cleanroom 2x2 LED bottom opening ,made of CRCA housing with acrylic cover that ensures IK07 protectionr. LED Used shall be SMD type and fixture should have minimum efficacy at System level >=100 lumens/watt with Minimum system Lumens 3600-4200lm , Life of fixture : 50000 burning Hrs. @ L70B50 Lumen maintenance, CCT of 4000K (SDCM<=5), CRI Ra >=80, THD<10%, PF >0.95, an operating Voltage Range of 140 - 240 VAC.Minimum Internal Surge Protection 4.0KV, IP65 & IK04 protection, Operating temperature of the luminaire shall be -10°C to +45°C Manufacturer shall have inhouse lab approved by NABL or ministry of science of govt of India. LM 79 and LM80 reports need to be submitted from a NABL/UL accredited lab to verify above parameters. Both the fixture and Driver should have separate BIS approval. | Nos. | 42 |  | 350 | 0 | 14700
|  | SUPPLY, INSTALLATION, TESTING AND COMMISSIONING FOLLOWING DECORATIVE LIGHTS |  |  |  |  | 0 | 0
D1 | MR | LED Decorative Circular Pendant Light IP20, 3000K, Dali Dimmable. CRI>90, Lifetime > 50000 hrs. Size : 2 x 900mm Dia + 1 x 600mm As per design/drawing and Direction/ Selection of engineer in charge | Set | 23 |  | 350 | 0 | 8050
D2 | MR | LED Decorative Circular Pendant Light IP20, 3000K, Dali Dimmable. CRI>90, Lifetime > 50000 hrs. Size : 450mm Dia As per design/drawing and Direction/ Selection of engineer in charge | Set | 24 |  | 350 | 0 | 8400
D3 | MR | LED Decorative Circular Pendant Light IP20, 3000K, Dali Dimmable. CRI>90, Lifetime > 50000 hrs. Size : 450mm Dia As per design/drawing and Direction/ Selection of engineer in charge | Set | 62 |  | 350 | 0 | 21700
D4 | MR | LED Decorative Circular Pendant Ring Light IP20, 3000K, Dali Dimmable. CRI>90, Lifetime > 50000 hrs. Size : 400mm Dia As per design/drawing and Direction/ Selection of engineer in charge | Set | 2 |  | 350 | 0 | 700
D5 | MR | LED Decorative Disc hanging Light IP20, 3000K, Dali Dimmable. CRI>90, Lifetime > 50000 hrs. Size : 600mm Dia As per design/drawing and Direction/ Selection of engineer in charge | Set | 13 |  | 350 | 0 | 4550
D5a | MR | LED Decorative Ring hanging Light IP20, 3000K, Dali Dimmable. CRI>90, Lifetime > 50000 hrs. Size : 600mm Dia As per design/drawing and Direction/ Selection of engineer in charge | Set | 76 |  | 350 | 0 | 26600
D6 | MR | LED Decorative Disc hanging Light IP20, 3000K, Dali Dimmable. CRI>90, Lifetime > 50000 hrs. Size : 600mm Dia + 400mm Dia As per design/drawing and Direction/ Selection of engineer in charge | Set | 36 |  | 350 | 0 | 12600
D7 | MR | Supply of stretch ceiling fabric system, designed for interior architectural applications, complete with aluminium perimeter profiles, fixing accessories, and finish treatment as required. The fabric shall be made of high-quality PVC / polyester composite or equivalent material, having thickness not less than 0.2 mm, weight 180–250 g/m², with matte, satin, or translucent finish as specified. The stretch membrane shall be non-toxic, fire-retardant (minimum Class B-s1,d0 as per EN 13501 1 or Class 1 as per BS/ASTM equivalent), anti-static, and resistant to moisture, bacteria, and UV radiation. The system shall be capable of spanning large areas without visible joints (up to 50 m² per sheet) and allow integration of lighting, diffusers, sprinklers, and access hatches. Installation shall be by means of harpoon or clip system, with thermal stretching at ~40–50 °C for uniform tension, ensuring a seamless and wrinkle-free appearance. Mechanical performance shall permit elongation up to 10% without damage, tensile strength ≥ 150 N/5 cm, and tear resistance ≥ 20 N. The stretch ceiling fabric shall be washable, maintain colour stability over its service life, and be easily demountable and re-installable for maintenance. Accessories shall include certified aluminium profile systems (wall, ceiling, or concealed), fixing brackets, and corner pieces, compatible with gypsum board, concrete, or wooden substrates. 10W/sqft, 4000K P.F>0.95.DALI BALLAST. | Sqft. | 2650 |  | 350 | 0 | 927500
D8 | MR | LED Decorative Four Petal pendant light IP20, 3000K, Dali Dimmable. CRI>90, Lifetime > 50000 hrs. Size : 600mm length of each petal As per design/drawing and Direction/ Selection of engineer in charge | Set | 24 |  | 350 | 0 | 8400
D9 | MR | LED Decorative three globe shaped pendant light IP20, 3000K, Dali Dimmable. CRI>90, Lifetime > 50000 hrs. Size : 250mm Dia of globe As per design/drawing and Direction/ Selection of engineer in charge | Set | 1 |  | 350 | 0 | 350
D10 | MR | LED Decorative four globe shaped pendant light IP20, 3000K, Dali Dimmable. CRI>90, Lifetime > 50000 hrs. Size : 150mm Dia of globe As per design/drawing and Direction/ Selection of engineer in charge | Set | 1 |  | 350 | 0 | 350
D11 | MR | LED Decorative circular pendant light IP20, 3000K, Dali Dimmable. CRI>90, Lifetime > 50000 hrs. Size : 1200mm Dia + 600mm Dia As per design/drawing and Direction/ Selection of engineer in charge | Set | 1 |  | 350 | 0 | 350
D13 | MR | LED Decorative circular pendant light IP20, 3000K, Dali Dimmable. CRI>90, Lifetime > 50000 hrs. Size : 1200mm Dia + 600mm Dia As per design/drawing and Direction/ Selection of engineer in charge | Set | 2 |  | 350 | 0 | 700
D14 | MR | LED Decorative wave patteren pendant light IP20, 3000K, Dali Dimmable. CRI>90, Lifetime > 50000 hrs. Length: 1500mm As per design/drawing and Direction/ Selection of engineer in charge | Set | 1 |  | 350 | 0 | 350
D15 | MR | LED Decorative 10 globes (5x2) shaped pendant light IP20, 3000K, Dali Dimmable. CRI>90, Lifetime > 50000 hrs. Size : 150mm Dia of globe As per design/drawing and Direction/ Selection of engineer in charge | Set | 1 |  | 350 | 0 | 350
D16 | MR | LED Decorative circular metal pendant light IP20, 3000K, Dali Dimmable. CRI>90, Lifetime > 50000 hrs. Size : 400mm Dia As per design/drawing and Direction/ Selection of engineer in charge | Set | 4 |  | 350 | 0 | 1400
D17 | MR | LED Decorative acoustic pendant light IP20, 3000K, Dali Dimmable. CRI>90, Lifetime > 50000 hrs. Size : tbc As per design/drawing and Direction/ Selection of engineer in charge |  | 2 |  | 350 | 0 | 700
D18 | MR | LED Decorative acoustic pendant light IP20, 3000K, Dali Dimmable. CRI>90, Lifetime > 50000 hrs. Size : tbc As per design/drawing and Direction/ Selection of engineer in charge |  | 16 |  | 350 | 0 | 5600
D19 | MR | LED Decorative 6 globes (3x2) shaped pendant light IP20, 3000K, Dali Dimmable. CRI>90, Lifetime > 50000 hrs. Size : 150mm Dia of globe As per design/drawing and Direction/ Selection of engineer in charge | Set | 4 |  | 350 | 0 | 1400
D20 | MR | LED Decorative acoustic pendant light IP20, 3000K, Dali Dimmable. CRI>90, Lifetime > 50000 hrs. Size : 900mm Dia of globe As per design/drawing and Direction/ Selection of engineer in charge | Set | 8 |  | 350 | 0 | 2800
D22 | MR | LED Decorative surface Disc Light IP20, 3000K, Dali Dimmable. CRI>90, Lifetime > 50000 hrs. Size : 500mm Dia As per design/drawing and Direction/ Selection of engineer in charge | Set | 30 |  | 350 | 0 | 10500
D23 | MR | SUpply & Fixing of Nature connect LED fixtures with high light levels up to 4500 lm for sky and sun; 10800 lm for daylight,high melanopics level of 700 MEDI at workdesk height during the early afternoon at a ceiling height of approximately 2.80 m, UGR<19. The housing shall be CRCA. The luminaire should comply with LEED & WELL standards. CCT: 2700 K to blue for the sky and sun. 2700 K to 6500 K for the Daylight, CRI>90, Option of connectivity thorugh Interacat & Dynlaite. Fixture should have combination of blue hue of sky, change in intensity of sky and daylight rhythm for general illumination in one solution. In addition to the mini island with the skylight and the daylight panel, the system is combined with NatureConnect link. This is the device that connects the NatureConnect luminaires to commonly used control systems like Interact. It allows these control systems to send simple commands in order to select a NatureConnect scene or change the brightness, while NatureConnect link takes care of executing the complex light recipes to the luminaires. In addition to NatureConnect luminaires based on DALI and DMX, it also supports DALI DT8 tunable white luminaires. DALI TUNNABLE BALLAST |  | 16 |  | 350 | 0 | 5600
D24 | MR | LED Decorative Balloon light IP20, 3000K, Dali Dimmable. CRI>90, Lifetime > 50000 hrs. Size : 400mm Dia + 600mm Dia As per design/drawing and Direction/ Selection of engineer in charge | Set | 2 |  | 350 | 0 | 700
D25 | MR | LED Decorative metal pendant light IP20, 3000K, Dali Dimmable. CRI>90, Lifetime > 50000 hrs. Size : 400mm Dia As per design/drawing and Direction/ Selection of engineer in charge | Set | 60 |  | 350 | 0 | 21000
D26 | MR | LED Decorative suspended acoustic circular pendant light IP20, 3000K, Dali Dimmable. CRI>90, Lifetime > 50000 hrs. Size : 600mm Dia As per design/drawing and Direction/ Selection of engineer in charge | Set | 18 |  | 350 | 0 | 6300
D27 | MR | LED Decorative suspended wooden pendant light IP20, 3000K, Dali Dimmable. CRI>90, Lifetime > 50000 hrs. Size : 300mm Dia As per design/drawing and Direction/ Selection of engineer in charge | Set | 26 |  | 350 | 0 | 9100
D28 | MR | LED Decorative cloud shape light IP20, 3000K, Dali Dimmable. CRI>90, Lifetime > 50000 hrs. Size : tbc As per design/drawing and Direction/ Selection of engineer in charge | Set | 1 |  | 350 | 0 | 350
D29 | MR | LED Decorative square ring light IP20, 3000K, Dali Dimmable. CRI>90, Lifetime > 50000 hrs. Size : 1200mmx1200mm + 600mmx600mm As per design/drawing and Direction/ Selection of engineer in charge | Set | 5 |  | 350 | 0 | 1750
D30 | MR | LED Decorative two globe shaped pendant light IP20, 3000K, Dali Dimmable. CRI>90, Lifetime > 50000 hrs. Size : 250mm Dia of globe As per design/drawing and Direction/ Selection of engineer in charge | Set | 1 |  | 350 | 0 | 350
D31 | MR | LED Decorative ring light IP20, 3000K, Dali Dimmable. CRI>90, Lifetime > 50000 hrs. Size : 2 x 900mm Dia + 1 x 600mm Dia As per design/drawing and Direction/ Selection of engineer in charge | Set | 2 |  | 350 | 0 | 700
D32 | MR | LED Decorative suspended acoustic circular pendant light IP20, 3000K, Dali Dimmable. CRI>90, Lifetime > 50000 hrs. Size : 600mm Dia As per design/drawing and Direction/ Selection of engineer in charge | Set | 10 |  | 350 | 0 | 3500
|  | TOTAL CARRIED OVER TO SUMMARY | [5 empty] | 3542150

## LMS
ITEM NO. | DSR / NDSR (MR) | ITEM DESCRIPTIONS | Unit | QTY. | Rate |  | Amount (In Rs.)
[5 empty] | DSR | Non-DSR | DSR | Non-DSR
SUB HEAD R1 |  | LMS - LIGHTING MANAGEMENT SYSTEM
Design, Supply, installation, testing and commissioning of following Automatin System for Lighting Management System:
LMS - LIGHTING
Important Notes: 1. DALI -2 Type 2 Drivers shall be considered for all the fixtures. 2. All the Sensors, Keypads, Controller shall be compatible for DALI Type 2. 3. Drivers shall be flicker free in operations. 4. Drivers shall Comply to DALI Part 252, 253.
1 | MR | Supply, Installation, Testing and Commissioning of LMS Distribution board as per approved installation dwgs. Reference Standard: IS 8623 , Enclosure:1.2mm CRCA Sheet Steel, Powder Coated, Door : Single Door, Cable Entry : Top & Bottom, shall be of IP 42 Sheet steel door. Note:1) Separate Earth bus/Neutral bus for each phase ' 2) Each Circuit shall have yellow ferrules with circuit number. 3) Accessories required for installation of DB's on Wall/Column/Gyp Board shall be considered 4) DB's shall be covered with powder coated (paint should match with DB Color) wire ways/raceways/camuflauging all around and up to ceiling to receive incoming circuits and the rate of the same shall be included in the DB section/part only. 5) Laminated A3 OR A4 size SLD copy shall be pasted inside DB door 6) Safe shroud for Neutral link shall be provided. 1. Main controller - Capable of controlling up to 1056 switch legs 2. Low voltage power supply - Capable of supplying 75 power draw units. | Set | 10 | 16250 | 3500 | 162500 | 35000
2 | MR | Supply of Lighting control and monitor software, captures floor wise consumption, each event, Energy Reporting & monitoring per processor. | Set | 10 | 422500 | 25000 | 4225000 | 250000
3 | MR | Supply of Lighting control BACnet softwares for BMS integration | Set | 10 | 128700 | 10000 | 1287000 | 100000
4 | MR | SITC of Software for Energy Reporting & monitoring per processor, English. | Set | 10 | 195000 | 15000 | 1950000 | 150000
5 | MR | Supply, Installation, Testing and Commissioning of DALI2.0 certified UNIVERSAL DALI controller with dynamic grouping and 4 hr fade time dimming feature. Controller shall be Single or Dual link as per requirement and can handle 64 unique DALI adresses and 64 Unique DALI groups on the same link. Drivers for Static dimming, DT-6 and DT-8 type of dimming cna be connected to the same link | Nos | 91 | 112970 | 10000 | 10280270 | 910000
6 | MR | Supply, Installation, Testing and Commissioning of 4 channel switching relay module with 5A rating for each circuit and switching cycles shall be rated for at least 500000 cycles or above | Nos | 82 | 38870 | 5000 | 3187340 | 410000
7 | MR | SITC of Wireless Occupancy/Vacancy Sensor for rooms with a frequency of 865 MHz, Ceiling mount, infrared, 37.2 sq m (400 sq ft), battery-powered, 102 mm (4.0 in) diameter | Nos | 1034 | 9500 | 1000 | 9823000 | 1034000
8 | MR | SITC of Wireless Occupancy/Vacancy Sensor for rooms With a frequency of 865 MHz, battery- powered, white similar to Hallway type detection | Nos | 80 | 9500 | 1000 | 760000 | 80000
9 | MR | SITC of Wireless Occupancy/Vacancy Sensor for rooms With a frequency of 865 MHz, battery- powered, white similar to Corner mount 90 deg detection | Nos | 21 | 9500 | 1000 | 199500 | 21000
10 | MR | SITC of Wireless Occupancy/Vacancy Sensor for rooms With a frequency of 865 MHz, battery- powered, white similar to Corner mount 90 deg detection with RELAY of 16A rating to make it STANDALONE system - (B1 BOH area) | Nos | 4 | 9500 | 1000 | 38000 | 4000
#REF! | MR | SITC of Sensor Module, to connect 10 number of sensors either of the Occupancy / Daylight / Personal sensors/PIco. No wired connections, ceiling mount. | Nos | 140 | 13260 | 1000 | 1856400 | 140000
#REF! | MR | SITC of Wireless personlised control Keypad with a WPC approved frequency of 865 Mhz, 3 Button with raise and lower for smaller rooms, with faceplate, mounts on glass surfaces also, with 10 year battery life along with necessary fixing arrangements and programming at site etc, complete as required. Similar to Lutron PN2 3bRL series with face plate for LIGHT ONLY | Nos | 105 | 16650 | 2500 | 1748250 | 262500
#REF! | MR | SITC of Wireless personlised control Keypad with a WPC approved frequency of 865 Mhz, 6 Button with raise and lower for bigger rooms, with faceplate, mounts on glass surfaces also, with 10 year battery life along with necessary fixing arrangements and programming at site etc, complete as required. Similar to Lutron PN2 3bRL & PN2 3B series with dual gang face plate for LIGHT & SHADES | Nos | 12 | 20000 | 3500 | 240000 | 42000
#REF! | MR | SITC of Wireless personlised control Keypad with a WPC approved frequency of 865 Mhz, 6 Button with raise and lower for bigger rooms, with faceplate, mounts on glass surfaces also, with 10 year battery life along with necessary fixing arrangements and programming at site etc, complete as required. Similar to Lutron PN2 3bRL & PN2 3B series with dual gang face plate for LIGHT ONLY | Nos | 31 | 20000 | 3500 | 620000 | 108500
#REF! | MR | SITC of 8/10 button wired keypad loctaed in electrical room for Master and scene control that includes shades + Lights for LARGE ROOMS | Nos | 31 |  |  | 0 | 0
#REF! | MR | SITC of A/V Integration Module for conenction to A/V controllers via RS232/Ethernet | Nos | 17 |  |  | 0 | 0
#REF! | MR | SITC of desktop server with Microsoft Windows 2010 Server Operating System Installed. The hardware Includes the computer with a high performance hard drive for maximum data integrity, a monitor, a keyboard and a mouse. | Nos | 1 |  |  | 0 | 0
#REF! | MR | Network Swithch - 6 port | Nos | 10 |  |  | 0 | 0
20.1 | 39.18.1 | 1 run of cable | RM | 500 |  |  | 0 | 0
21 | MR | QS cable for power and data. Cable Common – 12 AWG (4.0 mm2); Power – 12 AWG (4.0 mm2); MUX Data – 22 AWG (0.25 mm2); Data – 22 AWG (0.25 mm2); Sense Line – 18 AWG (0.75 mm2); Drain Wire – 24 AWG (0.2 mm2) | RM | 3420 |  |  | 0 | 0
22 | MR | Complete commissioning of the system | Lot | 10 |  |  | 0 | 0
23 | 1.2 | Supplying and fixing of following sizes of steel conduit along with accessories in surface/recess including painting in case of surface conduit, or cutting the wall and making good the same in case of recessed conduit as required. |  |  |  |  | 0 | 0
23.1 | 1.20.2 | 25mm | RM | 3785 |  |  | 0 | 0
|  | Note: Cost to include visit to OEM factory before delivery of materials at site for a FAT, process and quality inspection of the proposed materials in the tender under this head for 3 persons from user / project manager / designer firm. |  |  |  |  | 0 | 0
TOTAL CARRIED OVER TO SUMMARY
SUB HEAD R2 |  | MOTORISED SHADES - WITHOUT FABRIC
Design, Supply, installation, testing and commissioning of following Automatin System for Motorised:
1 | MR | Motorised shades (wo the fabric) - SITC of Low Voltage DC Addressable Roller Shade Motor (Considering individual motor per 1 or 2 glass panel ),Noise level should be less than 38 dBA at 3 feet, Maximum fabric coverage should be upto 100 Sq ft. Motors in the same window façade should move in unison using Intelligent Hembar alignment technology, Seemless integration to lighting management system without use of interfaces- NO FABRIC | Nos. | 234
2 | MR | Power supply to convert DC from AC for shades - Individual power supply 24V outlet and supply power draw units to EDUs | Nos. | 369
3 | MR | Tube & hambers suitable for above | RM | 1107
4 | MR | SITC of 8/10 button wired keypad loctaed in electrical room for FM team for manual intervention. | Nos. | 10
5 | MR | SITC of main controller to connect to shades link, Panel accepts one 220-240V, 1 phase, 2 wire, 10A feed, (10A-1P over-current protection, per circuit | Nos. | 4
6 | MR | Shades realted web-based software license which allows for control and programming of motorised shades. | Set | 4
7 | MR | Software for AUTOMATIC MOVEMENT OF SHADES based on sun position - | Set | 4
8 | MR | QS cable for power and data. Cable Common – 12 AWG (4.0 mm2); Power – 12 AWG (4.0 mm2); MUX Data – 22 AWG (0.25 mm2); Data – 22 AWG (0.25 mm2); Sense Line – 18 AWG (0.75 mm2); Drain Wire – 24 AWG (0.2 mm2) - LUTBLU. | RM | 1361
9 | MR | Commissioning of the complete system (Shades) | Set | 10
10 | 1.2 | Supplying and fixing of following sizes of steel conduit along with accessories in surface/recess including painting in case of surface conduit, or cutting the wall and making good the same in case of recessed conduit as required.
| 1.20.2 | 25mm | RM | 1800
Note: Fabric in Architect scope.
TOTAL CARRIED OVER TO SUMMARY

## FIRE FIGHTING
Sl. No. | DSR 2025/M R | DESCRIPTION OF ITEMS | UNIT | Total Qty | Rate (In Rs.) |  | Amount (In Rs.)
[5 empty] | DSR | Non-DSR | DSR | Non-DSR
B HEAD E |  | SPRINKLER, PIPING & FITTINGS
1 | 27.7 | Providing, laying, testing & commissioning of 'C' class heavy duty MS pipe conforming to IS 1239/Class -II of IS: 3589 including Welding, fittings like elbows, tees, flanges, tapers, nuts bolts, gaskets etc. and fixing the pipe on the wall/ceiling with suitable clamp/support frame and painting with two or more coats of synthetic enamel paint of required shade complete as required : For Sprinkler System
1.1 | 2027-07-01 | 25 mm dia | RM | 8335 | 619 | 150 | 5159365 | 1250250
1.2 | 2027-07-02 | 32 mm dia | RM | 462 | 788 | 188 | 364056 | 86856
1.3 | 2027-07-03 | 40mm dia | RM | 480 | 903 | 225 | 433440 | 108000
2 | MR | Providing, laying, jointing, testing and commissioning of following sizes of MS 'C' Class (Heavy duty) grooved pipes conforming to IS-1239 including all accessories like orifice plate(of required dia), UL/FM listed DI grooved fittings like elbows, tees, SINGLE BOLT COUPLING upto 100 mm and double bolt for above 100 mm, flange adaptors, reducers etc. with grooved jointing shall be used on the pipes complete as per specification. G.I. pipe sleeve of suitable higher size shall be provided wherever the pipes are crossing the walls/floors and sealing the sleeves with glass wool in between & fire sealent compound at either end all as per Project Manager’s / Consultants requirements including cutting holes and chases in brick. RCC work and making good the same to original conditions complete in all respects. Grooving of Pipes using manufacturers machine shall also be included in the
2.1 |  | 50 mm dia | RM | 756 | 1263 | 300 | 954828 | 226800
2.2 |  | 65 mm dia | RM | 980 | 1330 | 375 | 1303400 | 367500
2.3 |  | 80 mm dia | RM | 241 | 1623 | 450 | 391143 | 108450
2.4 |  | 100 mm dia | RM | 85 | 2350 | 600 | 199750 | 51000
2 | 27.21 | Providing, fixing, testing & commissioning of 15mm dia quartzoid bulb type sprinklers of rating 68°C with required accessories:
2.1 | 27.21.1 | Pendent Sprinkler (68 °C) | Nos. | 2745 | 650 | 200 | 1784250 | 549000
2.2 | MR | Pendent Sprinkler (79 °C) | Nos. | 43 | 650 | 200 | 27950 | 8600
2.3 | MR | Pendent Sprinkler (141 °C) | Nos. | 43 | 650 | 200 | 27950 | 8600
3 | 27.25 | Supplying, installation, testing & commissioning of sprinkler flexible pipe (UL Listed) of stainless steel complete with 15 NPT on reducer thread with maximum working pressure of 175 PSI test pressure of 875 PSI (Burst) with branch line (Inlet) 25mm NPT male thread to sprinkler head (Outlet) 15mm NPT female thread with reducer, nipple, 2 side brackets, center bracket, stockbar of following sizes complete as required.
| 27.25.2 | 1000 mm | Nos. | 1647 | 1000 | 300 | 1647000 | 494100
4 | MR | Providing and fixing Portable Clean Agent (FE-36)/FE236fa Hexaflouropropane type fire extinguisher, ISI Marked IS 15683:2006, Gas listed under EPA SNAP, EPDM Rubber Hose, CE MArked Valve, suitable for Class A,B and C type of fires, conforming to ISO 14520, FM approved and UL listed. (1 cylinder for every 140 sq.m)-6Kg (For Critical areas only) | NOS. | 50 | 2500 | 250 | 125000 | 12500
4a | MR | Providing and fixing 6 Kg. ABC MAP-90% Powder type fire extinguishers are manufactured and marked to Indian standard IS: 15683. Hose shall made of EPDM Rubber, CE Marked Valve, Suitable first aid appliance for fighting fires in Class A, B & C fire that is wood, textile, flammable liquids & gases. (For general areas) | NOS. | 150 | 2000 | 500 | 300000 | 75000
5 | MR | Providing and fixing Modular type ceiling mounted clean agent (FE-36)/FE236fa Hexaflouropropane type fire extinguisher, ISI Marked IS 15683:2006, Gas listed under EPA SNAP, having sprinkler with glass bulb rated at 68 deg.C, CE MArked Valve, suitable for Class A,B and C type of fires, conforming to ISO 14520, FM approved and UL listed.-10Kg | Nos. | 30 | 36000 | 1000 | 1080000 | 30000
6 | MR | Wet chemical stored pressure 2Ltr capacity (K-Type) including accessories, pressure guage and floor mounting accessories (kitchen area) | Nos. | 20 | 3250 | 250 | 65000 | 5000
|  | TOTAL CARRIED OVER TO SUMMARY |  |  |  |  | 13863132 | 3381656
B HEAD F |  | PANEL FLOODING SYSTEM
Note : This is a design and build item. The quoting agency shall have the responsibility for doing all calculations, engineering designs, shop drawings and execution post award of work. Necessary coordination with the electrical Panel Vendor shall also be done by the agency
Design, Engineering, Supply, Installation, testing and commissioning of Automatic Linear pneumatic Tube Detection based FK- 5-1-12 Gas Suppression System for Electrical Panels comprising of the following items:
1 | MR | Supply, fixing, testing and commissioning of 1 KG capacity FK-5-1-12 assembly including automatic valve, push in connector for tube, 1 KG cylinder FK-5-1- 12 gas cylinder , mounting bracket, with all accessories as required. | No. | 50
2 | MR | Supply, fixing, testing and commissioning of 2 KG capacity FK-5-1-12 DLP assembly including automatic valve, push in connector for tube, 2 KG cylinder FK-5-1- 12 gas cylinder , mounting bracket, with all accessories as required. | No. | 1
3 | MR | Supply, fixing, testing and commissioning of 4 KG capacity FK-5-1-12 DLP assembly including automatic valve, push in connector for tube, 4 KG cylinder FK-5-1- 12 gas cylinder , mounting bracket, with all accessories as required. | No. | 0
4 | MR | Supply, fixing, testing and commissioning of 6 KG capacity FK-5-1-12 DLP assembly including automatic valve, push in connector for tube, 4 KG cylinder FK-5-1- 12 gas cylinder , mounting bracket, with all accessories as required. | No. | 0
5 | MR | Supply, fixing, testing and commissioning of Linear pneumatic heat Detection Tube with all necessary fittings & supports to complete the works etc as required. UL listed tube as per UL521 | RM | 253
6 | MR | Supply, fixing, testing and commissioning of End of Line adapter with Pressure gauge | No. | 51
7 | MR | Supply, fixing, testing and commissioning of Pressure Switch to monitor Pressure drop in the tube, switch point 5 Bars. Switch Type SPST, Normally Open, Electric Rating : 120/240 VAC-375 VA, 24 VAC-125 VA, Open 160 psi y-7, Close 185 psi y- 5,Pressure switch + adaptor / 5bar. | No. | 51
8 | MR | Supply, fixing, testing and commissioning of T Connection, Brass, Nickle plated, | No. | 10
9 | MR | Supply, fixing, testing and commissioning of End of plug used for fitting at the tube end to terminate the point. | No. | 10
10 | MR | Supply, fixing, testing and commissioning of Master control unit for controlling system including pressure switches,buzzers , electronic hooters,electrical wiring and other all necessary accessories as required to make entire system functional. Panel shuold be with battery back up | No. | 51
Note: Actual Linear pneumatic heat Detection Tube quantities and cylinder capacities shall be calculated based on approved Panel GA drawings and tenderer need to be submit detail calculation, drawings for evaluation of the design and quantities requirement
TOTAL CARRIED OVER TO SUMMARY
B HEAD G |  | INERGEN (IG-541) INERT GAS SYSTEM (UPS+BATTERY + SERVER ROOMS)
Design, Engineering, Supply, Installation, testing and commissioning of Inergen Inert
1 |  | CYLINDERS, PRESSURE CONTROL VALVE AND HOSE
1.1 | MR | Cylinder seamless PESO approved, 140L, 300 bar, (IG 541 filled 58.3 Kgs) with Cylinder Valve QRV TD 300 , (MAIN ) | Nos | 16
1.2 | MR | Contact Pressure Gauge (NC) for 300 bar system | Nos | 16
1.3 | MR | Discharge Hose with sealings 375mm | Nos | 16
1.4 | MR | Pressure control valve CF-S HP | Nos | 16
2 | MR | MANIFOLD CHECK VALVE
2.1 | MR | Check valve KRV-1 complete | Nos | 16
2.2 | MR | Cap KRV-1 ( For Pressure Testing) | Nos | 16
3 |  | RELEASE UNIT PRIMARY AND SLAVE CYLINDERS
3.1 | MR | Release device electrical QRV | Nos | 8
3.2 | MR | Release device manual QRV | Nos | 8
3.3 | MR | Hose MX PH300, DN4x600 | Nos | 8
3.4 | MR | Union GE 6-PLR-ED A3C | Nos | 8
3.5 | MR | Union ET06LOMDCF | Nos | 8
3.6 | MR | Safety device malfunction pressure SFD DN4 300 | Nos | 8
3.7 | MR | Union EW 06 L CF | Nos | 8
3.8 | MR | Union GZR06L/06SCF | Nos | 8
3.9 | MR | Adapter M12x1.5 – G1/8 | Nos | 8
4 |  | PRESSURE SWITCH
4.1 | MR | Limit switch pneumatic operated | Nos | 3
4.2 | MR | Adapter, 1/4” NPT to M12 x 1.5 Hose | Nos | 3
4.3 | MR | Adapter, Pressure Switch G 1/4 to M12 x 1.5 Hose | Nos | 3
4.4 | MR | DISCHARGE NOZZLE
4.5 | MR | VN TFI Brass 360 Degree 25mm | Nos | 21
4.6 | MR | Orifice Plate for 25mm Nozzle (PKT Qty - 10Nos) | Nos | 20
5 |  | WARNING STICKER
5.1 | MR | Warning Sign (Sticker) - DO NOT ENTER | Nos | 3
5.2 | MR | Warning Sign (Sticker) - VACATE AREA | Nos | 3
6 |  | TOOLS
6.1 | MR | Reset Tool QRV ( Only One No. Considered for whole system) | Lot | 3
7 |  | PIPINGS AND DETECTION PART
7.1 | MR | SCH80/160 , Cylinder Manifold, Manifold Coupling, End Cap | Lot | 3
7.2 | MR | ASTM A53 / A106 Gr.B, Pipes & Fittings | Lot | 3
7.3 | MR | Pipe support & painting. | Lot | 3
7.4 | MR | Cylinder Rack supports | Lot | 3
7.5 | MR | Gas realease panel | Lot | 3
7.6 | MR | Smoke Detector | Lot | 3
7.7 | MR | Response Indicator | Lot | 3
7.8 | MR | Manual Actuator | Lot | 3
7.9 | MR | Manual Abort | Lot | 3
7.1 | MR | Sounder cum strobe | Lot | 3
7.11 | MR | UL flow calculation | Lot | 3
TOTAL CARRIED OVER TO SUMMARY
B HEAD H |  | KITCHEN HOOD SUPPRESSION
Design, Engineering, Supply, Installation, testing and commissioning of Kitchen Hood Suppression Sysetm as follows:
1 | MR | Extinguishant :- 9 Ltr Wet Chemical Agent wet chemical agent to protect Commerical Kitchen & protect the class "F" Fire ( Greased Based Fire). Can : S.S, Sheet metal thickness 1.2 mm, 100% Hydraulic Pressure tested, conform to EN/PED standarda. Can shall be manufactured as per IS:15683 and
Tube for automatic fire detection and suppression system made by special modified Polyamide (PA), Color Grey RAL1018, High grade quality, Inner diameter 4mm, OuterDiameter 6 MM,
Kitchen System Hose, 8 X 1 Tube Adapter, Stainless Steel, Maximum Working Pressure 220 Bar at 20°C
SS Tube Fitting G1/4 "
SS Tube Fitting Straight Union for Flexible Hose
SS Tube Fitting Elbow
T connector for actuator
SS OD Pipe-8 mm of 1 meter
Pipe Brackets for 8 mm SS Pipe
Straight Fitting for Nozzle
Stainless steel Class F Liquid Agent Nozzle, G1/4" Male
Cross Panel Tubing for Detection Tube
Manual Actuator include Pressure Gauge , connection for filling adapter with yellow safety coller
Pressure Switch to monitor Pressure drop in the tube, switch point 5 Bars.
Wall Brackets For End Line Device
Master Control Unit with hooter
1.1 | MR | Kitchen Hood Suppression for Hood Size: 7500 mm (L) x 1700mm (W) x 550mm (H) | Lot | 1
1.2 | MR | Kitchen Hood Suppression for Hood Size: 8100 mm (L) x 1500mm (W) x 550mm (H) | Lot | 1
1.3 | MR | Kitchen Hood Suppression for Hood Size: 2200 mm (L) x 1200mm (W) x 550mm (H) | Lot | 1
1.4 | MR | Kitchen Hood Suppression for Hood Size: 2000 mm (L) x 1200mm (W) x 550mm (H) | Lot | 1
1.5 | MR | Kitchen Hood Suppression for Hood Size: 5400 mm (L) x 1200mm (W) x 550mm (H) | Lot | 1
TOTAL CARRIED OVER TO SUMMARY
B HEAD I |  | FIRE CURTAIN
1 | MR | Supply, Installation, testing & comissioning of Automatic Fire Safe 120 fire Curtain with Galv. MS Head Box, Powder Coated Side & Adjustment Channels and Bottom Bars with Motors for power up operation fixed into Steel rollers with woven glass fiber fabric stainless steel glass fiber mesh, reinforced with stainless steel wire having micronized aluminium polymer coating on each side of the fabric (silver/grey) with its control panel and all installation assemblies & accessories reuired to complete the installation. The operation shall be suitable for dedicated 230 Volts UPS, 50 Hz AC supply. Complete system tested in accordance with BS EN-8524-1 for product and EN 1634-1 for fire testing (for 120
List of component of Fire Curtains:Top box, Side Guides, Curtains, barrel including motor, dummy end and bottom rail, Individual Control Panel (FC01), Key switch,Override switch(Egress Switch),etc.
Installation: The fire curtain has fixing options to suit all types of ceiling configurations and can be integrated into either a suspended or a solid ceiling. It remains hidden until required. Upon receiving a signal from the fire detection system or on loss of power with the gravity fail safe system, the curtain automatically unwinds to its operational position all complete as per manufacturers specifications and direction of Engineer in- Charge.
Note: Cost to include visit to OEM factory before delivery of materials at site for a FAT, process and quality inspection of the proposed materials in the tender under this head for 3 persons from user / project manager / designer firm.
1.1 | MR | 1800X3000 MM | Each | 21
1.2 | MR | 2000X3000 MM | Each | 3
TOTAL CARRIED OVER TO SUMMARY
1 | MR | Removing of exisiting Upright sprinklers from the existing sprinkler network, providing dummy and storing as per site engineer's instructions.( IDF/SERVER ROOM/UPS & BATTERY ROOM) (vendor is responsible for safe handling of sprinklers, if any damage occurs during removing , same shall be procured by vendor and install without extra cost) | Nos. | 110 |  | 350 | 0 | 38500
2 | MR | Cutting , removing, rerouting / providing dummy of existing fire fighting pipes, sizes from 25 to 150mm dia from various places or reroute the existing pipes as per the site requirement ( IDF/SERVER ROOM/UPS & BATTERY ROOM) Vendor to visit the site, analyse the quantum of works involved & quote accordingly.
2.1 | MR | 25mm nominal dia | RM | 165 |  | 150 | 0 | 24750
2.2 | MR | 32mm nominal dia | RM | 150 |  | 188 | 0 | 28200
2.3 | MR | 40mm nominal dia | RM | 120 |  | 225 | 0 | 27000
2.4 | MR | 50mm nominal dia | RM | 120 |  | 300 | 0 | 36000
2.5 | MR | 65mm nominal dia | RM | 120 |  | 375 | 0 | 45000
2.6 | MR | 80mm nominal dia | RM | 120 |  | 450 | 0 | 54000
2.7 | MR | 100mm nominal dia | RM | 70 |  | 600 | 0 | 42000
2.8 | MR | 150mm nominal dia | RM | 30 |  | 900 | 0 | 27000
3 | MR | Relocating of existing sprinklers to new positions as per site including a few meters of MS Class 'C' Pipe taking care not to damage/break the glass bulb, including all necessary supports, pipe jointing as required | Nos | 220 |  | 250 | 0 | 55000
4 | MR | Modification in existing sprinkler network as per the drawing attached Work involves cutting the existing entier branch from main header and relocate as per the drawing item shall inclusive of removing the existing branch with bulbs and refixing the same with required supports.
4.1 | MR | 25mm nominal dia | RM | 330 |  | 300 | 0 | 99000
4.2 | MR | 32mm nominal dia | RM | 110 |  | 376 | 0 | 41360
4.3 | MR | 40mm nominal dia | RM | 55 |  | 450 | 0 | 24750
4.4 | MR | 50mm nominal dia | RM | 110 |  | 600 | 0 | 66000
4.5 | MR | 65mm nominal dia | RM | 110 |  | 750 | 0 | 82500
4.6 | MR | 80mm nominal dia | RM | 110 |  | 900 | 0 | 99000
4.7 | MR | 100mm nominal dia | RM | 55 |  | 1200 | 0 | 66000
4.8 | MR | 150mm nominal dia | RM | 22 |  | 1800 | 0 | 39600
|  | TOTAL CARRIED OVER TO SUMMARY |  |  |  |  | 0 | 895660

## SUMMARY OF HVAC WORK
Name of Project: “Interior Fit-out work in the office space of Power Finance Corporation Limited, Tower-H, World Trade Centre, Nauroji Nagar, New Delhi-110029 including Operation & Maintenance for 06 years”
SUMMARY OF HVAC WORK
SECTION | DESCRIPTION | Amount (In Rs.)
|  | DSR | Non DSR | TOTAL
SUB HEAD A | PLUMBING -PIPING & VALVES
SUB HEAD B | AIR DISTRIBUTION - DUCTING, GRILLES, THARMAFUSERS ETC.
SUB HEAD C | HVAC EQUIPMENTS
SUB HEAD D | CHILLERS
SUB HEAD E | AHU, FCU & TFA
SUB HEAD F | EVAPORATIVE COOLING - AIR WASHER
SUB HEAD G | HI - WALL SPLIT SYSTEMS
SUB HEAD H | BMS (BUILDING MANAGEMENT SYSTEM)
TOTAL
Total DSR
Total Cost ( Carried Forward) in Rs.

## HVAC BOQ
Bill of Quantities
Name of Project: “Interior Fit-out work in the office space of Power Finance Corporation Limited, Tower-H, World Trade Centre, Nauroji Nagar, New Delhi-110029 including Operation & Maintenance for 06 years”
Name of Work : HVAC WORK
ITEM NO. | DSR / NDSR (MR) | ITEM DESCRIPTIONS | UNIT | Total Qty | Rate (In Rs.) |  | Amount (In Rs.)
[5 empty] | DSR | Non-DSR | DSR | Non-DSR
SUB HEAD A |  | PLUMBING -PIPING & VALVES
1 |  | INSULATED CHILLED WATER PIPING (Nitrile rubber insulation)
| 30.2 | Supplying, laying/ fixing, testing and commissioning of following nominal sizes of chilled water piping inside the building (with necessary clamps, vibration isolators and fittings but excluding valves, strainers, gauges etc.) duly insulated with following closed cell elastomeric nitrile rubber of minimum 45 Kg / cum density, thermal conductivity 0.037 W/MK or better at 20 deg mean temperature class 'O' Nitrile insulation applied by suitable adhesive complete including repairing of damage to building etc. as per specifications and as required complete in all respect.
Note:-The Pipes of sizes 150mm & below shall be M.S. 'C' class as per IS : 1239 and pipes size above 150mm shall be welded black steel pipe heavy class as per IS: 3589, from minimum 6.35mm thick M.S. Sheet for pipes upto 350 mm dia. and from minimum 7mm thick MS sheet for pipes of 400 mm dia and above.
1.1 | 2030-02-07 | 125mm dia.(32 mm thick insulation) | Meter | 95 | 3028 | 825 | 287660 | 78375
1.2 | 2030-02-08 | 100mm dia. (32 mm thick insulation) | Meter | 44 | 2708 | 675 | 119152 | 29700
1.3 | 2030-02-09 | 80mm dia.(32 mm thick insulation) | Meter | 134.2 | 1998 | 525 | 268131.6 | 70455
1.4 | 2030-02-10 | 65mm dia(32 mm thick insulation) | Meter | 105.6 | 1733 | 425 | 183004.8 | 44880
1.5 | 2030-02-11 | 50mm dia(32 mm thick insulation) | Meter | 28.6 | 1683 | 350 | 48133.8 | 10010
1.6 | 2030-02-12 | 40mm dia. (32 mm thick insulation) | Meter | 288.2 | 1335 | 275 | 384747 | 79255
1.7 | 2030-02-13 | 32 mm dia(19 mm thick insulation) | Meter | 836 | 1238 | 238 | 1034968 | 198968
1.8 | 2030-02-14 | 25 mm dia(19 mm thick insulation) | Meter | 61.6 | 1104 | 200 | 68006.4 | 12320
2 | CIVIL 18.8 | Providing and fixing sound insulated Polyproplene piping system as per EN 12056 Part Providing and fixing Chlorinated Polyvinyl Chloride (CPVC) pipes, having thermal stability for hot & cold water supply, including all CPVC plain & brass threaded fittings and fixing the pipe with clamps at 1.00 m spacing. This includes jointing of pipes & fittings with one step CPVC solvent cement and the cost of cutting chases and making good the same including testing of joints complete as per direction of Engineer in Charge. Concealed work, including cutting chases and making good the walls etc. - For drain pipe.
2.1 | CIVIL 18.7.5 | 40 mm dia | Meter | 45 | 320 | 65 | 14400 | 2925
2.2 | CIVIL 18.8.4 | 32 mm dia | Meter | 195 | 105 | 25 | 20475 | 4875
2.3 | CIVIL 18.8.3 | 25 mm dia | Meter | 155 | 145 | 30 | 22475 | 4650
3 | 30.5 | Supplying, laying, fixing, testing and commissioning of following thickness closed cell elastrometric nitrile rubber of class 'O' applied by suitable adhesive, as per specifications and as required complete in all respect.
3.1 | 2030-05-01 | 32mm | Sq.M | 44 | 960 | 220 | 42240 | 9680
3.2 | 2030-05-02 | 19mm | Sq.M | 450 | 520 | 160 | 234000 | 72000
INSULATED VALVES
4 | 30.7 | Supplying, fixing, testing and commissioning of following valves, strainers, gauges in the chilled water plumbing duly insulated to the same specifications as the connected piping and adequately supported as per specifications.
4.1 | 2030-07-01 | BUTTERFLY VALVE (MANUAL) with C I body SS Disc, Nitrile Rubber Seal & O- Ring PN 16 pressure rating for chilled water/hot eater circulation as specified.
4.1.1 | 30.7.1.5 | 80 mm dia | Each | 16 |  |  | 0 | 0
4.1.2 | 30.7.1.6 | 65 mm dia | Each | 4 |  |  | 0 | 0
4.1.3 | 30.7.1.7 | 50 mm dia | Each | 4 |  |  | 0 | 0
4.1.4 | 30.7.1.8 | 40 mm dia | Each | 26 |  |  | 0 | 0
4.2 | 2030-07-02 | BALANCING VALVE WITH BUILT IN MEASURING FACILITY with CI body flanged construction with EPDM coated disc with long pitch with protected out pipe insulation & PN 16 pressure rating for chilled / hot water circulation as specified.
4.2.1 | 30.7.2.5 | 80 mm dia | Each | 6 |  |  | 0 | 0
4.2.2 | 30.7.2.6 | 65 mm dia | Each | 1 |  |  | 0 | 0
4.2.3 | 30.7.2.8 | 40 mm dia | Each | 1 |  |  | 0 | 0
4.2.4 | MR | 32 mm dia | Each | 7 |  |  | 0 | 0
4.3 | 2030-07-03 | NON - RETURN VALVE with duel plate of C I body SS plates vulcanized NBR seal flanged end & PN 16 pressure rating for chilled / hot water circulation including insulation as specified.
4.3.1 | 30.7.3.5 | 80 mm dia | Each | 4 |  |  | 0 | 0
4.4 | 2030-07-04 | Y - STRAINER of Ductile CI Body flanged ends with stainless steel strainer for chilled / hot water circulation including insulation as specified.
4.4.1 | 30.7.4.5 | 80 mm dia | Each | 4 |  |  | 0 | 0
4.4.2 | 30.7.4.6 | 65 mm dia | Each | 1 |  |  | 0 | 0
4.4.3 | 30.7.4.7 | 50 mm dia | Each | 2 |  |  | 0 | 0
4.4.4 | 30.7.4.8 | 40 mm dia | Each | 12 |  |  | 0 | 0
4.4.5 | MR | 32 mm dia | Each | 36 |  |  | 0 | 0
4.4.6 | MR | 25 mm dia | Each | 8 |  |  | 0 | 0
4.5 | 30.8 | Providing and fixing in position industrial type pressure gauges with gun metal / brass valves complete etc. as required | Each | 134 |  |  | 0 | 0
4.6 | 30.9 | Providing & fixing in position industrial type mercury thermometers complete etc. as required. | Each | 134 |  |  | 0 | 0
VALVES WITHOUT INSULATION
5 | 3.11 | Supplying, fixing, testing and commissioning of following valves, gauges and strainers for condenser water circulation as per specifications.
5.1 | 2030-11-03 | Supplying, fixing, testing and commissioning of following Motorised Butterfly valves with C.I body, SS Disc,O-ring and minimum PN-16 pressure rating,confirming to BS 5155,IS 13095,with IP-55 actuator, capable of accepting upto 10V DC,and upto 20 mA electric signal and providing similar transduced feedback output to control system as required.
5.1.1 | 30.11.3.8 | 80 mm dia | Each | 4 |  |  | 0 | 0
5.1.2 | 30.11.3.9 | 65 mm dia | Each | 0
5.1.3 | 30.11.3.10 | 50 mm dia | Each | 0
5.2 | 2030-11-04 | Supplying, fixing, testing and commissioning of following sizes electronic, self-balancing, pressure independent type dynamic balancing valve with integrated 2 way modulating control valves in a single body.The actuator shall be capable of accepting upto 10 V DC and upto 20 mA electric signal and shall provide similar transduced feedback output to control system.Maximum close off pressure shall not ne less than 6 Bar for upto 50 mm valves and 7 Bar for 65mm & above.Valves should have pressure rating of 25 Bar monimum.
5.2.1 | 30.11.4.4 | 80 mm dia | Each | 0
5.2.2 | 30.11.4.5 | 65 mm dia | Each | 1 |  |  | 0 | 0
5.2.3 | 30.11.4.6 | 50 mm dia | Each | 2 |  |  | 0 | 0
5.2.4 | 30.11.4.7 | 40 mm dia | Each | 12 |  |  | 0 | 0
5.2.5 | 30.11.4.8 | 32 mm dia | Each | 36 |  |  | 0 | 0
5.2.6 | 30.11.4.9 | 25 mm dia | Each | 8 |  |  | 0 | 0
5.3 | CIVIL 18.17 | Providing and fixing gun metal gate valve / Ball Valve with C.I. wheel of approved quality (screwed end):
5.3.1 | CIVIL 18.17.1 | 25 mm nominal bore | Each | 16 |  |  | 0 | 0
5.3.2 | CIVIL 18.17.2 | 32 mm nominal bore | Each | 86 |  |  | 0 | 0
6 | MR | Flexible Pipe Connections/Bellows.
Supply, installation, testing and commissioning of insulated Flexible Pipe Connections at chiller (inlet & oulet) & chilled water pumps (inlet & outlet) and as per specifications. Flexible connections/bellows shall be complete with mating flanges, nuts and bolts and gaskets:
PN16 RATED
6.1 | MR | 80mm NB | Each | 16 |  |  | 0 | 0
| Note: | All the piping & Accessories shall be Pre-Cleaning & Descaling to be done by before the commissioning of chilled water system.
TOTAL CARRIED OVER TO SUMMARY
B HEAD B |  | AIR DISTRIBUTION - DUCTING, GRILLES, THARMAFUSERS ETC.
1 | 30.12 | DUCTING, GRILLS,DIFFUSER AND INSULATION
| 2030-12-01 | Supplying, installation, balancing and commissioning of factory fabricated GSS sheet metal rectangular/ round/oval ducting complete with neoprene rubber gaskets, elbows, splitter dampers, vanes, hangers, supports, bends, transitions, reducers, end caps, collars etc as required complete in all respect in confirmation to IS : 655 and approved drawings and specifications of following sheet thickness complete as required.
FACTORY FABRICATED RECTANGULAR DUCT
1.1 | 30.12.1.1 | Thickness 0.63 mm sheet | Sq.M | 16966.0296 |  |  | 0 | 0
1.2 | 30.12.1.2 | Thickness 0.80 mm sheet | Sq.M | 5041 |  |  | 0 | 0
1.3 | 30.12.1.3 | Thickness 1.00 mm sheet | Sq.M | 50 |  |  | 0 | 0
1.4 | 30.12.1.4 | Thickness 1.25 mm sheet | Sq.M | 25 |  |  | 0 | 0
OVAL DUCT
1.5 | 30.12.1.2 | Upto 600 mm dia / 22G (0.80mm) | Sqm | 2354 |  |  | 0 | 0
1.6 | 30.12.1.3 | 601-1200 mm dia / 20G (1.00mm) | Sqm | 450 |  |  | 0 | 0
1.7 | MR | Extra for internaly thermaly lined with 9mm thick Nitrile rubber insulation fixed with adhesive in duct under fabrication in factory complete as per directior of Engineer in charge (Rate of factory fabricated duct to be paid in above mentioned DSR item) | Sqm | 2804 |  |  | 0 | 0
2 | 2030-12-02 | Supplying, installation, balancing and commissioning of fabricated at site GSS sheet metal rectangular/ round ducting complete with neoprene rubber gaskets, elbows, splitter dampers, vanes, hangers, supports, bends, transitions, reducers, end caps, collars etc as required complete in all respect in confirmation with IS : 655 and approved drawings and specifications of following sheet thickness complete as required.
2.1 | 30.12.2.1 | Thickness 0.63 mm sheet | Sq.M | 1696.603 |  |  | 0 | 0
2.2 | 30.12.2.2 | Thickness 0.80 mm sheet | Sq.M | 504.1 |  |  | 0 | 0
3 | 30.13 | Supplying, installation, testing and commissioning of GI volume control duct damper complete with neoprene rubber gaskets, nuts, bolts, screws linkages, flanges etc in confirmation to SMACNA/IS and as per specifications complete etc. as required. | Sq.M | 208.1 |  |  | 0 | 0
4 | 30.16 | Supplying & fixing of powder coated extruded aluminium Return Air Grills with louvers but without volume control dampers complete in confirmation to SMACNA/IS and as per specifications complete etc. as required. | Sq.M | 139.5 |  |  | 0 | 0
5 | 30.19 | Supplying, Fixing, installation, testing and commissioning of thermal insulated flexible duct of following sizes duly supported at regular interval as per site requirement etc. in confirmation to SMACNA/IS and as per specifications complete etc. as required.
5.1 | 30.19.1 | 200mm dia | Meter | 705 |  |  | 0 | 0
5.2 | 30.19.1 | 150mm dia | Meter | 410 |  |  | 0 | 0
6 | 30.2 | Supplying, Fixing, testing and commissioning of fire dampers of minimum 90 minutes fire rated in supply air duct/main branch and return air path as and where required of required sizes i/c control wiring, the damper shall be motorized and spring return so as to close the damper in the event of power failure automatically and open the same in case of power being restored. The spring return action shall be inbuilt mechanism and not externally mounted. The damper shall also be closed in the event of fire signal and, in confirmation to IS and as per specifications complete etc. as required.
6.1 | 30.20.1 | Fire Damper | Sq.M | 116.5 |  |  | 0 | 0
6.2 | 30.20.2 | Actuator | Each | 193 |  |  | 0 | 0
7 | 30.21 | Supplying and fixing of acoustic lining of supply air duct and plenum with 25/15 mm thick resin bonded glass wool having density of 32 kg/m³, with 25 mm X 25 mm GI section of 1.25 mm thick, at 600 mm centre to centre covered with Reinforced Plastic tissue paper and 0.5 mm thick perforated aluminium sheet fixed to inside surface of ducts with cadmium plated nuts, bolts, stick pins, CPRX compound in confirmation to SMACNA/IS and as per specifications complete etc. as required.
7.1 | 30.21 | 25mm | Sq.M | 1673.5 |  |  | 0 | 0
7.2 | MR | 15mm for Z-Piece | Sq.M | 102.96 |  |  | 0 | 0
8 | 30.23 | Supplying and fixing of following thickness duly laminated aluminium foil of mat finish closed cell Nitrile rubber (Class "O") insulation on existing duct after applying suitable adhesive for Nitrile rubber. The joints shall be sealed with 50 mm wide and 3 mm thick self adhesive nitrile rubber tape insulation complete as per specifications and as required.
8.1 | 30.23.1 | 19mm | Sq.M | 55 |  |  | 0 | 0
8.2 | 30.23.2 | 25mm | Sq.M | 11607.475 |  |  | 0 | 0
9 | MR | 24 X 7 AC ROOMS, CRITICAL ROOMS (SERVER, DATA CENTRE, UPS, BATTERIES, NETWORK & HUB ROOMS) FLOOR & CEILING THERMAL INSULATION (NOT EXPOSED TO SUN)
9.1 |  | Supply & Installation of floor / ceiling insulation with 10mm thick closed cell elastomeric rubber EPDM ,50kg/cub.m density , Rohs compliant, Class 'O' insulation faced with 7ml glass cloth & secured with manufacturer approved adhesive. The insulation shall be No smoke, self extingushing type and with vapour barrier quality. | Sq.M | 680 |  |  | 0 | 0
10 | MR | SLOT DIFFUSERS
Supply, installation, testing & commissioning of High Quality (High Throw/Jet Throw) Extruded Aluminium powder coated Supply Air Slot Diffusers with adjustable air pattern controllers, with factory fabricated accoustically lined with mineral fibre supply air 22G Aluminium plenum and with sliding type GI hit & miss damper in matt black finish. Supply air plenum shall have factory fitted spigot connector.
10.1 |  | 2 Slot (25mm air gap) ovear all width with flanges - 125mm, opening in false ceiling-104mm width | Meter | 1541 |  |  | 0 | 0
11 | 30.17 | SQUARE DIFFUSERS MULTI CONE SUITABLE FOR GRID CEILING (600 x 600) WITH ACOUSTICALY LINED PLENUM - FOR SUPPLY AIR / RETTURN
Supplying, Fixing, installation, testing and commissioning of supply air diffusers of powder coated aluminium with aluminium volume control dampers with anti smudge ring & removable core in confirmation to SMACNA/IS and as per specifications complete etc. as required.
Supply Air Diffusers with lined plenum & with volume control damper:
Neck Size Overall size
11.1 | 30.17 | 250mm x 250mm 595mm x 595mm | Sqmt | 17.64 |  |  | 0 | 0
11.2 | 30.17 | 300mm x 300mm 595mm x 595mm | Sqmt | 7.2 |  |  | 0 | 0
11.3 | 30.17 | 595mm x 595mm 595mm x 595mm | Sqmt | 5.4 |  |  | 0 | 0
5.13 |  | ROUND / CIRCULAR MULTI-CONE DIFFUSER
Supply, installation, testing and balancing of round / circular Aluminium powder coated ceiling diffuser, flush type with inner removable core. Diffuser shall have 18G Aluminium 2 Blade butterfly key operated volume control damper for supply air (damper cost inclusive), Diffusers frame material shall be 18G Extruded Aluminium (Flat Type) and blade material shall be 0.9mm removable core (Aluminium sheet core):
11.1 | 30.17 | Supply air diffusers with volume control damper:
Outer Dia
a. | 30.17 | 600mm | Sqmt | 13.5 |  |  | 0 | 0
12 | MR | VAV BOXES:
SUPPLY OF VARIABLE AIR VOLUME BOXES (VAV'S) Installation, Testing and Commissioning of VAV boxes complete with factory fabricated GI supports and fixing arrangement of the following capacities of VAV Boxes.
Quoted prices to include cost of equipment including, Packing, Forwarding charges, Transport Charges, Transit insurance & Testing etc.
VAVs shall be pressure independent type & low velocity type, cooling only (Without heating coils / strips)
VAV Boxes shall be slow reacting type capable of delivering variable air volume type by the action of opposed blade volume control damper
VAV boxes shall be supplied with end flanges for attachment to flanged duct ends and shall be complete with all internal Acoustic treatment.
The casing shall be double skin type of Galvanized sheet steel construction with a completely sealed, easily removable. The access shall be provided in the bottom side only. VAV boxes shall be factorty accousticaly lined. The complete VAV box , actuator and controller shall be factory assembled.
VAV shall be electronically controlled networkable controller type complete with low leakage damper actuator, Microprocessor unit, wall / ceiling mounted temperature sensor with ON/OFF Switch, control transformer, unit hander brackets etc.
VAV Boxes shall also be able to reset any air flow between zero and the maximum air quantity that the boxes can handle without changing orifices or other parts, but the boxes shall be factory set at 20% of the maximum flow as minimum flow. VAV controller shall be BTL certified, support dual protocol natively with a mimimum torque of 8Nm (70 in- lb) with built in minimum of 2 AI, 2 DI and 2 AO as a standard for future integration. Add-on modules to increase capacity shall not be preferred
Controller shall come with built in RT clock and support BACnet Schedule. It should also incorporate as a default, energy saving programs that may be activated at a later date without the need of additional programming or download of software.
The noise level from the VAV boxes shall not exceed 35dbA
The quoted price shall be inclusive of the temperature sensor for each VAV unit & associated cable required for the functioning of the VAV system
LCD Thermostat should double as a calibration and programming tool without the need for additional programming software or tools. The thermostat at the minimum shall be able to perform the below functions 1.&Enter K Factor, Design Flows 2.&Balancing Option of VAV 3.&Override Damper from Thermostat 4.&Display Current CFM, Target Flow and Damper Position 5.&Password protected menu to display the Differtial Pressure reading sensed by the Controller
VAV box shall be complete with its termostat and wiring. Thermostat of VAV boxes shall be digital and it shall allow temperature presets to be adjustable from the room/space and as well as by the BMS.
UL Listed & AHRI certified VAV Boxes only to be considered.
Note:- |  | The Velocity through inlet of VAV inlet of VAV should not exceed 2000FPM
The capacities of the Rectangular units with the above specification are as follows:
i. |  | Rectangular VAV
a. | MR | 0-230CFM | Nos | 98 |  |  | 0 | 0
b. | MR | 231-360CFM | Nos | 26 |  |  | 0 | 0
c. | MR | 361-520CFM | Nos | 91 |  |  | 0 | 0
d. | MR | 521-710CFM | Nos | 61 |  |  | 0 | 0
e. | MR | 711-925CFM | Nos | 19 |  |  | 0 | 0
f. | MR | 926-1450CFM | Nos | 59 |  |  | 0 | 0
g. | MR | 1451-2100CFM | Nos | 8 |  |  | 0 | 0
ii. |  | Oval VAV
h. | MR | 45-450CFM | Nos | 29 |  |  | 0 | 0
i. | MR | 80-800CFM | Nos | 58 |  |  | 0 | 0
j. | MR | 125-1250CFM | Nos | 9 |  |  | 0 | 0
k. | MR | 200-2000CFM | Nos | 18 |  |  | 0 | 0
l. | MR | 300-3000CFM | Nos | 14 |  |  | 0 | 0
13 | MR | Integrators for the above VAVs to connect with the BMS system to read and modify the parameters. Integrator should release open protocol BACnet / MODBUS to integrate with third party BMS System. 1 Set of intigrator for Two AHU. | Set | 10 |  |  | 0 | 0
15 | MR | Communication cable and conduit work: 2C x 1.5 sq.mm copper conductor shielded cable
|  | Supply, laying , testing and commissioning of 2C x 1.5 sq.mm copper conductor shielded cable in existing conduit. (Communication cable) | RM | 7350 |  |  | 0 | 0
16 | 1.2 | 25 mm dia 16G MS conduit
| 1.20.2 | Supplying and fixing of following sizes of steel conduit along with accessories in surface/recess including painting in case of surface conduit, or cutting the wall and making good the same in case of recessed conduit as required. : (Conduit for communication cable).
| 1.20.2 | 25mm dia | RM | 7350 |  |  | 0 | 0
17 | MR | FIRE RESISTANT FLEXIBLE CANVASS CONNECTIONS
|  | Supply, fabrication, installation and testing of the flexible canvass connections constructed out of fire resistant double canvas sleeve as per the approved shop drawings. It shall be complete with flanges, nuts and bolts and fire sealant | Sqm | 42.95 |  |  | 0 | 0
18 | MR | MS WELDED DUCTING FOR KITCHEN EXHAUST/SCRUBBER - EXHAUST
|  | Supply, fabrication, Installation, testing and commissioning of 16 G CRCA MS Sheet metal ducts (welded) in accordance with the approved shop drawings and complete with supporting arrangement as per specifications. Ducts shall be painted with fire resistant paint and shall be suitable for 250 Deg C and the supporting arrangement shall be strong enough to with stand fire conditions. Duct supporting arrangement shall be factory fabricated Modular Hanging / Supporting system comprising Channel, Threaded rods & Clamps system NOTE: DUCTING SUPPORTING SYSTEM TO BE DESIGNED BY A COMPETENT AGENCY TO ENSURE SAFETY OF THE INSTALLATION, BUILDING AND THE PERSONS. CONTRACTOR TO HIRE A SPECIALISED AGENCY FOR DESIGN AND INSTALLATION OF THE DUCT SUPPORT SYSTEM AND ASSUME COMPLETE RESPONSIBILTY ON ADEQUACY OF THE SUPPORT SYSTEM. CONTRACTOR TO SUBMIT A CERTICATE FROM THE STRUCTUAL CONSULTANT ALONG WITH THE DESIGN AND DRAWINGS SUBMITTED TO THE CLIENT/PMC. | Sq.M | 525 |  |  | 0 | 0
19 | MR | FIRE RATED PAINT - KITCHEN EXTRACT DUCTS:
|  | Supply and application of Fire-Retardant Ductwork. Ducts shall be coated with Fire Resistance Coating of minimum 600–700-micron (DFT) thickness applied over ducts to provide 2 hours Fire Rating. The Fire-Resistance Coating shall be tested as per requirements of BS 476: Part 6 ‘Class O’ and Part 7 ‘Class 1’ and BS 476 Part 24 (Type A and B) to analyze Stability, Integrity, and Insulation performance for 2 hours, the duct sheet shall also conform to performance criteria (stability, integrity, insulation) without insulation for 2 hours. The average and maximum temperature of unexposed faces with or without insulation shall not exceed 140 deg. Cel and 180 deg. Cel respectively to ensure the insulation performance criteria. The coating shall be free or has minimum toxic elements such as lead, mercury, arsenic and has low VOC less than 50 gm/liter. Coated Ducts shall be treated externally with 48 Kg/m3, 50 mm thick mineral wool Insulation laminated with aluminium foil. | Sqm | 525 |  |  | 0 | 0
20 | MR | With Resin Bonded Fibre Glass Wool
|  | Kitchen Exhaust Air Duct Supply and installation of 50 mm thick Glasswool insulation with factory laminated Aluminium facing and black glass tissue on the other side for supply air duct of density 32 kg/m3, 2 layer 7ml UV cloth and protective coating foster/starbond 30-36/chemxcoat, 2 coats as per the specification, fixed with adhesive as approved by the manufacturer. | Sqm | 525 |  |  | 0 | 0
TOTAL CARRIED OVER TO SUMMARY
B HEAD C |  | HVAC EQUIPMENTS
1 | MR | PUMPS - VERTICAL INLINE TYPE (FOR ALL VERTICAL INLINE PUMPS)
Design & Supply, Installation, Testing and Commissioning of Centrifugal pumps of Vertical Inline design split coupled with TEFC squirrel cage 4-pole induction motor with IP55 protection, class F insulation, factory skid mounted on a common base frame. Pump set shall be flexible long- coupled type and with OSHA-compliant coupling guard. Pump set shall be provided with CI Casing (BS1452 Grade 220)/Ductile Iron casing, Gunmetal Bronze (BS1400 LG2C) impeller, SS (BS970 416) Shaft, mechanical seal, inertia base & vibration isolation springs. Motor shall be suitable for 415V ± 10%, 50Hz ± 3%, 3-phase AC supply. Motor shall be suitable for VFD operation i.e. motor suitable for any low voltage & low frequency range due to speed reduction / variation through VFD without heating and noise generation. Suction side : Suction pipe, manual butterfly isolating valve & suction guide with strainer. Discharge Side:- Discharge pipe, triple duty valve comprising check valve (NRV), manual butterfly isolating valve & manual balancing valve. Pressure gauges including ports at suction & discharge. All these items shall be factory fitted & assembled at pump manufacturer's plant.
Motors shall be TEFC, IP55 rated & Class F Insulation.
Motor Effeciency shall be as per ECBC+ 2017: ECBC+: IE3
Pump Mechanical Efficiency: As per ECBC+: 2017: ECBC+: 75%
Motor for VFD driven pumps shall be suitable for VFD operation with higher grade of winding insulation to take care of heating due to operation at lower frequencies & lower voltages.
Necessary civil work such as pump foundation etc are excluded from the scope of work. But necessary foundation nuts/ bolts & vibration isolation pads to be provided.
Pump Motor’s Local Power Off Locable Push Button to be provided with each pump set as part of pump cost as explained below:
● Each pump motor shall have a local OFF push button station with lockable off, fixed on the pump cable tray drop or at a suitable location , but near the pump for disconnection of power locally.
● Cost of supply & installation of required OFF push button station with lockable OFF shall be deemed to be inclusive in the cost of the pump set in this item / sub-head.
● Necessary control cabling from the local isolator to pump starter / VFD in the panel shall be accounted separately on the electrical cabling sub head.
● Refer specifications & sketches for power isolators.
Note: This item shall not be required with pump mounted VFD’s.
PUMP MOUNTED VED TO BE PROVIDED (ONLY IN CASE OF VARIABLE PUMPING SYSTEM)*:
Pump mounted VFD with disconnect switch for variable flow pumps .i.e. Note: Pump mounted VFD shall be complete with the following AND To be provided as part of the pump package and shall consist of:
Pump Mounted IP 55 VFD with disconnect switch.
VFD to have THDI not more than 40%
Output cabling from pump mounted VFD to Pump motor.
VFD shall have display of all the necessary electrical parameters and pump flow & head.
EMC & RFI FILTRATION
VFD’s for sensitive installations where life critical data communications are of importance ,like: • Hospitals • Airports • Electronic Industry • Data centres • Communication centres These installations Must have ‘C1’ category of RFI & EMC filters for 50 meters of cable length. These are applicable to all the VFD’s of pumps . For these above mentioned critical applications, if pump motors are more than 90Kw, then ‘C2’ category of filters to be used if ‘ C1’ is not available. VFD’s for normal buildings and others similar installations shall have ‘C3’ category of RFI & EMC filter for pumps.
MICROPROCESSOR BASED PUMP CONTROLLER (Pump mounted / wall mounted pump controller) (ONLY IN CASE OF VARIABLE PUMPING SYSTEM)*
Pump Controller With parallel pumping software to manage :
sequential operation of pumps
Equal run hour of pumps
To have necessary 'DO', 'DI', 'AI', 'AO' to receive input from pressure / temperature sensors & to modulate / to give command to pumps.
Should be BMS compatible.
Pressure sensors / temperature sensors with necessary cabling & conduiting
Pumps shall be selected for following performance characteristics.
Note: Cost to include visit to OEM factory before delivery of materials at site for a FAT, process and quality inspection of the proposed materials in the tender under this head for 3 persons from user / project manager / designer firm.
1.1 | MR | PRIMARY CHILLED WATER PUMPS - VARIABLE FLOW - VARIABLE SPEED (Terrace floor)
Chilled water flow 144USGPM
Head 35 Mtr
Motor 20HP (Approx.)
Working Pressure 175 PSI (12 Bar = 12 kg / Cm²)
Pump to be complete with Pump mounted VFD.
|  | Chilled water pumps with VFD as described above. (3W + 1S) | Nos. | 4 |  |  | 0 | 0
1.2 | MR | MICROPROCESSOR BASED PUMP CONTROLLER (ONLY IN CASE OF VARIABLE PUMPING SYSTEM) | Set | 1 |  |  | 0 | 0
Pump Controller With parallel pumping software to manage :
sequential operation of pumps
Equal run hour of pumps
To have necessary 'DO', 'DI', 'AI', 'AO' to receive input from pressure / temperature sensors & to modulate / to give command to pumps.
Should be BMS compatible.
Pressure sensors / temperature sensors with necessary cabling & conduiting
2 | MR | AIR FILTRATION
2.1 |  | Active Air Purification (Bipolar Ionization)
Supply, Installation, Testing, and Commissioning of Plasma Air Ionizer to improve Indoor air quality by using Bi-polar Ionization technology, producing equal amounts of positive and negative oxygen ions. The system kills microorganism and pathogens, remove Odour, and VOC and reduce dust particle /particulate matter / PM2.5 /PM 10.The product should UL / Intertek listed. The product has minimal or negligible pressure drop &amp; low power consumption. The life of the Tube should be 17,600* hours. The power consumption of 3000 CFM units should not exceed 8 watts. The power consumption of 5000 CFM units should not exceed 16 watts. The power consumption of 10000 CFM units should not exceed 50 watts. The unit shall be installed inside on Supply Duct utilizing a contractor-supply mounting bracket. Power to the ionization unit should be interlocked with the system fan operation. A five-position ion level control knob shall be their to vary the ion output between 50% and 100%.Tube-Based Model Should be Underwriters Laboratories Inc.Standards UL867. Classified as plenum rated per UL 2043.
2.1.1 | MR | upto 2000 CFM | Nos. | 5 |  |  | 0 | 0
2.1.2 | MR | 2001 CFM to 6500 CFM | Nos. | 24 |  |  | 0 | 0
2.1.3 | MR | 6501 CFM to 18000 CFM | Nos. | 6 |  |  | 0 | 0
2.1.4 | MR | 18001 CFM to 28000 CFM | Nos. | 11 |  |  | 0 | 0
2.2 |  | Chemical Biological & Radiological (CBR) Filter
Biological & Radiological (CBR) Filtration System suitable for installation inside AHU / TFA / Ventilation Cabinet, complete with factory assembled housing, mounting frames, sealing gaskets and all necessary accessories. The unit shall comprise pre-filter section, electrostatic particle charging / ionization section (non-ozone generating type), high efficiency particulate filtration media (minimum H13 as per EN 1822 / ISO 29463 or equivalent), and gas phase filtration section with activated carbon / impregnated media for removal of gaseous contaminants (VOC, SOx, NOx etc.), with antimicrobial treated filter media. Technical Requirements: • Suitable for 1000 / 2000 CFM (as per schedule). • Filtration efficiency as per relevant EN / ISO standards. • Initial pressure drop as per manufacturer’s standard design at rated airflow. • Filter depth minimum 350 mm. WELL Compliance Requirement: The filtration system shall be capable of supporting compliance with WELL Building Standard air quality performance requirements including particulate matter reduction (PM2.5, PM10) and reduction of gaseous contaminants (such as VOCs), as per project design criteria. Manufacturer shall submit third-party laboratory test reports as per relevant EN / ISO
2.2.1 | MR | 800-1000 CFM | Nos. | 0
2.2.2 | MR | 2000 CFM | Nos. | 0
2.2.3 | MR | 2100-3000 CFM | Nos. | 2 |  |  | 0 | 0
2.2.4 | MR | 5000 CFM | Nos. | 1 |  |  | 0 | 0
2.2.5 | MR | 6000 CFM | Nos. | 0
2.2.6 | MR | 8000 CFM | Nos. | 2 |  |  | 0 | 0
2.2.7 | MR | 12000 CFM | Nos. | 2 |  |  | 0 | 0
2.2.8 | MR | 17000 CFM | Nos. | 0
2.2.9 | MR | 20000 CFM | Nos. | 0
2010-02-02 | MR | 22500 CFM | Nos. | 0
2011-02-02 | MR | 25250 CFM | Nos. | 0
4 | MR | INLINE FANS
Supply, installation, testing & commissioning of Circular / Rectangular Inline Fans made out of galvanized steel. The impeller with backward blades shall be powered by 1/3 Ph. motor. The Rectangular Inline Fans shall be insulated with polyurethene foam having good sound absorbing & moisture resistance features. The motors shall be 1/3 Ph., 2 Pole. The fan & motor assembly shall be low noise.The fan shall be suitable for speed control by using a fan regulator.
Circular/Rectangle Inline Fan
4.1 | MR | 700 CFM at 20 mm Static | Nos. | 8 |  |  | 0 | 0
4.2 | MR | 300 CFM at 20 mm Static for Battery Ex. | Nos. | 1 |  |  | 0 | 0
5 | MR | AXIAL FAN
5.1 | MR | FRESH AIR FAN FOR PUMP ROOM
Supply, installation, testing & commissioning of Tube/Vane Axial Fan with impeller having adjustable pitch angle blades and complete with suitable motor & drive assembly. Motor shall also be suitable for Variable Speed drive. Motor shall be suitable for 415 ± 10% V, 3 Phase, 4 Wire, 50 ±5%Hz electrical supply. Motor shall be IP-55. Fans shall be AMCA Certified & listed for performance & sound power level (Vendor to confirm if the fan selection offered is certified for performance and sound or only for performance). The complete fan assembly alongwith the motor & drive assembly shall be fire rated i.e. suitable to operate upto 250°C for 2 hours and meet the duty parameters. Fans for high temp. application shall be UL or EN Certified in addition to AMCA certified & listed. Motor shall be IP55, class H insulation.The fan duty shall be :
Air Qty : 1400 CFM
Total Static Pressure : 30 mm Wg
Fan Speed : 2850rpm approx.
Fan motor : 0.75 KW approx.
Fan dia : 400mm approx.
Motor Efficiency Class: IE3* as per IEC 60034-30-1
Motors shall be TEFC, Squirrel cage induction motors, IP 55, Class F insulation
Noise Level : Not more than 78-80 dbA @ 3m distance
Minimum Total efficiency : not less than as per FEG-63 as per AMCA
Fan duty : Fresh Air Fans.
|  | Fan as described above | Set | 1 |  |  | 0 | 0
Note:Fan to have safety wire mesh screen on any exposed face.
5.2 | MR | EXHAUST AIR FAN FOR PUMP ROOM
Supply, installation, testing & commissioning of Tube/Vane Axial Fan with impeller having adjustable pitch angle blades and complete with suitable motor & drive assembly. Motor shall also be suitable for Variable Speed drive. Motor shall be suitable for 415 ± 10% V, 3 Phase, 4 Wire, 50 ±5%Hz electrical supply. Motor shall be IP-55. Fans shall be AMCA Certified & listed for performance & sound power level (Vendor to confirm if the fan selection offered is certified for performance and sound or only for performance). The complete fan assembly alongwith the motor & drive assembly shall be fire rated i.e. suitable to operate upto 250°C for 2 hours and meet the duty parameters. Fans for high temp. application shall be UL or EN Certified in addition to AMCA certified & listed. Motor shall be IP55, class H insulation.The fan duty shall be :
Air Qty : 1400 CFM
Total Static Pressure : 30 mm Wg
Fan Speed : 2850rpm approx.
Fan motor : 0.75 KW approx.
Fan dia : 400mm approx.
Motor Efficiency Class: IE3* as per IEC 60034-30-1
Motors shall be TEFC, Squirrel cage induction motors, IP 55, Class F insulation
Noise Level : Not more than 78-80 dbA @ 3m distance
Minimum Total efficiency : not less than as per FEG-63 as per AMCA
Fan duty : Fresh Air Fans.
|  | Fan as described above | Set | 1 |  |  | 0 | 0
Note:Fan to have safety wire mesh screen on any exposed face.
5.3 | MR | SMOKE EXHAUST AIR FAN FOR OFFICE
Supply, installation, testing & commissioning of Tube/Vane Axial Fan with impeller having adjustable pitch angle blades and complete with suitable motor & drive assembly. Motor shall also be suitable for Variable Speed drive. Motor shall be suitable for 415 ± 10% V, 3 Phase, 4 Wire, 50 ±5%Hz electrical supply. Motor shall be IP-55. Fans shall be AMCA Certified & listed for performance & sound power level (Vendor to confirm if the fan selection offered is certified for performance and sound or only for performance). The complete fan assembly alongwith the motor & drive assembly shall be fire rated i.e. suitable to operate upto 250°C for 2 hours and meet the duty parameters. Fans for high temp. application shall be UL or EN Certified in addition to AMCA certified & listed. Motor shall be IP55, class H insulation.The fan duty shall be :
5.3.1 | MR | Zone-1
Air Qty : 33700 CFM
Total Static Pressure : 30 mm Wg
Fan Speed : 1450rpm approx.
Fan motor : 15 KW approx.
Fan dia : 1120mm approx.
Motor Efficiency Class: IE2* as per IEC 60034-30-1
Motors shall be TEFC, Squirrel cage induction motors, IP 55, Class F insulation
Noise Level : Not more than 78-80 dbA @ 3m distance
Minimum Total efficiency : not less than as per FEG-63 as per AMCA
Fan duty : Fresh Air Fans.
|  | Fan as described above | Set | 1 |  |  | 0 | 0
Note:Fan to have safety wire mesh screen on any exposed face.
5.3.2 | MR | Zone-2
Air Qty : 31000 CFM
Total Static Pressure : 30 mm Wg
Fan Speed : 1450rpm approx.
Fan motor : 11 KW approx.
Fan dia : 1120mm approx.
Motor Efficiency Class: IE2* as per IEC 60034-30-1
Motors shall be TEFC, Squirrel cage induction motors, IP 55, Class F insulation
Noise Level : Not more than 78-80 dbA @ 3m distance
Minimum Total efficiency : not less than as per FEG-63 as per AMCA
Fan duty : Fresh Air Fans.
|  | Fan as described above | Set | 1 |  |  | 0 | 0
Note:Fan to have safety wire mesh screen on any exposed face.
6 | MR | DRY SCRUBBER UNIT COMPLETE WITH VFD PANEL
Supply, Installation, testing and commissioning of Double Skin Construction, floor mounted / ceiling suspended dry scrubber unit complete with backward curved direct driven SISW plug fan with 3 Phase, TEFC, Sq. cage induction motor suitable for 415V±10%V & 50Hz±3% electric supply. Motor shall be of high efficiency and shall be suitable for VFD operation. Fan impeller with motor shall be mounted in such as way that motor shall be out of hot air stream.
Scrubber shall be comprising of Electrostatic section made of 18 gauge galvanised sheet, high bake epoxy powder coated, washable type aluminium mesh filters, stainless steel spiked ionizers to create high voltage DC field, aluminum collector plates which should be alternatively charged positive and negative with large collecting area with 14" deep cell, to work as magnet for charged smoke and oil particles. Average efficiency of 90-95% in single pass as per ASHRAE test method. Electrostatic Precipitator should be able to charge particles from 0.01 micron to 10 microns through solid state power supply. Collector cell should be of permanent type and incorporate slide out facility for easy removal for cleaning. Power supplies shall be 100% solid state UL Listed, Module of capacity 3900 CFM & above shall be equipped with Pulse width modulating (PWM). The system should be fitted with interlock switch for safety .The units should be BMS compatible for Run, Wash, Fault feedback, dry contact point. The system should allow connection to a fan section to achieve 630 FPM velocity across the air cleaner. The units should be with Auto Wash system as per specification.
ESP shall be of 18G GSS powder coated cabinet. Electro-static Air cleaner shall be of Industrial Grade, which will collect dry & wet particles like dust, oil mist, cooking fumes & various pollutants.
Dry Scrubber shall have U.V. Ozone lamp fitted with electrostatic cell for odour removal.
2 layers rubber VI pads with GI Sheet in between dry scrubbers unit casing & foundation block for floor mounted unit.
In case of a Ceiling suspended dry scrubber, it shall be complete with mounting arrangement and spring isolator.
Fan shall be AMCA certified fan for performance & sound power level.
Motor Efficiency Class: IE3 as per IEC 60034-30-1
Motors shall be TEFC, IP55 rated & Class F Insulation.
Electrical Control Panel:
Short Circuit Fault with stand Capacity: 18KA
a. Dry Scrubber shall be complete with its electrical control panel made out of 1.2mm thick SS-306 steel enclosure. Suitable VFD for fan, power & control wiring & arrangement for ESP power supply with all safety interlocks. The ESP and fan shall trip immediately on opening of the door through a limit switch. And ESP cannot be turned on if fan is not running. But fan can run without ESP being 'ON'.
Incomer of Panel shall be 3P MPCB with S/C release of suitable rating & fault with stand capacity. 3 Pole aluminium bus bars of suitable rating, and out goings as 3P MPCB with S/C release of suitable capacity / rating as per KW / HP of scrubber fan motor & stater for scrubber fan & 3P MPCB / 3P MCB for 415V (2 Phase) / 230V (1 Phase) cast resin encapsulated control transformer of 'VA' capacity as per load of ESP modules & DP MCB & DC Power pack for ESP for converting 230V, 1 Phase to 'DC' supply for ESP.
Metering: VAF meter (110V)
Note: Only 3 Phase power, R,Y,B without neutral power supply shall be given to the electrical panel i.e. neutral shall not be provided. So necessary PT / CT cast resin type to be provided for control & power wiring and for power to ESP unit. PT shall be 415 √3 / 110 / √3 for R, Y, B phase indication lamps (63.5V), LED type & 110V VAF meter. Quote price shall be complete with sensor, pressure switch and other acccessies to modulate the VFD with respect to requirement of the cfm.
b. Control Panel may be kept nearby Dry Scrubber & necessary power cabling & earthing from panel to scrubber to be accounted for in this panel cost.
cost shall be inculsive of tempreture sensors, duct pressure sensor, Supply air humidity sensor. Etc.
The Dry Scrubber unit shall be offered for inspection at manufacturer’s works prior to dispatch. The inspection shall include verification of material specifications, fabrication quality, internal components, surface treatment, dimensional checks, performance parameters and compliance with approved technical submittals. Dispatch clearance shall be issued only after satisfactory inspection by the Engineer-in-Charge / Client’s representative. All arrangements for inspection including testing facilities, instruments and manpower shall be provided by the manufacturer without any extra cost.
The scrubber units shall be of following duty :
Air Qty Static Pr. (TSP) Approx. fan Floor / Ceiling in CFM in mmWg Motor HP suspended
6.1 | MR | 1300 65 mmWg 1.50 Ceiling suspended | Nos. | 2 |  |  | 0 | 0
6.2 | MR | 8300 65 mmWg 5.0 Floor Mounted | Nos. | 2 |  |  | 0 | 0
6.3 | MR | 18100 65 mmWg 15.0 Floor Mounted | Nos. | 2 |  |  | 0 | 0
7 | MR | Dirt Separator
Supply installation Testing and commissioning of Dirt separator In-line removal of dirt particles within chilled water system. The acceptable design shall incorporate a separating element to force water into tranquillity zones for dirt removal. A nozzle shall force cleans water into the main flow to divert contaminated water through the separating element. Dirt particles shall be removed via a blow down valve on the base of the vessel whilst ferrous particles down to 4 µm shall be captured by a magnetic device(25 Neodymium magnets) in the lower part of the vessel. It shall be able to provide up to 40% separation per cycle. It shall be able to remove at least 35% of 150 µm dirt particles per cycle. The magnet shall be retractable to enable ferrous particles to be released and discharged through the drain valve which will incorporate an internal scraper to dislodge particles that adhere to the inner surface of the vessel base.
Manufactured and designed In accordance with Pressure Equipment Directive 2014/68/EU. The cylindrical vessel shall be manufactured from welded steel. Material shall be EN/ISO: S235JR+N. Inlet and outlet of the unit shall be via horizontally-opposed, coaxial flanged connections in accordance with EN 1092-1 PN 10. Suitable for glycol solution up to 50%, Temperature range -10 C to 120 C. The maximum permissible flow velocity shall be 3 m/s. The Dirt Separator shall be sized appropriate to the maximum operating pressure and flow velocity of the system. Inlet and outlet of the unit (Dia- 150 mm).
7.1 |  | 432 USGPM (150mm Dia) | Nos. | 1 |  |  | 0 | 0
8 | MR | Dynamic pressurization unit with deareater
Supply, installation, testing & commissioning of pressurization system comprising pressure less expansion tank, pressurization pump, controls, piping’s & fittings and controller, skid mounted system. The pressurization unit shall have two Flow regulating, solenoid valve in spill lines with duty/standby/assist function to avoid pressure peaks in the system and a safety relief valve for protection of vessel, Constant speed centrifugal pump (orientation vertical/horizontal) with non-return valve. The use of electrically actuated ball valve in the spill line is not permitted since it takes time to react and increases pressure peaks which leads to malfunctioning of the system. In order for customer or OEM to remotely monitor & control operation, fault diagnosis related needs the unit must be equipped with cloud based wireless communication with such features. System pressure shall be regulated within ± 0.2 bar (2.9 psi) of the set pressure. Expansion pressurization and deaeration of the system to be provided by an integrated pump with pressure less expansion tank(s) The total Volume checked by vendor.
The whole system duly tested from factory conforming to international standards PED-2014/68/EU. The system shall consist of minimum following components & features: a) Twin Pressurization Unit c/w pumps(orientation verticle/horizontal), Flow regulator valve, solenoid valve in spill lines, Safety relief valve, Pressure sensor, Pipe fittings c/w Controller & display. b)Pressure less Expansion Tank 400 Liters c/w high quality butyl rubber bladder, rupture sensor, weight sensor, coalescing pall rings for active de- aeration, drain cock and adjustable feet for height adjustment, as unit is subject to atmospheric pressure, tank pressure rating should be 3 bar. Expansion Tank shall have third party certificate (TUV / lloyds registered). c) Flexible Connection: Flexible Connection must include a de-aeration sensor for signalling the controller to continue/stop the active de-aeration. d) Backflow Preventer c/w, water meter, ball valve and non-return valve, strainer/Particle filter/ and shut-off valve according to DIN 1988 and DIN EN 1717 in top up connection. e) Controller with display unit showing system content, system pressure and status of the main operating components in Realtime. top up function, flood limiter/shut down function in event of serious leak. In case of any fault controller shall display the fault code and generate the alarm.
8.1 |  | 400 Litres, Static Head = 6M | Nos. | 1 | 600000 | 50000 | 600000 | 50000
9 | MR | VACCUM DEGASSERS
Supply, installation, testing & commissioning of Vacuum Degasser/ Deaeration Unit to remove dissolved gases without boiling the water in the process, Deaeration to be performed by creating a vacuum with a frequency controlled pump. It should always automatically regulate the desired deaeration level of the system water and only deaerates as and when necessary (energy saving).The inbuilt sensors in the system should continuously measure the temperature and pressure in the system. The specially developed software supports the new technology of sensitive deaeration and offers greater insight into the water quality and system performance and have a interactive display for the same. it shall comply with machinery directive 2006/42/EC, PED 2014/68/EU, Low Voltage Directive 2014/35/EU and EMC Directive 2014/30/EU.
Vacuum degasser Eco-300 shall be capable of degas given system volume at System operating Pressure. Connections: Inlet- 25.4mm , Outlet -12.7mm. Minimum deaeration: 15 ml/l. Standard deaeration: 12 ml/l. Maximum deaeration: 8 ml/l (as per VDI 2035 and 4708). Supply voltage (V): 1 ~ 230. Maximum noise production (dB): 55. system operating pressure should be 0.6 - 2.7 bar. Degasser System shall consist of following main components: i) Bleeding device with gas detector ii) Pressure sensor. iii) Frequency controlled pump. iv) Rugged enclosure. v)Controller with Interactive display giving real-time insight into the deaeration performance and the quality of the system water, intuitive operation. And other necessary components as per requirement.
9.1 |  | Static Head = 6M (ECO_300) | Nos. | 1 |  |  | 0 | 0
10 | MR | CHILLED WATER TYPE PRECISION AC UNITS (pac
Supply, Installation, Testing and Commissioning of CW type packaged airconditioning units, self contained floor mounted with bottom/Top discharge type complete with inbuilt 2 way PICV, fan section with statically & dynamically balanced centrifugal backward curved plug type fan driven by Electronically Commutated (EC) motor having true soft start characteristics, multirows deep hydrophilic coated slant type cooling coil with copper tubes and aluminium fins. The cabinet Shall be provided with double skin panels on all sides with inner panel of minimum thickness of 0.8mm and outer panel of thickness of 1.0mm and fabricated out of heavy gauge steel sheets with minimum 19mm thick Rockwool insulation sandwitched in between. The enclosure shall be factory painted to a smooth finish and shall be supported on a fabricated steel structure.
The unit shall be equipped with high efficiency HDPE washable filters of Merv 8 efficiency, SS drain pan duly insulated with 9mm thick Class "O" closed cell insulation, micro- processor based programmable logic controller, Steam Electrode humidifier, strip type heaters, thermostat, water detection kit for water spillage under the false floor all complete in a unit as per the specifications. The enclosure shall be factory painted to a smooth finish. Unit should be suitable for automatic fan speed variation based on inside conditions achieved to affect more power saving. The precision unit shall also be complete with microprocessor based electrical panel comprising of indication lights, Star-delta/DOL starter,over load protection, necessary relay to be hooked-up with fire & smoke detection system to facilitate auto trip of precision unit and necessary copper control wiring. The packaged units shall be complete with auto sequencing, power loss auto sequencing arrangement, alarm, clogged filter alarm.as required. Each unit shall be provided with BMS integration card & master card to communicate all relevant data with BMS.(Applicable in the event BMS is there). The PAC units shall be suitable for operation on 400 ±5% volts, 50 Hz three phase AC power supply. Fan outlet velocity shall not exceed 300 MPM.
Chilled Water In : 6.66°C
Chilled Water Out : 13.33°C
Return air Temp 27 ± 1 Deg C / 50 ± 5 % RH ;
Type of Discharge : Bottom dischagre with fan section below false floor( False floor height should be 600 mm)
The indoor unit shall also have heater & humidifier.
The external static pressure of fan shall not be less than 20mm Wg.
The controller of the unit shall be intelligent.
The controller shall also after auto sequential operation of Precision AC Units.
The unit shall be complete with motorised damper on suction side.
PR.AC shall have atleast two dry contacts for remote alarms.
10.1 |  | 11.50 TR Actual Capacity (7400 CFM) ( Chilled Water Microprocessor units SERVER ROOM (4W+1S) BOTTOM DISCHARGE | Set | 5 |  |  | 0 | 0
10.2 |  | 9.5 TR Actual Capacity (5700 CFM) ( Chilled Water Microprocessor units - UPS ROOM (3W+1S) TOP DISCHARGE | Set | 4 |  |  | 0 | 0
Notes:
1. Water connection shall be provided at one point with in 5m in the room. The entire onward piping upto the machines shall be done by other agency.
2. Drain piping with insulation and connection upto 10 M the nearest drain point in the room shall be included. The drain piping shall be of 25mm dia GI 'B' Class duly insulated with 9mm thick nitrile rubber.
3. Necessary mounting stands for indoor units also to be included in the scope of works.
4. Cost shall also include lifting, shifting and positioning to site as per site requirement and height of floor in the building.
5. Each unit should have a inbuilt card for Bacnet/Modbus output for BMS monitoring.
6. The unit shall have water leak detection sensing tape with alarm initiation system, on detection of water leakage under the machine in the vicinity.
7. The unit shall have a feature to trip off automaticaly in the event of receiving a fire signal from the fire detection system. The necessary cabling between the fire relay control module with in the space/ room and the unit's controller shall be considered in the scope of work and supply.
8.The indoor unit shall be with drain pump kit having lift head 3.5 mtr approx.
9. Factory Inspection scope to be added in the BOQ, considering representation from Consultant, PMC & Client.
10. Factory Acceptance Test, Site Acceptance test, Load Test at site with dummy load needs to be added to the scope of Supplier.
11. Themo Loggers required as per site rquirement as the Load test.
12. 110% capacity load bank for PAC testing to be arranged properly in accordance with safety standard requirement at the site during load test.
13.Associated cable of appropriate size for load bank testing
14. Battery operated tool/ Vaccum cleaners / Vaccum Pump to be used at the time of PAC's installation.
15. Ensuring proper handover and trainings for the ops team post testing commissioning with load analysis report and capturing load test parameters duly signed /reviewed by all project team stake holders.
16. Ensuring factory and site testing as per method statement suggested by Engineering consultant.
17. PAC Vendor to ensure proper plumbing connection to Dehumidifier unit.
18. Testing, commissioning with load analysis report & load parameters shall be signed by project team.
19. Factory and site testing method shall be as per engineering consultant.
20. Bidder to study the enclosed layouts and confirm suitability of space/ size as shown.
21. Cost to include visit to OEM factory before delivery of materials at site for a FAT, process and quality inspection of the proposed materials in the tender under this head for 3 persons from user / project manager / designer firm.
10.3 | MR | MISCELLANEOUS
Supply, installation, testing & commissioning of ADVANCED AIR TERMINAL DISTRIBUTION (Supply Air Floor Grilles) COMPRISING OF :
Top Cover, GI Powder Coated with perforations to deliver airflow of 1100 CFM, with aerofoil aluminium damper , suitable to take the load of the rack upto 800kgs per tile of size 595mmX595mm, provision for fitment and operation of microprocessor controller with display. Actuator to modulate the vanes from 0 to 100% to take feed back from the sensors. Microprocessor controller or PLC based interface with programmable control logic protocol , including two sensors to modulate the airflow from 0 to 100% based on the rack temperature and regulating the right amount of air volume. The average of both sensors to be input for actual conditions to the control logic. Display to be setable for temperature, communication on modbus to be available.
Neck Size Overall Size
2010-03-01 |  | ADVANCED AIR TERMINAL DISTRIBUTION (Supply Air Floor Grilles) '595mm x595mm 600mm x 600mm | Nos. | 30 |  |  | 0 | 0
10.4 |  | Supply, installation, testing & commissioning of COLD AISLE CONTAINMENT:
2010-04-01 | MR | Cold Aisle Containment Door : The door fame should be of Aluminium / GI Frame powder coated or Anodized having 4 mm thick Fire retardant Transparent sheets with 90 % approx Viewable area. The door should be equipped with necessary fittings and lock. | Nos | 1 |  |  | 0 | 0
2010-04-02 | MR | Cold Aisle Containment Top Panel : Customized Fire Retardant Rigid UL V- 0 Plastic 3 mm sheet cut in accordance to the rack for the said cold aisle enclosure with support taken from the actual /false ceiling . Transparency high. | Sqm | 15 |  |  | 0 | 0
11 |  | Air Purification Unit For Server Room
| MR | Supply, Installation, Testing & Commissioning of Air Purification Unit preloaded with minimum, 01 No Pre-Filter, 04 No Honeycomb Chemical Filters (flat-bed type), 01 No After Filter and One No. Final-Filter and all associated accessories etc. Air Purification System should be capable to deliver constant ‘clean’ air output in server room of dimensions 10 Meters x 9 Meters x 3.81 Meters (LxWxH)
11.1 | MR | 1000 CFM | Nos. | 1 |  |  | 0 | 0
11.2 | MR | 500 CFM | Nos. | 1 |  |  | 0 | 0
12 | MR | Astronomical timer-cum-controller
|  | Supply, installation, testing & commissioning of Astronomical timer-cum- controller with NO/NC contact and suitable relays complete in all respect, for auto-controlling Inline Fan operation. (for Battery Room). (Logic:10 min operation every 1 hour) | Nos. | 2 |  |  | 0 | 0
13 | MR | Hydrogen Sensor for battery room
|  | Supply,installation,testing and commissioning of Flameproof/ Explosionproof Hydrogen detector with SPDT Relay. Sensor should be complete with connection post for BMS and Astronomical time cum controller to efficient operation. | Nos. | 1 |  |  | 0 | 0
14 | MR | Sequential controller
|  | Supply,installation,testing and commissioning of Sequential Controller for controlling Split Unit and ventilation fan. The controller shall ensure cyclic operation of AC units. It shall also have inbuilt temperature sensor & temperature display. | Nos. | 17 |  |  | 0 | 0
15 |  | BTU Meter
Supply, installation, testing and commissioning of Ultrasonic type flow meters (BTU Meter) with in-built display including the provision for installing the meter in the chilled water pipe line with with suitable flanges and fittings with Thermowell temperature sensors. Meter shall be suitable for single phase AC power supply. The BTU hour meters shall be insulated in such a manner so that the display is not covered. The BTU meter shall have its own integrator and interconnected control wiring between the BTU meter and integrator. Suitable no of repeaters shall be provided in the cost of BTU meter only. The meter will have low maintenance and high accuracy. Can operate in cooling as well heating mode shall be suitable for system integration with Mod bus module for centralised data logging. Canopy to be considered for display of BTU meters if installed on the terrace.The meter shall be suitable for following pipes sizes:
Dia in mm NB
15.1 | MR | 125 mm dia | Nos. | 1 |  |  | 0 | 0
15.2 | MR | 100 mm dia | Nos. | 0
15.3 | MR | 80 mm dia | Nos. | 0
15.4 | MR | 65 mm dia | Nos. | 0
15.5 | MR | 50 mm dia | Nos. | 0
15.6 | MR | 40 mm dia | Nos. | 0
15.7 | MR | 32 mm dia | Nos. | 7 |  |  | 0 | 0
15.8 | MR | 25 mm dia | Nos. | 0
17 | MR | PUSH BUTTONS
17.1 | MR | Stay-Put Type ON/OFF Push Buttons in a Hinge Box. (150mm x 150mm size) - in IP-rated Outdoor-type Weather-proof enclosure. OFF push button shall be in a Lockable-type 2 hour / 250 deg. C Fire Rated Enclosure. | Nos. | 54 |  |  | 0 | 0
17.2 | MR | Stay-Put Type OFF Push Buttons in a Hinge Box. (150mm x 150mm size) - in IP-rated Outdoor-type Weather-proof enclosure. OFF push button shall be in a Lockable-type 2 hour / 250 deg. C Fire Rated Enclosure. | Nos. | 2 |  |  | 0 | 0
| 28.5 | CABLING & WIRING
18 | 2028-05-01 | Supplying & laying of 2x1.5 sqmm fire survival armoured cable, 600/1000V rated with annealed copper conductor having glass mica fire barrier tape covered by an extruded layer of Cross Linkable Ethylene Propylene Rubber (EPR) insulation and LSZH inner bedding, steel wire armouring & LSZH outer sheath complete as required. | RM | 4200 |  |  | 0 | 0
TOTAL CARRIED OVER TO SUMMARY
B HEAD D |  | CHILLERS
1 | 33.3 | AIR COOLED SCROLL CHILLERS WITH VFD
Supplying, installation, testing and commissioning of following capacity Air- Cooled, Scroll Chiller package complete with VFD (Variable Frequency Drive), hermetic / semi hermetic, multiple scroll type compressors each with step less capacity control of 25 % to 100 % of the rated capacity, with microprocessor based control panel, motor, starter panel (VFD), machine mounted, air- cooled condensers, factory fitted chiller insulation, water flow switch , vibration spring Isolators, victaulic couplings, integral refrigerant piping and wiring with single/ two circuits, automatic and safety controls mounted in central console panel and all mounted on a steel frame (complete as per specifications) i/c suitable foundation/mounting structure made of RCC/MS Structure i/c anticorosive paint, anti vibration pad, power control cable and connection inter connection etc. as per design approved by engineer-in-charge. Motor shall be suitable for 415±10% 50 cycles. 3 phase AC supply. Refrigerant gas used shall be R- 32/R454B/R134A/R410 or GWP refrigerant.
The chiller shall be Building Management System (BMS)compatible. The system shall be in confirmation to IS :16590 and CPWD Specification as amended upto date. BEE Star labeling and CPWD Specification as amended upto date and tested as per IS 16590.
Chilled water Leaving Temp. (6.67°C)
Chilled water Entering Temp. (12.2°C)
Evaporator fouling factor = 0.018 m²°C/kW
Condenser air entering temp. : As per Site Dry Bulb Temperature
Suitable for Seismic Zone and Altitude as per location/site. Microprocessor based controller.
Note: Cost to include visit to OEM factory before delivery of materials at site for a FAT, process and quality inspection of the proposed materials in the tender under this head for 3 persons from user / project manager / designer firm.
1.1 | 2033-03-02 | 51 TR - 70 TR BEE 4 Star Rated (Actual Capacity 4 Nos. x 60 TR (3W+1S)) | per TR | 240 |  |  | 0 | 0
2 | MR | CHILLER PLANT OPTIMIZER
Design, Supply, installation, testing & commissioning of BTL-listed CHILLER PLANT OPTIMIZER (CPO) in 16G powder coated, lockable sheet steel enclosure. It must combine Bacnet listed 32 bit Supervisory controllers, IO CARDS (with accessories like Transformer, MCB, internal wiring and Relays with bases), Bacnet listed 32 bit DDC/IOM controllers for equipment control along with Chiller plant optimization software and logic. It should be capable to monitor, operate and generate reports from remote location. It should possess 3 tier architecture combination of hardware and software and also must include advance graphics for easy storage (min. 12 months) and report generation.
(A) Multi user with simultaneous minimum 5 user login facility, (B) Unlimited user without additional licence, (C) Shall be browsed by Microsoft Internet Exlporer and Netscape Navigator, (D) BTL certified, (E) Web engine should be 32bit configuration, (F) Should have inbuilt display and keys to operate in absence of PC, (G) Should have inbuilt IO points, (H) Functionally able to act as a DDC controller also apart from Supervisory controller function, (I) Web engine should support ASHRAE standard BACnet MS/TP protocol, Proprietry Protocol shall not be accepted. Interface for software integration on Chiller on N2/BACnet MS/TP protocol. (J) Web engine should support integration of third party protocol (eg MODbus-RTU) seemlessly without adding additional hardware, (K) Web engine should support DHCP function for IP addressing
Chiller plant manager shall essentially be able to perform the following functions :
Chillers start and stop operation.
Chillers auto sequencing.
Optimizing chillers operation with optimization software and logic.
Auto start and stop of condenser water pumps.
Auto start and stop of chilled water pumps.
On and off operation of motorised butterfly valves at chiller outlet, at condenser outlet.
Having capability for Software integration with secondary chilled water pumps panel.
Having capability to monitor, operate and generate reports from remote location.
Load Management and Optimization to ensure maximum performance and energy efficiency using Artificial Intelligence and Machine Learning. The CPO should be able to define the most energy efficient operation of the complete plant by capping the max. IKW/TR.
Wiring Standard
2C x 1.0Sqmm, 1.1 KV grade PVC Insulated, stranded copper conductor, Lead Free armoured FRLS with all accessories for field devices.
3C x 1.5Sqmm, 1.1 KV grade PVC Insulated, stranded copper conductor, Lead Free armoured FRLS cable with all accessories for Powering DDC, Actuators etc.
3Cx 1.0Sqmm, 1.1 KV grade PVC Insulated, stranded copper conductor, Lead Free armoured, FRLS twisted (14 ~ 16 twists per mtr) cable, for communication. With all accessories. 3rd core shall be used for shielding.
PVC insulated, Twisted Pair, tinned copper conductor CAT-6 cables for BMS / CPO Network. Armoured FRLS as per relevant IS standard.
2C x 1.0Sqmm, 1.1 KV grade PVC Insulated, stranded flexible copper conductor, un-armoured FRLS wire for Field devices, last mile connectivity.
All sensors / field devices as per specifications.
All wiring in necessary heavy-duty GI conduiting complete with bends & junction boxes etc.
UPS of suitable capacity with 10min battery back-up
|  | Chiller Plant Optimizer as described above and suitable for 15% additional points over the IO summary as enclosed. | Sets | 1 |  |  | 0 | 0
Note: Cost to include visit to OEM factory before delivery of materials at site for a FAT, process and quality inspection of the proposed materials in the tender under this head for 3 persons from user / project manager / designer firm.
TOTAL CARRIED OVER TO SUMMARY
B HEAD E |  | AHU, FCU & TFA
1 | 35.1 | CEILING SUSPENDED AHU
Supplying, Installation, testing and commissioning of Factory built ceiling suspended chilled water double skin type horizontal/vertical air handling units of following capacity, made of 25mm thick panels consisting of pre plasticized G.I. casing of thickness 0.8mm outside layer and 0.8 mm inside layer with Polyurethane Foam (PUF) insulation factory injected between them by injection moulding machine, complete with blower section with blower suitable for static pressure as required, minimum 2 bend PVC eliminators, cooling coil section with aluminium finned copper tubes (tubes thickness not less than 0.5mm) cooling coil of 4 row deep, filter section with 50mm thick metal viscous/ washable synthetic type air prefilters, belt drive package with Totally Enclosed Fan Cooled (TEFC) drive motor of efficiency class IE3 suitable for 415 ± 10% volts, 50Hz, 3 Phase AC supply suitably designed for Variable Frequency Drive (VFD) applications, drain connections, stainless steel (18G) drain pan with PUF insulation, 150 mm dia. dial type pressure gauges (2 nos.)and industrial type thermometres (2 nos.) at the inlet and outlet of coil, auto purge valve wherever required, necessary vibration Isolation arrangement, noise level shall not exceed 70 dB. AHU shall be AHRI/Eurovent certified, fan shall be AMCA certified etc. Complete as per CPWD specification/drawings and as directed by Engineer-in-Charge. (Total static pressure considered is 50 mm WG).
1.1 | 2035-01-01 | 1000 CFM | Each | 1 |  |  | 0 | 0
1.2 | 2035-01-02 | 1600 CFM | Each | 3 |  |  | 0 | 0
1.3 | 2035-01-03 | 2000 CFM | Each | 1 |  |  | 0 | 0
1.4 | 2035-01-04 | 2500 CFM | Each | 6 |  |  | 0 | 0
1.5 | 2035-01-05 | 3000 CFM | Each | 22 |  |  | 0 | 0
1.6 | 2035-01-06 | 4000 CFM | Each | 2 |  |  | 0 | 0
1.7 | 2035-01-07 | 5000 CFM | Each | 2 |  |  | 0 | 0
1.8 | 2035-01-08 | 6000 CFM | Each | 0
2 | MR | TFA AIR HANDLING UNIT'S (AHU) - OUTDOOR/INDOOR, FLOOR MOUNTED -- THERMAL BREAK DESIGN - WITH BACKWARD CURVED DIDW CENTRIFUGAL FAN
MOUNTED, sectionalized construction, draw through type, THERMAL BREAK DESIGN air handling unit (AHU) as per specifications & complete with the following: 1-Construction Features: Double Skin Sandwich Panel: 48±2mm thick with PUF 40 kg / m². Sheet Thickness: Outer sheet: 1.0mm pre-coated plasticized galvanized steel & Inner sheet: 0.8mm plain galvanized sheet. Condensate drain: 18G SS 304 sheet with insulation. Copper Coil with Aluminium Fins: Coil thickness 0.5mm,12FPI & AHRI certified for performance. 1A. Intake Dampers& Louvres Fresh Air intake section with Bird Screen, Intake Louvers and manual * volume control dampers , complete assembly in Aluminium construction.(Indoor installed TFA unit will not have bird screen and intake louvres.) • With Manual Damper* 2-Air Filteration in Fresh air* : a. Pre-filter section with MERV-8 filters.(Synthetic media pre-filter, 90% down to 10 microns) 3-AHU with marine light, door limit switch and door interlock.
d. Motor Effeciency shall be as per ECBC 2017: ECBC+: IE3 Fan’s mechanical efficiency: not less than 70% for Backward curved fans. e.Fan & motor shall be mounted on a common base frame with motor sliding rails & complete base frame mounted on the AHU casing with vibration isolation spring isolators. f.Providing Local Power Isolator in a weather proof enclosure, single isolator for DOL & VFD based motor and two isolators in Star-Delta based motor. Notes: a.2 layers rubber VI pads with GI Sheet in between AHU casing & foundation block. b. Fan Outlet velocity: Not Exceeding 9.2 m/s. c. Noise Level: Not Exceeding 68-70 db @1m distance from AHU. d.Coil Working pressure* = 150 PSI/10kg/cm²/PN10*
The AHU selection shall be :
CFM TSP TR Cooling Approx. mmWg Coil Motor (Row) (KW)
2.1 | MR | 4000 80 22.5 8 3.7 | Nos. | 2 |  |  | 0 | 0
2.2 | MR | 2800 80 22.5 8 1.5 | Nos. | 2 |  |  | 0 | 0
2.3 | MR | 1100 80 22.5 8 1.1 | Nos. | 1 |  |  | 0 | 0
Note:
1. Contractor / Equipment manufacturer to calculate total static pressure (TSP) in mm Wg by adding ESP & internal static pressure of the unit. TSP selected should be such that under all operating conditions, the designed ESP & CFM (duty parameter) is delivered.
2.Necessary civil work such as plinth / foundation / base for AHU mounting is excluded from scope of work.
3 | MR | TFA AIR HANDLING UNIT'S (AHU) WITHOUT COOLING COIL
MOUNTED, Sectionalized construction, outdoor construction, Ventilation Unit as per specifications and complete with the following: a.Fan section with DIDW Centrifugal fan, high efficiency fan, Forward Curved blower with fire retardant canvass connection at fan inlet. AMCA Certified & listed for performance & sound power level. Fan shall be as per FEG-71 Grade as per AMCA. b. Intake Dampers& Louvres Fresh Air intake section with Bird Screen, Intake Louvers and manual * volume control dampers , complete assembly in Aluminium construction.(Indoor installed TFA unit will not have bird screen and intake louvres.) • With Manual Damper* c-Air Filteration in Fresh air* : a. Pre-filter section with MERV-8 filters.(Synthetic media pre-filter, 90% down to 10 microns) d.High efficiency 'IE3' squirrel cage induction motor suitable for 415±10% volts, 50±5%Hz, 3 phase AC supply. Motor shall be suitable for VFD operation. It shall be complete with V-Belt drive package. Motor Effeciency Class: IE3* as per IEC 60034-30-1 e.Fan & motors shall be mounted on a common base frame with motor sliding rails & complete base frame mounted on the Ventilation Unit casing
CFM TSP Approx. mmWg Motor (KW)
3.1 |  | 2600 65 1.5 | Nos. | 1 |  |  | 0 | 0
4 | MR | Cabinet Fan For
MOUNTED, Sectionalized construction, outdoor construction, Ventilation Unit as per specifications and complete with the following: a.Fan section with DIDW Centrifugal fan, high efficiency fan, Forward Curved blower with fire retardant canvass connection at fan inlet. AMCA Certified & listed for performance & sound power level. Fan shall be as per FEG-71 Grade as per AMCA. b. Intake Dampers& Louvres Fresh Air intake section with Bird Screen, Intake Louvers and manual * volume control dampers , complete assembly in Aluminium construction.(Indoor installed TFA unit will not have bird screen and intake louvres.) • With Manual Damper* c-Air Filteration in Fresh air* : a. Pre-filter section with MERV-8 filters.(Synthetic media pre-filter, 90% down to 10 microns) d.High efficiency 'IE3' squirrel cage induction motor suitable for 415±10% volts, 50±5%Hz, 3 phase AC supply. Motor shall be suitable for VFD operation. It shall be complete with V-Belt drive package. Motor Effeciency Class: IE3* as per IEC 60034-30-1 e.Fan & motors shall be mounted on a common base frame with motor sliding rails & complete base frame mounted on the Ventilation Unit casing
CFM TSP Approx. mmWg Motor (KW)
Centralized pantry Exhaust
4.1 |  | 3300 40 1.1 | Nos. | 1 |  |  | 0 | 0
Toilet Exhaust
4.2 |  | 2300 40 0.75 | Nos. | 1 |  |  | 0 | 0
4.3 |  | 800 40 0.75 | Nos. | 1 |  |  | 0 | 0
4.4 |  | 700 40 0.75 | Nos. | 1 |  |  | 0 | 0
5 | 35.4 | HIGH WALL FAN COIL UNIT
Supplying, installation ,testing and commissioning of High wall Fan Coil Unit comprising of two 2 rows deep chilled water cooling coil, centrifugal blowers, fractional horsepower (FHP) motor , synthetic fibre filters, insulated & extended condensate drain pan, casing, coil piping connections, condensate drain piping connections & wiring. Fan coil units shall be suitable for operation on 220 + 10% Volts, 50Hz, single phase power supply of following sizes & capacities. Complete as per CPWD specification and as directed by Engineer-in-charge.
5.1 | 2035-04-01 | 2.0 TR nominal capacity with 800 Cfm air quantity. (400 CFM, 0.9 TR) | Each | 4 |  |  | 0 | 0
5.2 | 2035-04-02 | 1.5 TR nominal capacity with 600 Cfm air quantity. (841 CFM, 2.3 TR) | Each | 2 |  |  | 0 | 0
5.3 | 2035-04-03 | 1.0 TR nominal capacity with 400 Cfm air quantity. (989 CFM 2.9 TR) | Each | 2 |  |  | 0 | 0
6 | MR | DRAIN PUMP
6.1 | MR | Supply, Installation, Testing & Commissioning of On Line Type Condensate drain pump for Hi-wall units complete with water level sensor and accessories as required. Quoted price shall be inclusive of controller, NRVs & water sensors and associated wiring etc. to make installation complete. Drain Pump shall be suitable for operation on 220+6 % volts 50 Hz, 1phase AC power supply.(head 1meter) | Nos. | 11 |  |  | 0 | 0
TOTAL CARRIED OVER TO SUMMARY
B HEAD F |  | EVAPORATIVE COOLING - AIR WASHER
1 | 36.1 | EVAPORATIVE COOLING - AIR WASHER
Supplying, Installation, Testing and Commissioning of factory assembled double skin central evaporative cooling plant having following specifications. a. Air washer section comprising 50 mm thick pre-air filter made out from washable Aluminium wire mesh filter with 90 % down to 10 microns. b. Humidification section comprising of Wet pads 200 mm thick impregnated cellulose paper media (Celdec pads) with two (2) bend PVC eliminator, internal casing with blank off's of wet section In SS-304 construction.
c. Fan Section comprising of belt driven, Double Inlet Double Width (DIDW) backward curved fan with outlet velocity less than or equal to 10 m/s and minimum efficiency of 70% Air Movement & Control Association International (AMCA) certified centrifugal fan suitable for required cfm at 50 mm WC static pressure.
d. Totally Enclosed Fan Cooled (TEFC) motor of IE-3 class as required with pulley, belt.
e. The unit shall be fabricated with frame work hollow extruded aluminium profile with 0.80 mm precoated GSS on outside and on inside complete with 25 mm thick Chloroflouro Carbon (CFC) free Polyurthane Frame (PUF) insulation of minimum 40 kg/cum density sandwiched in between inner and outer skins, SS -304 (18 SWG) Sump tank, 25mm C-PVC piping, make up, drain & quick fill and drain connection, Butterfly/Gate valves for pumps, make up, drain & quick fill and drain connections of sump, 2 no. Pumps of suitable capacity and necessary fittings, stand, anti vibration pads etc.as required.
f. Starter panel DOL/Star-Delta suitable for operation of Blower motor & pump made out of 1.6 mm thick sheet steel powder coated enclosure comprising of over load protection relay, short circuit & single phasing protection, ON / OFF push buttons, ammeter, voltmeter, indicating lamps, MCB, contactor etc. (As per Specification of CPWD & direction of Engineer- in -charge) complete in all respect
g. All as per pre approved by Engineer- in-charge.
1.1 | 2036-01-01 | 4300 CFM Say 5000 CFM | Each | 2 |  |  | 0 | 0
1.1 | 2036-01-04 | 12200 CFM | Each | 2 |  |  | 0 | 0
TOTAL CARRIED OVER TO SUMMARY
B HEAD G |  | HI - WALL SPLIT SYSTEMS
1 | 32.2 | HI - WALL SPLIT SYSTEMS
Supplying , Installation, Testing and Commissioning of Air Cooled Hi Wall split type Air conditioners complete with Indoor unit(IDU), Out door unit (ODU), surface / concealed copper Refrigerant piping with insulation (closed cell elastomeric nitrile rubber tubular pipe section) upto 3 Mtr (IDU to ODU), copper power cable upto 3.5 Mtr (IDU to ODU) i/c drain pipe R- 32/R-410/ R-407 Green Refrigerant, wireless Remote control, suitable for working between 180- 260V with low & high voltage cutoff and 50 hz ,1 phase AC supply capable of performing cooling, dehumidification, air circulation of following capacity with Scroll / rotary compressor. The system shall be able to deliver 100% of the rated capacity upto 42 0C. Min 5 year Original 242 DELHI SCHEDULE OF RATES (E&M)-2025 Equipment Manufacturer (OEM) warranty both compressor and Printed Circuit Board (PCB). Must comply : Electrical cable IS 694 or IS 9968 temperature sensing control IS /International Electrotechnical Commission (IEC) 60730, hermetic compressor IS 10617, heat exchanger IS 11329, capacitor IS 2993 and motor IS 12615. Complete as per CPWD specification and IS : 1391 Part II 2023. The system shall be able to operate up to 50 0C (out door ambient temperature).
1.1 | 2032-02-02 | 1.0 TR with 5 Star BEE Rating | Each | 2 |  |  | 0 | 0
TOTAL CARRIED OVER TO SUMMARY
B HEAD H |  | BMS (BUILDING MANAGEMENT SYSTEM)
Design, Supply, Installation, Testing, Commissioning & Handing over the Building Management System (BMS) and allied systems as per specifications as below.
1 |  | BMS Workstation and IT Components
1.1 | 42.1 | CENTRAL CONTROL SERVER
|  | Supplying Installation Testing Commissioning of Central Control Server System comprising of Intel®Xeon® CPU E5-2640 x64 (or better) compatible with dual and quad core processors, Windows 11 (Professional, Enterprise, Ultimate, 64 bit), Windows Server 2013 R2 (Standard, Enterprise, 64 bit) 16 GB or more, Video card and monitor capable of displaying at 1024 x 768 resolution or better, Latest Microsoft Licence Version Operating System Loaded with MS OFFICE 2019 Professional, Word, EXCEL, Power Point, Outlook Express, Microsoft Team official version lifetime licences suitable for running BMS software complete etc. as required. | Each | 1 |  |  | 0 | 0
| 42.2 | PC System
|  | Supplying Installation Testing Commissioning of Client PC System comprising of PC Hardware with minimum11th Gen Intel® I7 processor CPU E5-2640 x64 (or better), compatible with dual and quad core processors minimum 3.1 Ghz and 8GB or higher RAM, Hard Drive Space of 256 GB SSD or better, Video card and monitor capable of 1920 x 1080 pixel resolution or better with Ethernet adapter (10/100/1000 Mbps with RJ-45 connector) with 2 GB or higher Graphics card suitable for BMS System complete etc. as required. | Each | 1 |  |  | 0 | 0
1.2 | 42.4 | LED Display Supplying, Installation, Testing and Commissioning of following size LED display (LED monitor) industrial grade with 3840x2160 resolution or better, USB playback, bluetooth and miracast connectivity, 4X HDMI 2.0, DP 1.2, HDR 10/10+, brightness: 500-nits or better, Video wall mode should be available, contrast ratio: 1200:1, OPS slot, viewing angle (H/V): 170°/ 170°, response time less than 12ms, Display control shall be on monitor screen and programmable with remote (remote shall be supplied with system), Key Board, Optical Mouse, etc. as required.
1.3 | 42.6 | Touchscreen Color portable operator terminal Supplying Installation Testing Commissioning of following sizes Touchscreen Color portable operator terminal capable of connecting to one of the controllers on the communication bus and view parameters of the complete system. The terminal should be capable of viewing /changing parameters and trends, the specified parameters as per requirement etc. as required.
| 2042-06-02 | 7" Touch screen | Each | 1 |  |  | 0 | 0
1.4 | 26.2 | Supplying, installation, Testing & Commissioning of following capacity at full load (Unity Power Factor) ON LINE Uninterrupted Power Supply (UPS) system suitable for Single Phase input, Single Phase output AC Supply. The UPS shall include a Rectifier, inverter, battery bank suitable for 30 minutes back up (Battery VAH capacity shall not be less than 1600 VAH per KVA of UPS rating per Hour backup time) on full load (Battery shall be VRLA, SMF in ABS Container) and Static Bypass switch along with provision for manual bypass, suitable isolation transformer for additional protection against neutral faults etc. The UPS systems shall be Microprocessor based Digital Control, using Insulated Gate Bipolar Transistor (IGBT)'s both for the rectifier & inverter with PWM (Pulse Width Modulation) Technology. The quality of design, manufacturing and inspection process should confirm to the relevant Inter-national standards such as IEC/EN/VDE. The operating efficiency of the UPS systems shall be >95% at 100% non-linear loads. Current total harmonic distortion(ITHD)/ total demand distortion (TDD) on the input grid shall be < 5% at 100 %load. (The required LC filters shall be included in UPS cost), extreme power factor kit to be include to limit the input pf to 0.99 and output power factor shall be unity (i.e. kw rating of the UPS shall be kva rating x 1 ) however UPS shall be suitable to take load at 0.7 laging to 0.7 leading power factor loads. UPS shall be suitable for incoming supply AC single
| 2026-01-03 | 6 KVA | Each | 1 |  |  | 0 | 0
1.5 | 39.3 | port Layer 2 indoor Network Switch having features and specifications etc. as mentioned here under: At least 24 X RJ-45 Gigabit Ethernet Ports and additional 2 X 10G Base -T with 4 X SFP Ports with non-blocking architecture by having Switching capacity of min. 168Gbps and packet forwarding rate of 125Mpps or higher, 16K MAC table. Console Port, USB port, Stacking support of min. 8 units per stack. Internal dual AC Power supply, STP, RSTP, MSTP, BPDU Filter, BPDU Restriction, Min. 9K Jumbo Frame, LBD, IGMP Snooping V1/V2/V3, MLD Snopping V1/V2. IGMP /MLD Groups 1K or more, IPv4/IPv6 Loopback Interface, 16 L3 IP Interface, Ipv6 ND, VRRPv3, UDP Helper, ECMP. VLAN: 802.1Ǫ, Port based, Ǫ-in-Ǫ, Multicast VLAN, Protocol VLAN, VLAN Trunking, DHCP Snopping, Server, server Screening. RADIUS , TACACS+ Authentication, ǪoS: 802.1P, 8 queues per port, ǪoS : WRR, Strict+WRR, WRED, 802.1p. ACL: MAC based, IPv4C IPv6, TCP/UDP Port number, time based ACL, TFTP Client, SNMP V1, v2c, v3, SNMP traps, RMON, DHCP server, relay, client, LLDP, LLDP-MED, OAM, Dying Gasp, 802.3ah, sflow, RIP, OSPF v2/v3, policy based route, SSL, SSH. 6 kV surge protection on all Gigabit Ethernet ports and on all GE RJ-45 access ports. Certifications: UL, CE, FCC, RoHS, MTCTE, OEM/Product must be on Trusted Telecom Portal ofDepartment of Telecommunication, Government of India etc.
| 2039-03-01 | 24 port Layer 2 Non-PoE Network Switch | Each | 1 |  |  | 0 | 0
1.6 | MR | Supply, installation, testing and commissioning of hand held portable operator terminals (POT) minimum 7 inch. TFT display with capacitive touch screen type, shall be able to alarms , parameters etc. of DDC POT shall have integrated web server and a BACnet/ IP web interface to connect a HTML5 browser to a device on the network. POT With all required Providing,tors etc as per technical specification etc. | Each | 1 |  |  | 0 | 0
2 | 42.5 | BMS and Power Management Software:
2.1 |  | Supplying Installation Testing Commissioning of Necessary Software (UL listed) Packages containing Building Management with Capability of Collection, Storage, Processing and Controlling all the Data. Software shall support Open Standard Protocols like XML, BACnet, Modbus, Lon works etc. and without the use of Proprietary Protocols, with Enterprise Level Database Like MS SQL complete Lifetime Licenced & capable to collect, store & access all points from Fire Alarm Systems, IT Systems, Automation Systems, HVAC System, Lift, Energy management, Water Management System, etc. to create & monitor historical & event data, event management data, alarm management data & reporting data, Email Alerts for Critical alarms for all the systems. The scope includes additional software required by BMS software (to enable a standard Web browser) to be resident on the DDC/client machine (manufacture-specific browsers shall not be acceptable). User log-on identification and password shall be required & a minimum three-layered security system(User interface Level, Application Level and Data Base Level) to be deployed for safety. The supplied computer software shall employ objectoriented technology (OOT) for representation of all data and control devices within the system. This data shall reside on a server for all database access (Systems requiring proprietary database and user interface programs shall not be acceptable). All components and
| 2042-05-03 | For Upto 2500 point included | Nos. | 1 |  |  | 0 | 0
3 |  | Third Party Integration Controllers/ Integrators
| 42.1 | Supplying Installation Testing Commissioning following type 3rd party Integration unit to provide the interface between Ethernet LAN and the 3rd party field control devices or any other devices which need to be integrated. These shall also provide supervisory capability of functions over the devices connected to it. The purpose of using these units should be limited to integrate the devices only. The Unit must have two onboard Ethernet port, minimum 2/3 on board RS485 ports. The Integration unit should have inbuilt 4GB memory for program storage. The Unit must communicate over TCP/IP with communication speed of 10/100MBPS. The Integration unit should be capable of handling multiple protocol simultaneously such as Bacnet, Modbus, SNMP restricted to single protocol. All integrators should be mandatorily BTL listed. The integration unit shall be housed in suitable size sheet steel enclosure made of 1.6mm thick CRCA sheet, lockable front door with glass, arrangement for cable entry and duly powder coated complete etc as required. Integration of following services should be considered as per IO summary and BOQ
| 2042-10-03 | Integrator for 5000 Points | Each | 4 |  |  | 0 | 0
4 | 42.7 | BACnet IP DDC Controllers
capable of fully “stand- alone” operation i.e. In the event of loss of communicationwith other DDC’s or Control Station, they shall be able to function on their own. The controllers shall consist of dual/quad core 32 bit microprocessors with EPROM based operating system on BACNET. The network Topology shall not allow single point failure. Each DDC on field level shall have embedded TCP/IP (10/100Mbps) connectivity so that it can be hooked into the Local Area Network (LAN) provided by the client or on dedicated network . Each DDC can be accessed from the Graphical User Interface (GUI) or from a standard Web browser (WBI) by connecting the server alongwith inbuilt web browser. All controllers shall accept 230V+/- 10%, 50Hz Uninterrupted power supply provided by end user. Controller shall support DHCP addressing over Local Area Network (LAN) so that the static IP requirements get reduced however a single static IP shall be provided for system so that it can be hosted on to internet in consultation with end user. The microprocessor based DDC’s shall be provided with power supply, analoge to Digital and Digital to analoge converters with memory and capacity to accommodate input/output (I/O) hardware points (with or without an expansion board). Each DDC should have own board and shall accept 0-10 V / 4-20mA input signal having Minimum 20% spare capacity considered for expansion. Each DDC on field
4.1 | 2042-07-01 | DDC Controller-Type-I (Support upto 32 Points) | Each | 34 |  |  | 0 | 0
4.2 | 2042-07-02 | DDC Controller-Type-II (Support upto 64 Points) | Each | 11 |  |  | 0 | 0
4.3 | 2042-07-03 | DDC Controller-Type-III (Support upto 96 Points) | Each | 1 |  |  | 0 | 0
4.4 | 2042-07-04 | DDC Controller-Type-IV (Support upto 128 Points) | Each | 1 |  |  | 0 | 0
4.5 | 2042-07-05 | DDC Controller-Type-V (Support upto 160 Points) | Each | 1 |  |  | 0 | 0
|  |  |  | 1 |  |  | 0 | 0
4.6 | 42.8 | EXPNSION IO MODULE Supplying Installation Testing Commissioning of following type of input output (IO) expansion module complete etc. as required
4.6.1 | 2042-08-01 | I/O Module with 4 UIO channels | Each | 1 |  |  | 0 | 0
4.6.2 | 2042-08-02 | I/O Module with 8 UIO channels | Each | 36 |  |  | 0 | 0
4.6.3 | 2042-08-03 | I/O Module with 8 UI channels | Each | 154 |  |  | 0 | 0
4.6.4 | 2042-08-04 | I/O Module with 8 DI channels | Each | 1 |  |  | 0 | 0
4.6.5 | 2042-08-05 | I/O Module with 16 DI channels | Each | 20 |  |  | 0 | 0
4.6.6 | 2042-08-06 | I/O Module with 8 DO channels | Each | 1 |  |  | 0 | 0
4.6.7 | 2042-08-07 | I/O Module with 4 DO channels | Each | 11 |  |  | 0 | 0
5 |  | Sensors & Field Devices
Providing, Installing, Testing & Commissioning of necessary Input sensor transmitters/transducers comprising the following:
5.1 | 2042-11-06 | Immersion Temp Sensor for CHW line. Measuring range: -30 to 110 0C, Accuracy: +/- 1.3 0C | Nos. | 1 |  |  | 0 | 0
5.2 | MR | Providing, Installing, Testing & Commissioning of Water Differential Pressure Sensor | Nos. | 1 |  |  | 0 | 0
5.3 | 2042-11-05 | Outside Temp & Humidity Sensor with radiation shield. Measuring Range: Temp:- -15 to 50 0C & RH 0-100%, Accuracy: +/- 1 0C +/- 3% | Nos. | 1 |  |  | 0 | 0
5.4 | MR | Providing, Installing, Testing & Commissioning of Water Flow Meter | Nos. | 1 |  |  | 0 | 0
5.5 | 2042-11-01 | Water Differential Pressure (DP) Switch for Pump Status. | Nos. | 0
5.6 | 2042-11-12 | Differential pressure switch for filters & Blowers | Nos. | 219 |  |  | 0 | 0
5.7 | 2042-11-04 | Duct CO2 Sensor, 0-2000ppm, 0-10V/4-20mA Output. | Nos. | 41 |  |  | 0 | 0
5.8 | MR | Providing, Installing, Testing & Commissioning of Duct Pressure Sensors, accuracy shall be ± 1% including Integrated Pressure Probe, tubes, accessories etc. | Nos. | 21 |  |  | 0 | 0
5.9 | MR | Providing, Installing, Testing & Commissioning of Duct Temperature + Rh Sensor (Range 0-50 Deg C) shall be with rigid stem type. These shall be Platinum sensor suitable for duct installation and accuracy shall be ± 3% , for measuring supply -air temperature of AHUs etc., including Probe, tubes, accessories etc. | Nos. | 63 |  |  | 0 | 0
5.1 | MR | Providing, Installing, Testing & Commissioning of Hydrogen Gas Sensor for UPS and Battery Rooms | Nos. | 2 |  |  | 0 | 0
5.11 | 2042-11-07 | Water Pressure Sensor . Accuracy:+/-0.3% FSL | Nos. | 2 |  |  | 0 | 0
5.12 | MR | Providing, Installing, Testing & Commissioning of CO2 Sensor with Display. | Nos. | 263 |  |  | 0 | 0
5.13 | MR | Providing, Installing, Testing & Commissioning of T+RH modbus Sensor with Wire FOR CRITICAL ROOM - (LED Based Annunciator display panel for Temp+Rh with sensor, lead cable of 15 Mtrs with power supply complete for concealed wall mount) | Nos. | 17 |  |  | 0 | 0
5.14 | 2042-11-13 | Bi-Level Switches (Hi/Low) | Nos. | 2 |  |  | 0 | 0
6 |  | IAQ MONITOR SENSORS
|  | Providing, Installing, Testing & Commissioning of RESET Certified IAQ Monitor sensor with inbuilt mono display to show Real time display measure the levels of PM 2.5, PM 10, TVOC, CO2, Temperature, Humidity,Light level & Noise level on a real time basis. The IAQ Monitor shall be open protocol on BACnet IP/MSTP or Modbus RS485 enabled communication protocal and should be capable of getting connected with Wi-Fi or SIM . The Monitor should be capable of sending the indoor air quality information on display Screen/Mobile/Workstation as per Client's requirement.One Sensor should be placed at least one sensor prominaently positioned at the height of approx 5.6ft per 500 sqmt of regularly occupied space. Monitor should indicate the quality of air through changing the colours as per the NAAQS standards and should meet the WELL building standards. The sensors will be modular in design and can be separated from communication modules, making it easier to replace and maintain over the long term.Quoted price shall be inclusive of all necessary arrangement as required to make the unit proper functional. IAQ Monitor sensor shall be with BMS Communication through Backnet IP/MSTP or Modbus RS485 & the data rate will be set at every 10 seconds. | Nos. | 92 |  |  | 0 | 0
8 |  | CONDUITING WIRING & CABLING ETC.
All Cable, Conduit, Tray, Armoured cables Armouring shall be as per relevant IS standards
8.1 | MR | Providing, Laying, Testing & Commissioning of 2 x 1.5 sq.mm Annealed Tinned Copper Shielded armoured cable as per specification. (for I/O points hard wired to DDC). | RM | 56000 |  |  | 0 | 0
8.2 | MR | Providing, Laying, Testing & Commissioning of 4 x 1.5 sq.mm Annealed Tinned Copper Shielded armoured cable as per specification. (for I/O points hard wired to DDC). | RM | 4500 |  |  | 0 | 0
8.3 | MR | Providing, Laying, Testing & Commissioning of 3 x 1.5 sq.mm Annealed Tinned Copper Shielded armoured cable for signal and power as per specification. (power Cable for DDC Panel). | RM | 3500 |  |  | 0 | 0
8.3 | 39.18 | Supplying, drawing, Testing and commissioning of Cat6A UTP 4 pair, 23 AWG solid copper cable in existing conduit/ on surface, U/FTP, LSZH, NonPlenum, Horizontal (solid) Cable suitable for high speed data networking application supporting upto 10Gbps over a 100 meter channel. The 4 Unshielded Twisted Pairs (UTP) cable with color coded insulation for easy indentification should have FLAME PROPERTIES i.e. Flammability Test - IEC 60332-1, Smoke Density - IEC 61034, LSZH standards compliance: ANSI/TIA-568 C.2, ISO/IEC 11801, IEEE 802.3an, RoHS. Delay Skew should be < 45NS. The outer Cable Diameter should be 7.5 + 2 mm. Cable should have been tested and verified by UL/ ETL etc. complete as required.
| 39.18.1 | 1 Run of cable | RM | 3500 |  |  | 0 | 0
8.4 | 39.19 | Supplying and drawing following core Fiber Optic Cable having corrugated steel armoring. The Fiber should be SM Fiber Central -loose tube filled with Thixotropic jelly, duly following Standards: ISO 11801, IEC 60793- 1/60794-1-2, ITU-T-REC G.652D and Telecordia GR-20-core, High quality Electro Chromium Coated Corrugated Steel tape (ECCS ) and HDPE- Sheath, Operating ambient Temperature should be – 5 0C to +50 0C and Storage Temperature shall be – 5 0C to +50 0C, Max Attenuation ± 0.36 (db / km) at Operational Wavelength 1310 nm and ± 0.22 db / km at Operational Wavelength 1550 nm. type of fiber should be 9/125 / G.652D & Refractive Index should be 1.4670/1.4675. The value for Mode-filed, Cladding Diameter 9.2 ± 0.4 μm and 125 ± 0.7 μm correspondingly. The Dispersion value < 3.5 < 18 ps/nm-km and PMD value < 0.2 ps/km and Cable Cutoff wavelength < 1260 nm i/c splicing & marking etc. complete as required with core dia 50/125 µm (OM4) suitable for 10 Gbps ethernet ethernet distance at 850 nm of wavelength.
| 39.19.1 | Single Mode 6 Core Optical fiber cable | RM | 100 |  |  | 0 | 0
8.5 | 1.2 | Supplying and fixing of following sizes of steel conduit along with accessories in surface/recess including painting in case of surface conduit, or cutting the wall and making good the same in case of recessed conduit as required.
| 1.20.2 | 25mm dia | RM | 2500 |  |  | 0 | 0
8.6 | MR | Providing and laying of Industrial grade PVC flexible conduit with accessories | RM | 500 |  |  | 0 | 0
8.7 | MR | Providing and installation of Single Compression Glands for cable entry in DDC Panels | Nos | 800 |  |  | 0 | 0
8.8 | 4.6 | Supplying and installing following size of perforated Hot Dipped Galvanised Iron cable tray (Galvanisation thickness not less than 50 microns) with perforation not more than 17.5%, in convenient sections, joined with connectors, suspended from the ceiling with two numbers GI Suspenders i/c base of suitable size GI angle, GI bolts & nuts, fastner etc as required.
8.8.1 | 4.6.1 | 100 mm width X 20 mm depth X 1.6 mm thickness. | RM | 750 |  |  | 0 | 0
8.8.2 | 4.6.2 | 150 mm width X 50 mm depth X 1.6 mm thickness. | RM | 400 |  |  | 0 | 0
8.8.3 | 4.6.4 | 300 mm width X 50 mm depth X 1.6 mm thickness. | RM | 200 |  |  | 0 | 0
8.9 |  | Supplying and installing following size of perforated Hot Dipped Galvanised Iron cable tray "bends" (galvanisation not less than 50 microns) with perforation not more than 17.5%, in convenient sections, joined with connectors, suspended from the ceiling with two numbers GI Suspenders i/c base of suitable size GI angle, GI bolts & nuts, fastner etc as required.
8.9.1 | 4.7.1 | 100 mm width X 20 mm depth X 1.6 mm thickness. | Each | 30 |  |  | 0 | 0
8.9.2 | 4.7.2 | 150 mm width X 50 mm depth X 1.6 mm thickness. | Each | 40 |  |  | 0 | 0
8.9.3 | 4.7.4 | 300 mm width X 50 mm depth X 1.6 mm thickness. | Each | 70 |  |  | 0 | 0
IMPORTANT NOTES
The offered BMS shall be WEB-BASED system offering Multi-user interface without need of any proprietary BMS software License.
Minimum 5 simultaneous users shall be able to log-in to the BMS WEB- SERVER. The number of users, otherwise, shall be unlimited.
The Offered Web-Server and Embedded Web-Server Engines shall be capable of getting Dynamically Addressed on the DHCP Server.
Number of controllers shall have spare capacity for future expansion up to 15% for IO point and at System Level (Software shall have expansion capacity of 15% IO Points and 15% Software Points)
Wiring of motorized actuator shall be in BMS vendor scope and the power source shall be routed through the respective BMS panel which has UPS power.
Project Specific MAF (Manufacturer's Authorization Form) Certificate required along with the quotation from OEM to ensure the System Integrator is authorized & that the OEM will support the System Integrator before and during execution of the project.
TOTAL CARRIED OVER TO SUMMARY

## IT BOQ
Name of Work : IT Works
Sr. No. | DSR | DESCRIPTION OF ITEM | UNIT | QTY. | Rate |  | Amount (In Rs.)
[5 empty] | Supply | Installation | Supply | Installation
A |  | Passive Network System
1 |  | Supplying Installation Testing and Commissioning of 24 port Cat6A Patch Panel loaded. Must be of 1U height with clear label holders and white label with the panel. 24 Ports Cat-6A Patch Panel should have ETL/UL verification program certificate for compliance with ANSI/TIA- 568.2-D etc. complete as required. | Each | 262 | 64000 | 5000 | 16768000 | 1310000
2 |  | Supplying, Installation, Testing and commissioning of CAT6A Copper Quad Information Outlet (IO) with FacePlate with provision for connecting four I/O, along with spring type shutter for dust proof, face plate of color as per site requirement, should have ETL/UL verification program certificate for compliance with ANSI/TIA- 568.2-D. All copper Cable and Components should be from same OEM to maintain compatibility and interoperability etc. complete as required. | Each | 950 | 180 | 15 | 171000 | 14250
3 |  | Supplying, Installation, Testing and commissioning of CAT6A Copper Dual Information Outlet (IO) with FacePlate provision for connecting two I/O, along with spring type shutter for dust proof, face plate of color as per site requirement, should have ETL/UL verification program certificate for compliance with ANSI/TIA-568.2-D. All copper Cable and Components should be from same OEM to maintain compatibility and interoperability etc. complete as required. | Each | 480 | 175 | 15 | 84000 | 7200
4 |  | Supplying, Installation, Testing and commissioning of CAT6A Copper Single Information Outlet (IO) with FacePlate with provision for connecting one I/O, along with spring type shutter for dust proof, face plate of color as per site requirement, should have ETL/UL verification program certificate for compliance with ANSI/TIA- 568.2-D. All copper Cable and Components should be from same OEM to maintain compatibility and interoperability etc. complete as required. | Each | 530 | 150 | 15 | 79500 | 7950
5 |  | Supplying, Installation, Testing and commissioning of Single gang In-wall Rectangle GI Metallic Backbox of Dimension 86x86x45mm (HxWxD) | Each | 1960 |  |  | 0 | 0
6 | 39.18 | Supplying, drawing, Testing and commissioning of Cat6A UTP 4 pair, 23 AWG solid copper cable in existing conduit/ on surface, U/FTP, LSZH, Non- Plenum, Horizontal (solid) Cable suitable for high speed data networking application supporting upto 10Gbps over a 100 meter channel. The 4 Unshielded Twisted Pairs (UTP) cable with color coded insulation for easy indentification should have FLAME PROPERTIES i.e. Flammability Test - IEC 60332-1, Smoke Density - IEC 61034, LSZH standards compliance: ANSI/TIA-568 C.2, ISO/IEC 11801, IEEE 802.3an, RoHS. Delay Skew should be < 45NS. The outer Cable Diameter should be 7.5 + 2 mm. Cable should have been tested and verified by UL/ ETL etc. complete as required. |  |  |  |  | 0 | 0
| 39.18.1 | 1 run of cable | P/Mtr. | 303245 | 68 | 7 | 20620660 | 2122715
7 |  | Supplying, Installation, Testing and commissioning of following CAT6A Copper Patch Cord of length 2Mtr on Rack side. (6.5 ft) should have ETL/UL verification program certificate for compliance with ANSI/TIA-568.2-D etc. complete as required. | Each | 5700 | 575 | 25 | 3277500 | 142500
8 | 2039-12-02 | Supplying, Installation, Testing and commissioning of following CAT6A Copper Patch Cord of length 3Mtr on User side. (10ft) should have ETL/UL verification program certificate for compliance with ANSI/TIA-568.2-D etc. complete as required. | Each | 5700 | 620 | 25 | 3534000 | 142500
9 |  | Supplying Installation Testing and Commissioning of following core Multi mode Fiber Optic Cable having corrugated steel armoring, leser optimize 50/125 µm with HDPE jacket, LSZH (Low smoke Zero Halogen), Tight-buffered or loose tube, maximum attenuation: < 3.5 dB/km at 850 nm, <1.5 dB/km at 1300 nm, bandwidth > 2000 MHz-km at 850 nm, > 500 MHz-km at 1300 nm compliance and certifications: ISO/IEC 11801 Ed. 2.2, ANSI/TIA-568- C.3, ITU-T G.651.1 RoHS compliant. Multi Mode Fiber shall be Central-loose tube filled with Thixotropic jelly, duly following Standards: ISO 11801, IEC 60793- 1/60794-1-2, ITU-T-REC G.652D and Telecordia GR-20-core, High quality Electro Chromium Coated Corrugated Steel tape (ECCS ) and HDPE- Sheath, Operating ambient Temperature should be – 5 0C to +50 0C and Storage Temperature should be – 5 0C to +50 0C, Maximum Attenuation ± 3.5 dB/km at Operational Wavelength 850 nm and ± 1.5 dB / km at Operational Wavelength 1300 nm . type of fiber should be 50/125 / G.652D & Refractive Index should be 1.483/1.478, The value for Mode-filed,Cladding Diameter 50 ± 2.5 µm and 125 ± 1µm correspondingly i/c splicing & marking etc complete as required. |  |  |  |  | 0 | 0
|  | 24 Core Multi Mode Optical Fiber Cable | P/Mtr. | 2650 | 390 | 60 | 1033500 | 159000
10 |  | Supplying Installation Testing and Commissioning of Patch Cord of Optical Fiber Multi Mode or Single Mode LC to LC Fiber Duplex having high precision ceramic ferrule with good concentricity, Fiber corning single mode G652D, Cable Type 2mm with Mechanical specification Apex Offset < 50 µm, Fiber Height + 100 nm, End- face radius of Curvature 7mm < R <25mm, Repeatability < 0.2 db, Working ambient Temperature – 5 0C to +50 0C, Storage Temperature – 10 0C to +50 0C, Length -- 5meter, Type -- LC-LC Duplex etc complete as required. | Each | 270 | 19500 | 2000 | 5265000 | 540000
11 | 39.21.3 | Supplying Installation Testing and Commissioning of following port Rack Mount loaded 24 Port LIU with pigtail, Front-mounted cable saddles for jumper management, suitable to manage both splices and terminations, Pre-assembled shelves in multiple configurations, Rubber fiber slotted bracket built-in, metal splice shelf to protect the fibers, 2 fiber spools built-in for 900μm tight buffered fiber storing, Capable of storing up to 3 meters of 900μm tight buffered fiber per adapter, Removable front and rear covers for better access to interior of LIU, Should be Single / Multi mode LC Type fully loaded. Accessory kit consists of cable ties, mounting ear screws, and spiral wrap tube etc complete as required | Each | 22 | 64000 | 5000 | 1408000 | 110000
12 |  | Supplying Installation Testing and Commissioning of 42U rack 1000X800mm Dimension(DxW in mm),, floor- standing type, made from minimum 1.6 mm CRCA steel with adjustable 2 mm thick vertical mounting rails marked with all 42U positions, provision for minimum four cooling fans, and at least eight cable entry/exit points at the top and bottom with rubber grommets. It shall be powder coated in RAL 7035 or black and comply with UL and RoHS standards. The supply shall include two 6-socket 16A PDUs, three closed cable organizers, and a 20-piece hardware mounting kit, delivered in knocked-down condition with all required accessories. | Each | 16 | 50400 | 6300 | 806400 | 100800
13 |  | Supplying Installation Testing and Commissioning of 42U rack 1200X600mm Dimension(DxW in mm),, floor- standing type, made from minimum 1.6 mm CRCA steel with adjustable 2 mm thick vertical mounting rails marked with all 42U positions, provision for minimum four cooling fans, and at least eight cable entry/exit points at the top and bottom with rubber grommets. It shall be powder coated in RAL 7035 or black and comply with UL and RoHS standards. The supply shall include two 6-socket 16A PDUs, three closed cable organizers, and a 20-piece hardware mounting kit, delivered in knocked-down condition with all required accessories. | Each | 14 | 50400 | 6300 | 705600 | 88200
14 | 39.23.3 | Supplying Installation Testing and Commissioning of 15U Wall Mount Rack 1000X800mm Dimension(DxW in mm), having Fixed Structure with 0.8mm CRCA Sheet, completely knocked-down condition (CKD) Shape, Vertical Mounting Rail 1.6 mm with 'U'Marking, Minimum 2 cable entry/exit provision at Top and bottom with rubber protection, Front 5mm Toughened Glass with lock, wall mounting kit, Powder coated Color- RAL- 7035, complied with UL & RoHS, 2 x 6 sockets 16A power distribution units, 3 numbers closed cable organizer, Hardware mounting screws packet of 20 x 1 number, etc. complete as required. | Each | 5 | 18000 | 2250 | 90000 | 11250
|  | WIFI AP |  |  |  |  | 0 | 0
15 |  | Supplying Installation Testing and Commissioning of Enterprise-Class Wi-Fi 6E Tri-Band Indoor Access Point (4x4 MIMO): High-performance indoor wireless access point supporting tri-band operation (2.4 GHz, 5 GHz, and 6 GHz) with 4x4 multiple-input multiple-output (MIMO) technology. Designed for high-density enterprise or smart-building environments, supporting cloud-based or on-premises network management platforms. | Each | 218 |  |  | 0 | 0
16 |  | Supplying Installation Testing and Commissioning of enterprise-grade wireless access point software license valid for 5 years per individual access point | Each | 218 |  |  | 0 | 0
17 |  | Supplying, Installation, Testing and commissioning of indoor On Prem Hardware-based Wireless Controller designed for centralized WLAN management, supporting a minimum of 250 access points and 5,000 wireless clients with at least 5 Gbps throughput and up to 4,096 VLANs. Provides automated AP discovery, provisioning, firmware upgrades, monitoring, and troubleshooting. Includes RF optimization features such as Automatic Channel Selection (ACS), Transmit Power Control (TPC), Dynamic Frequency Selection (DFS), Radio Resource Management (RRM), and spectrum analysis. Supports WPA3, WPA2, WPA, and 802.1X authentication, captive portal guest access, WIPS, rogue AP detection, and seamless roaming using 802.11r/k/v with client load balancing. Offers wired and wireless QoS, traffic shaping, and application-aware policies. Equipped with 2x10G uplink ports and 4x2.5G/1G downlink ports, supporting LAG, 802.1Q VLAN tagging, static routing, and DHCP relay. Management via web GUI, CLI, SNMP v2c/v3, and Syslog, with secure boot, RBAC, HTTPS/SSH encryption, clustering, N+1 redundancy. | Each | 2 |  |  | 0 | 0
|  | Access Switches |  |  |  |  | 0 | 0
18 |  | Supplying Installation Testing and Commissioning of Enterprise-Class 48-Port Gigabit Network Switch with 10G Uplinks with Fixed-configuration Layer 2/Layer 3 network switch featuring 48 × 1 Gigabit Ethernet data ports and 4 × 10 Gigabit SFP+ uplink ports. Supplied with manufacturer essential feature set license for enterprise access-layer deployments and service coverage validity for 5 years. Shall include power adaptors and other accessories as required | Each | 116 | 42500 | 3500 | 4930000 | 406000
19 |  | Supplying Installation Testing and Commissioning of Enterprise-Class 24-Port Gigabit Network Switch with 10G Uplinks with Fixed-configuration Layer 2/Layer 3 switch featuring 24 × 1 Gigabit Ethernet data ports and 4 × 10 Gigabit SFP+ uplink ports.Supplied with manufacturer essential feature set license for enterprise access-layer deployments and service coverage validity for 5 years. Shall include power adaptors and other accessories as required | Each | 5 | 21250 | 2500 | 106250 | 12500
Sub-Total (A)
|  | Total (A) |  |  |  |  | 115651428.24

## Hybrid PBX Solution
Bill of Quantities
Name of Project: “Interior Fit-out work in the office space of Power Finance Corporation Limited, Tower-H, World Trade Centre, Nauroji Nagar, New Delhi-110029 including Operation & Maintenance for 06 years”
Name of Work :
Sr. No. | DSR/ MR | DESCRIPTION OF ITEM | UNIT | QTY. | Rate (In Rs.) |  | Amount (In Rs.)
[5 empty] | DSR | Non-DSR | DSR | Non-DSR
A |  | Hybrid PBX
1 | MR | Supplying Installation Testing and Commissioning of The Hybrid PBX/PABX/Communication System shall employ IP at its core with IP switching technology and 100% non-blocking,The 1000 port communication system should be configured for 1000 no’s Analog extension port and expandable upto 5000 ports , 02 no’s of Operator console,100 SIP Extensions, 16 Digital Extensions, 8 no’s of PSTN trunk port, 1 no’s of PRI port, 32 no’s of SIP trunk/channel License.Voice mail system with 256 hours of recording capacity. EPABX system should have server client architecture & FCAPS based NMS sysystem and NMS system should support redundancy as and when required . The system should be IPV6 ready,the system should have VoIP and VMS at its core i.e. VoIP and VMS modules should be mounted on the CPU. It should support digital key phone, GSM/3G/4G for voice. All interfaces except VoIP and VMS shall be in the form of expansion cards and can be plugged into the universal slots of the system as and when required in the future. VoIP and VMS Board module should sit on the CPU,The systems should be redundant which offer 100% duplication of power supply and CPU card. In the event of failure of the main power supply or CPU card, the standby will take over without disruption of on-going calls. : Certification:TEC,CE,FCC,ROHS, EMI-EMC" System should also support Cloud-based, enterprise-grade UC Solution Providing IM/Telephony Presence, click to call (dial by name, answer, release), Call Log, P2P Audio/Screen Sharing for All Users | Each | 1
2 | MR | Supplying Installation Testing and Commissioning of Telephones for Workstations, Meeting rooms with DTMF/ FSK compatible Caller ID, 16-digit LCD display, Ringer volume control Switch,30 incoming calls memory, Two-way speaker Phone with adjustable Volume,Two-way speaker Phone with adjustable Volume. | Each | 740
3 | MR | Supplying Installation Testing and Commissioning of Telephones for GM, CGM & ED Cabins having 16-Digit LCD Display with Backlight, 99 Nos Incoming Call Memory, 6-One Touch Memory,2 - Way Speaker Phone, Adjustable LCD Screen | Each | 155
4 | MR | Supplying Installation Testing and Commissioning of Telephones for Executive floor with 2.3 -inch, 128*64 backlit black and white display. The phone should provide handsfree mute and message keys, directory of 1000 contact, Provides fixed keys for common features like redial,hold, and mute, 4 menu keys for navigation. IEEE 802.3af. Power over Ethernet (PoE) or External Power Adapter Required. | Each | 47
5 | MR | Supplying Installation Testing and Commissioning of Telephones for CMD cabin with 5.5” touch screen, cordless handset, 2x6 virtual keyst, Dual-band Wi-Fi and Bluetooth 5.0 for wireless headset, 2x5 contextual touch keys, 5 function keys (F1-F5), VPN for secure work from home, Dual Gigabit Ethernet port, it shall have capability to pair with computer and smartphone by USB or Bluetooth. | Each | 1
Sub-Total (A)

## AV
Name of Project: “Interior Fit-out work in the office space of Power Finance Corporation Limited, Tower-H, World Trade Centre, Nauroji Nagar, New Delhi-110029 including Operation & Maintenance for 06 years”
Summary of AV BOQ
SR.NO | DESCRIPTION | Ground Floor | 1st Floor | 2nd Floor | Typical Floors 3rd, | 5th Floor | 7th Floor | 8th Floor | 9th Floor | QTY | UNIT RATE (INR) | TOTAL AMOUNT(INR)
SPACE
1 | Reception & Waiting Area | 1 | [7 empty] | 1
2 | Client Experience Zone | 1 | [7 empty] | 1
3 | Discussion Lounge | 2 | [7 empty] | 2
4 | 4 PAX Meeting Room |  | 2 | [6 empty] | 2
5 | 6 PAX Meeting Room | 5 |  |  |  | 1 |  |  |  | 6
6 | 7 PAX Meeting Room |  | 1 | [6 empty] | 1
7 | Two 8 PAX Divisible Meeting Rooms-Combined |  |  | 1 | 1 |  |  | 1 |  | 5
8 | 10 PAX Meeting Room |  | 1 | [6 empty] | 1
9 | 12 PAX Meeting Room |  |  | 1 | [5 empty] | 1
10 | Two 12 PAX Divisible Meeting Rooms-Combined |  |  | 1 | 1 | 1 |  | 1 |  | 6
11 | 9F - Two 12 PAX Divisible Meeting Rooms- Combined | [7 empty] | 1 | 1
12 | 22 PAX Training Room | 1 | [7 empty] | 1
13 | 16 PAX Training Room | 1 | [7 empty] | 1
14 | 4 Confrence Halls (individual and combined) |  | 1 | [6 empty] | 1
16 | Dealing Room |  |  |  |  | 1 |  |  |  | 1
18 | Borrower's Lounge |  | 1 | [6 empty] | 1
19 | Interview Room |  | 1 | [6 empty] | 1
20 | Meeting Lounge |  | 1 | [6 empty] | 1
21 | ED Cabin |  |  | 3 | 4 | 4 |  | 4 |  | 23
22 | Executive Dining |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 8
23 | Cafeteria/Townhall | [5 empty] | 1 |  |  | 1
24 | NOC Room |  | 1 | [6 empty] | 1
25 | SOC Room |  | 1 | [6 empty] | 1
26 | Multipurpose Rooms | [5 empty] | 1 |  |  | 1
27 | Podcast Room | [5 empty] | 1 |  |  | 1
28 | Chief Vigilance Office | [7 empty] | 1 | 1
29 | Functional Director Cabin | [7 empty] | 3 | 3
30 | CMD Cabin | [7 empty] | 1 | 1
31 | 25 PAX Board Room | [7 empty] | 1 | 1
32 | Ante Room Lounge /Lounge room | [7 empty] | 2 | 2
33 | Pre Function Area |  | 1 | [5 empty] | 2 | 3
34 | Immersive Experience | [7 empty] | 1 | 1
35 | Gym | 1 | [7 empty] | 1
36 | Creche | 1 | [7 empty] | 1
37 | Jumba & Meditation Room | [5 empty] | 1 |  |  | 1
38 | Displays on Trolley |  |  | 2 | 2 | 2 | 2 | 2 | 2 | 16
39 | Workplace Signage |  | 2 | 4 | 4 | 4 |  | 4 |  | 26
40 | Workplace Signage Software | 1 | [7 empty] | 1
Sub- Total (A)

## AUDIO & VISUAL SYSTEMS
Bill of Quantities
Name of Project: “Interior Fit-out work in the office space of Power Finance Corporation Limited, Tower-H, World Trade Centre, Nauroji Nagar, New Delhi-110029 including Operation & Maintenance for 06 years”
Name of Work: AUDIO & VISUAL SYSTEMS
S.NO | DESCRIPTION | UNIT | QTY | UNIT PRICE | TOTAL PRICE
Reception & Waiting Area
A | Display Devices & Accessories
1 | SITC of Indoor Active LED : 254 inch diagonal(6x2.37m), SMD, Die-Cast aluminium cabinet configuration, Pixel Pitch: 1.5 mm, 16:9 aspect ratio, minimum Brightness: 600 cd/m² , upto Contrast (10000:1), Wall resolution (W X H): 1920 X 1080, IP605rated(Module), Viewing angle degree (H 170 / V 170), LED Life range of 100000 hours, Refresh Rate(3840Hz), 18 bits processing, Front access 5% Spare support, 3 years warranty with Required Mounting and controls | Nos | 1
2 | SITC of Interactive 55" UHD resolution (3840x2160);Brightness - 500nits; Professional large format display with 3xHDMI input connectivity & built in speakers; Operating environment - 24/7 (with 3 years warranty) | Nos | 2
3 | SITC of Signage display kiosk designed to portrait mount a single digital signage screen with a rigid chassis which is fixed to a heavy duty steel base which can be used freestanding or bolted to the floor allowing 8-point micro-adjustment to ensure the mounted screen sits perfectly level and flush with the front opening of the kiosk, which is laser cut to match screens: from 39" up to 70" with Max load: 50kg VESA and Non-VESA fixings: 200 x 200 up to 600 x 400 | Nos | 2
B | Audio Devices
1 | SITC of Ceiling loudspeaker is equipped with a 4" full-range driver with a coaxial diffraction waveguide. With a short-term power rating of up to 200 W, the loudspeaker produces a maximum sound pressure of 109 dB. The dispersion pattern is 100° conical. The frequency response ranges from 55 Hz to 20 kHz | Nos | 16
2 | SITC of 4-channel digital amplifier (4*600W) with a 4 × 4 routing matrix and the following spec: frequency response : 20 Hz – 20 kHz, signal/noise ratio > 103 dB/A THD+N 0,15% (1 kHz, 8 ohms, 3 dB below clipping) dynamic range > 120 dB, DSP with 20 independent limiters, FIR filters, 8 × 10 fully parametric filter, 8 compressors, 8 noise gates & delays | Nos | 2
C | Control & Interface
1 | SITC of H.265, Full Hd and 4k Video, Html5, Graphics & Digital Audio, Hdmi Out, Ideal For Looping Video, Simple Html5 Widgets And Animation And Single Touchscreen | Nos | 3
2 | SITC of Multiple video windows can be positioned on LED, display based video walls or projector edge blends, displaying any of the sources connected to Processor, Up-Down-Cross Conversion, EDID manager, custom resolution editor, Modular chassis based Ultra-compact processor with Integrated front button panel for up to 2 x 4K HDMI input & 2 x 4K HDMI output | Nos | 1
3 | SITC of high-performance control processor designed for centralized AV control and numerous integrated control ports. Thed Device should have advanced security standards and Gigabit Ethernet, which ensures compatibility with interfaces using a standard network infrastructure.The Device should include all the required license to meet the requirement | Nos | 1
4 | SITC of 10' touchpanels feature capacitive, edge-to-edge glass touchscreens or high resolution LCD touchscreens that are fully-customizable to meet the User interface foe managing sources | Nos | 1
5 | SITC of 4K60 4:4:4 Transmitter for HDMI®, RS‑232, and IR Signal Extension over CATx Cable | Nos | 1
6 | SITC of 4K60 4:4:4 Receiver for HDMI®, RS‑232, and IR Signal Extension over CATx Cable | Nos | 1
D | Racks, Cables and Connectors
1 | SITC of 15Mtr HDMI Cable | Nos | 1
2 | SITC of Two Core with Sheilded speaker Cable | Mtr | 200
3 | SITC of 1.8Mtr HDMI Cable | Nos | 2
4 | SITC of Control Cable | Mtr | 100
5 | SITC of Cat6A Cable | Mtr | 120
6 | SITC of 42U Rack 100%compatibility with all equipments conforming to DIN 41494 (General industrial standard for equipments) Powder coated finish with seven tank pretreatment process meeting ASTM standard,Grounding & Bonding Options,Fan module Mount provision on top cover along with other accessories | Set | 1
Total (Inclusive of GST)
Client Experience Zone
A | Display Devices & Accessories
1 | SITC of Indoor DVLED : 163 inch diagonal(3.6x2.03m), Fully flip chip COB, Die-Cast aluminium cabinet configuration, Pixel Pitch: 1.5mm , 16:9 aspect ratio, Brightness: 600 cd/m² , Contrast (10000:1), Wall resolution (W X H): 1920 X 1080, IP605rated(Module), Cabinet dimensions ( W X H X D) : 600mm X 337.5mm X 29.9mm, Viewing angle degree (H 170 / V 170), LED Life (100000 hours), Refresh Rate(3840Hz), 18 bits processing, Front access 5% Spare support, 3 years warranty with Required Mounting and Controls including SITC of Multiple video windows can be positioned on LED, display based video walls or projector edge blends, displaying any of the sources connected to Processor, Up-Down-Cross Conversion, EDID manager, custom resolution editor, Modular chassis based Ultra-compact processor with Integrated front button panel for up to 2 x 4K HDMI input & 2 x 4K HDMI output | Nos | 1
2 | SITC of H.265, Full Hd and 4k Video, Html5, Graphics & Digital Audio, Hdmi Out, Ideal For Looping Video, Simple Html5 Widgets And Animation And Single Touchscreen | Nos | 1
B | Audio Devices
1 | SITC of the microphone array shall use beamforming technology that automatically focuses on whoever is speaking in the room. The beam will automatically detect the position of the person speaking and will follow the person around the room at all times. A threshold for the detection shall be adjustable. Live monitoring of the horizontal and vertical angle of the position.he microphone array shall have a Dante™ interface with two RJ 45 sockets (Primary and Secondary) for digital audio output, supporting both redundant and daisy-chain modes. The microphone array shall also feature a 3-pin terminal for analog audio output. All the associated mounting accessories to be included. | Nos | 1
2 | SITC of Digital signal processor (DSP) shall be open-architecture in configuration and be housed in a 4.25" width, 1U chassis. It shall offer eight (8) user-configurable card-slots for analog audio, USB, GPIO, relay and AES/EBU digital audio support. Additionally, it shall provide native Dante audio networking at 4x4 channels, and be compliant with AES67. The DSP shall feature a dual-core Linux processor with 40-bit floating point architecture.DSP must feature include advanced signal processing algorithms including (but not be limited to) various forms of mixers, equalizers, filters, crossovers, dynamics/gain controls, routers, room combiners, and delays. The program memory shall be nonvolatile and provide program security should power fail. | Nos | 1
3 | SITC of Ceiling loudspeaker is equipped with a 4" full-range driver with a coaxial diffraction waveguide. With a short-term power rating of up to 200 W, the loudspeaker produces a maximum sound pressure of 109 dB. The dispersion pattern is 100° conical. The frequency response ranges from 55 Hz to 20 kHz | Nos | 8
4 | SITC of Network compatible, DSP-controlled amplifier with 4 input channels and 4 output channels. CLASS D amplifier technology with 100 W output power at 4 ohm per channel. | Nos | 1
C | Control & Interface
1 | SITC of Wireless presentation Device to show an HDMI® output to the display (up to 4K), and various USB interfaces for wireless conferencing with all accessories and Power Supply Unit along with 1 wireless dongle | Nos | 1
2 | SITC of 10' touchpanels feature capacitive, edge-to-edge glass touchscreens or high resolution LCD touchscreens that are fully-customizable to meet the User interface foe managing sources | Nos | 1
3 | SITC of Universal Switcher with HDMI 2.0 and USB-C connectivity, Provides atleast Two HDMI® input and One USB-C Input and one HDMI output. The Device should be able to provide USB connections for peripherals | Nos | 1
4 | SITC of HDMI & USB‑C® wallplate for video, audio and control up to 330’ (100 m) over a shielded CAT 6A cable | Nos | 2
5 | SITC of 4K60 4:4:4 Transmitter for HDMI®, RS‑232, and IR Signal Extension over CATx Cable | Nos | 3
6 | SITC of 4K60 4:4:4 Receiver for HDMI®, RS‑232, and IR Signal Extension over CATx Cable | Nos | 4
D | Racks, Cables and Connectors
1 | SITC of 15Mtr HDMI Cable | Nos. | 1
2 | SITC of Two Core with Sheilded speaker Cable | Mtr | 150
3 | SITC of 1.8Mtr HDMI Cable | Nos. | 4
4 | SITC of 1.8Mtr USB C Cable | Nos | 2
5 | SITC of 4.6Mtr USB C Cable | Nos | 2
6 | SITC of Control Cable | Mtr | 100
7 | SITC of Cat6A Cable | Mtr | 150
8 | SITC of USB-C to HDMI Female Active Adapter | Set | 1
Total (Inclusive of GST)
Immersive Experience Area
A | Display Devices & Accessories
1 | SITC of Indoor DVLED : 163 inch diagonal(3.6x2.03m), Fully flip chip COB, Die-Cast aluminium cabinet configuration, Pixel Pitch: 1.5mm , 16:9 aspect ratio, Brightness: 600 cd/m² , Contrast (10000:1), Wall resolution (W X H): 1920 X 1080, IP605rated(Module), Cabinet dimensions ( W X H X D) : 600mm X 337.5mm X 29.9mm, Viewing angle degree (H 170 / V 170), LED Life (100000 hours), Refresh Rate(3840Hz), 18 bits processing, Front access 5% Spare support, 3 years warranty with Required Mounting and Controls | Nos | 2
2 | SITC of Multiple video windows can be positioned on LED, display based video walls or projector edge blends, displaying any of the sources connected to Processor, Up-Down-Cross Conversion, EDID manager, custom resolution editor, Modular chassis based Ultra-compact processor with Integrated front button panel for up to 4 x 4K HDMI input & 2 x 4K HDMI output | Nos | 1
3 | SITC of Interactive 55" UHD resolution (3840x2160);Brightness - 500nits; Professional large format display with 3xHDMI input connectivity & built in speakers; Operating environment - 24/7 (with 3 years warranty) | Nos | 1
4 | SITC of Custom Kiosk to fit the 55' Display with a Architect Approved Finish | Nos | 1
5 | SITC of H.265, Full Hd and 4k Video, Html5, Graphics & Digital Audio, Hdmi Out, Ideal For Looping Video, Simple Html5 Widgets And Animation And Single Touchscreen | Nos | 2
B | Audio System
1 | SITC of Ceiling loudspeaker is equipped with a 4" full-range driver with a coaxial diffraction waveguide. With a short-term power rating of up to 200 W, the loudspeaker produces a maximum sound pressure of 109 dB. The dispersion pattern is 100° conical. The frequency response ranges from 55 Hz to 20 kHz | Nos | 6
2 | SITC of 4-channel digital amplifier (4*600W) with a 4 × 4 routing matrix and the following spec: frequency response : 20 Hz – 20 kHz, signal/noise ratio > 103 dB/A THD+N 0,15% (1 kHz, 8 ohms, 3 dB below clipping) dynamic range > 120 dB, DSP with 20 independent limiters, FIR filters, 8 × 10 fully parametric filter, 8 compressors, 8 noise gates & delays | Nos | 1
C | Switching & Interface
1 | SITC of 10' touchpanels feature capacitive, edge-to-edge glass touchscreens or high resolution LCD touchscreens that are fully-customizable to meet the User interface foe managing sources | Nos | 1
2 | SITC of high-performance control processor designed for centralized AV control and numerous integrated control ports. Thed Device should have advanced security standards and Gigabit Ethernet, which ensures compatibility with interfaces using a standard network infrastructure.The Device should include all the required license to meet the requirement | Nos | 1
3 | SITC of HDMI & USB‑C® wallplate for video, audio and control up to 330’ (100 m) over a shielded CAT 6A cable | Nos | 1
4 | SITC of Switcher enabled 8 HDMI 2.0 inputs and Eight HDMI output. | Nos | 1
5 | SITC of 4K60 4:4:4 Transmitter for HDMI®, RS‑232, and IR Signal Extension over CATx Cable | Nos | 2
6 | SITC of 4K60 4:4:4 Transmitter for HDMI®, RS‑232, and IR Signal Extension over CATx Cable | Nos | 3
7 | SITC of Collaboration Device with 4K HDMI Output for Active LED Video Wall, 1 HDMI Input & 1 KVM Touch Control Interactive Canvas expands 20 times the surface area of the physical touchscreen,Wireless device sharing supports macOS, iOS, Windows, Android, Linux,Annotation toolset to annotate anything on the Canvas, including live feeds,Easy Content Sharing share content from a USB on the fly, or select from integrated network drive or cloud server,Multiple remote users able to view and collaborate on the canvas with Unlimited Use License,Multi Touch Collaboration System with perpetual license | Nos | 1
D | Racks, Cables and Connectors
1 | SITC of 15Mtr HDMI Cable | Nos. | 2
2 | SITC of Two Core with Sheilded speaker Cable | Mtr | 150
3 | SITC of 1.8Mtr HDMI Cable | Nos. | 6
4 | SITC of 1.8Mtr USB C Cable | Nos | 2
5 | SITC of 4.6Mtr USB C Cable | Nos | 2
6 | SITC of Control Cable | Mtr | 100
7 | SITC of Cat6A Cable | Mtr | 150
8 | SITC of 24U Rack 100%compatibility with all equipments conforming to DIN 41494 (General industrial standard for equipments) Powder coated finish with seven tank pretreatment process meeting ASTM standard,Grounding & Bonding Options,Fan module Mount provision on top cover along with other accessories | Set | 1
Total (Inclusive of GST)
Discussion Lounge
A | Display Devices & Accessories
1 | SITC of 85" UHD resolution (3840x2160);Brightness - 500nits; Professional large format display with 3xHDMI input connectivity & built in speakers; Operating environment - Min. 24/7 (with 3 years warranty) | Nos | 1
2 | SITC of Push Pull mount for screens from 65" upto 120". Pop-out system with load bearing capacity of 125Kg. Micro-adjustment of +/-7mm (0.3") at 8 points, Screen height adjustment: +15mm (0.6") for seamless display alignment, Integrated locking mechanism prevents accidental pop-out of mount, Safety screws to prevent unauthorised removal of screens with all mounting hardware included. | Nos | 1
B | Control & Interface
1 | SITC of H.265, Full Hd And 4k Video, Html5, Graphics & Digital Audio, Hdmi Out, Ideal For Looping Video, Simple Html5 Widgets And Animation And Single Touchscreen | Nos | 1
C | Switching & Interface
1 | SITC of Single-gang wall mount input or output for HDMI® digital video and audio. | Nos | 1
2 | SITC of Wireless presentation Device to show an HDMI® output to the display (up to 4K) and various USB interfaces for wireless conferencing with all accessories and Power Supply Unit along with 1 wireless dongle | Nos | 1
3 | SITC of Collaboration Switcher with HDMI 2.0 and USB-C connectivity, Provides atleast Two HDMI® input and atleast One USB-C Input and atleast one HDMI output. | Nos | 1
D | Cables & connectors
1 | SITC of 15Mtr HDMI Cable | Nos. | 2
2 | SITC of 1.8Mtr HDMI Cable | Nos. | 3
3 | SITC of 1.8Mtr USB C Cable | Nos | 2
4 | SITC of 4.6Mtr USB C Cable | Nos | 2
5 | SITC of Cat6A Cable | Mtr | 20
Total (Inclusive of GST)
Interview Room
A | Display Devices & Accessories
1 | SITC of 65" UHD resolution (3840x2160);Brightness - 500nits; Professional large format display with 3xHDMI input connectivity & built in speakers; Operating environment - 16/7 (with 3 years warranty) | Nos | 1
2 | Push Pull mount for screens from 42" upto 75". Pop-out system with load bearing capacity of 50Kg. Micro- adjustment of +/-7.5mm (0.3") at each corner Screen height adjustment: +15mm (0.6") for seamless display alignment, Integrated locking mechanism prevents accidental pop-out of mount, Safety screws to prevent unauthorised removal of screens with all mounting hardware included. | Nos | 1
B | Video Conferencing
1 | SITC of 4K Dual Lens Speaker Tracking Camera with 12x Zoom the camera Should have AI-powered Speaker tracking,Autotracking, Automframing and PIP, The camera should be able to five output via HDMI, Ethernet, 3G-SDI, USB. The camera Should include all the required Mounting Accessories. | Nos | 1
2 | Microsoft Teams Room Compute along with a 10 inch Touch Panel to integrate with 3rd Party peripherals | Nos | 1
C | Audio System
1 | SITC of The microphone array shall use beamforming technology that automatically focuses on whoever is speaking in the room. The beam will automatically detect the position of the person speaking and will follow the person around the room at all times. A threshold for the detection shall be adjustable. Live monitoring of the horizontal and vertical angle of the position.he microphone array shall have a Dante™ interface with two RJ 45 sockets (Primary and Secondary) for digital audio output, supporting both redundant and daisy-chain modes. The microphone array shall also feature a 3-pin terminal for analog audio output. All the associated mounting accessories to be included. | Nos | 1
2 | SITC of Digital signal processor (DSP) shall be open-architecture in configuration and be housed in a 4.25" width, 1U chassis. It shall offer eight (8) user-configurable card-slots for analog audio, USB, GPIO, relay and AES/EBU digital audio support. Additionally, it shall provide native Dante audio networking at 4x4 channels, and be compliant with AES67. The DSP shall feature a dual-core Linux processor with 40-bit floating point architecture.DSP must feature include advanced signal processing algorithms including (but not be limited to) various forms of mixers, equalizers, filters, crossovers, dynamics/gain controls, routers, room combiners, and delays. The program memory shall be nonvolatile and provide program security should power fail. | Nos | 1
3 | SITC of Ceiling loudspeaker is equipped with a 4" full-range driver with a coaxial diffraction waveguide. With a short-term power rating of up to 200 W, the loudspeaker produces a maximum sound pressure of 109 dB. The dispersion pattern is 100° conical. The frequency response ranges from 55 Hz to 20 kHz | Nos | 4
4 | SITC of Network compatible, DSP-controlled amplifier with 4 input channels and 4 output channels. CLASS D amplifier technology with 100 W output power at 4 ohm per channel. | Nos | 1
D | Switching & Interface
1 | SITC of Cable cubby with 2 Universal Power Sockets with Passthrough cables 1 HDMI, 1 usb-C, 1 USB-A & 1 LAN | Nos | 1
2 | SITC of Wireless presentation Device to show an HDMI® output to the display (up to 4K), an HDMI input, and various USB interfaces for wireless conferencing with all accessories and Power Supply Unit along with 1 wireless dongle | Nos | 1
3 | SITC of Collaboration Switcher with HDMI 2.0 and USB-C connectivity, Provides atleast Two HDMI® input and atleast One USB-C Input and atleast one HDMI output. | Nos | 1
E | Room Scheduler
1 | SITC of 10.1-inch diagonal, Anti-glare and anti-fingerprint Room Scheduling Screen, The device should Integrates with O365, Exchange and Google Calendar,Integrated wall mounting works with all types of surfaces: glass walls, brick walls or dry walls ,15° tilted angle allows for ergonomic use and accessibility, | Nos | 1
F | Racks, Cables and Connectors
1 | SITC of 15Mtr HDMI Cable | Nos. | 2
2 | SITC of Two Core with Sheilded speaker Cable | Mtr | 150
3 | SITC of 1.8Mtr HDMI Cable | Nos. | 2
4 | SITC of 1.8Mtr USB C Cable | Nos | 2
5 | SITC of 4.6Mtr USB C Cable | Nos | 2
6 | SITC of Control Cable | Mtr | 50
7 | SITC of Cat6A Cable | Mtr | 20
8 | SITC of 15U Rack 100%compatibility with all equipments conforming to DIN 41494 (General industrial standard for equipments) Powder coated finish with seven tank pretreatment process meeting ASTM standard,Grounding & Bonding Options,Fan module Mount provision on top cover along with other accessories | Set | 1
Total (Inclusive of GST)
4 PAX Meeting Room
A | Display Devices & Accessories
1 | SITC of 43" UHD resolution (3840x2160);Brightness - 500nits; Professional large format display with 3xHDMI input connectivity & built in speakers; Operating environment - 16/7 (with 3 years warranty) | Nos | 1
2 | SITC of Push Pull mount for screens from 42" upto 75". Pop-out system with load bearing capacity of 50Kg. Micro-adjustment of +/-7.5mm (0.3") at each corner Screen height adjustment: +15mm (0.6") for seamless display alignment, Integrated locking mechanism prevents accidental pop-out of mount, Safety screws to prevent unauthorised removal of screens with all mounting hardware included. | Nos | 1
B | Video Conferencing
1 | SITC all in one UC Video Bar featuring inbuilt microphones and stereo speakers. The device Should have a 4K Ultra HD camera and a maximum of 120 degree FOV. The device should be with a BYOD capability. The device should have capbility to support 2 displays if required.The Audio Pickup of Microphone should be atleast 15ft. | Nos | 1
C | Switching & Interface
1 | SITC of Cable cubby with 2 Universal Power Sockets with Passthrough cables 1 HDMI, 1 usb-C, 1 USB-A & 1 LAN | Nos | 1
D | Room Scheduler
1 | SITC of 10.1-inch diagonal, Anti-glare and anti-fingerprint Room Scheduling Screen, The device should Integrates with O365, Exchange and Google Calendar,Integrated wall mounting works with all types of surfaces: glass walls, brick walls or dry walls ,15° tilted angle allows for ergonomic use and accessibility, | Nos | 1
E | Cables & connectors
1 | SITC of 5Mtr HDMI Cable | Nos | 2
2 | SITC of 1.8Mtr HDMI Cable | Nos | 2
3 | SITC of 4.6Mtr USB C Cable | Nos | 1
4 | SITC of Cat6A Cable | Mtr | 20
Total (Inclusive of GST)
6PAX Meeting Room
A | Display Devices & Accessories
1 | SITC of 55" UHD resolution (3840x2160);Brightness - 500nits; Professional large format display with 3xHDMI input connectivity & built in speakers; Operating environment - 16/7 (with 3 years warranty) | Nos | 1
2 | SITC of Push Pull mount for screens from 42" upto 75". Pop-out system with load bearing capacity of 50Kg. Micro-adjustment of +/-7.5mm (0.3") at each corner Screen height adjustment: +15mm (0.6") for seamless display alignment, Integrated locking mechanism prevents accidental pop-out of mount, Safety screws to prevent unauthorised removal of screens with all mounting hardware included. | Nos | 1
B | Video Conferencing
1 | SITC all in one UC Video Bar featuring inbuilt microphones and stereo speakers. The device Should have a 4K Ultra HD camera and a maximum of 120 degree FOV. The device should be With native Teams MS teams with a 10' Touch Panel and with a BYOD capability. The device should have capbility to support 2 displays if required.The Audio Pickup of Microphone should be atleast 15ft. | Nos | 1
C | Switching & Interface
1 | SITC of Cable cubby with 2 Universal Power Sockets with Passthrough cables 1 HDMI, 1 usb-C, 1 USB-A & 1 LAN | Nos | 1
D | Room Scheduler
1 | SITC of 10.1-inch diagonal, Anti-glare and anti-fingerprint Room Scheduling Screen, The device should Integrates with O365, Exchange and Google Calendar,Integrated wall mounting works with all types of surfaces: glass walls, brick walls or dry walls ,15° tilted angle allows for ergonomic use and accessibility, | Set | 1
E | Cables & connectors
1 | SITC of 5Mtr HDMI Cable | Nos | 2
2 | SITC of 1.8Mtr HDMI Cable | Nos | 2
3 | SITC of 4.6Mtr USB C Cable | Nos | 1
4 | SITC of Cat6A Cable | Mtr | 20
Total (Inclusive of GST)
7 PAX Meeting Room
A | Display Devices & Accessories
1 | SITC of 55" UHD resolution (3840x2160);Brightness - 500nits; Professional large format display with 3xHDMI input connectivity & built in speakers; Operating environment - 16/7 (with 3 years warranty) | Nos | 1
2 | SITC of Push Pull mount for screens from 42" upto 75". Pop-out system with load bearing capacity of 50Kg. Micro-adjustment of +/-7.5mm (0.3") at each corner Screen height adjustment: +15mm (0.6") for seamless display alignment, Integrated locking mechanism prevents accidental pop-out of mount, Safety screws to prevent unauthorised removal of screens with all mounting hardware included. | Nos | 1
B | Video Conferencing
1 | SITC all in one UC Video Bar featuring inbuilt microphones and stereo speakers. The device Should have a 4K Ultra HD camera and a maximum of 120 degree FOV. The device should be With native Teams MS teams with a 10' Touch Panel and with a BYOD capability. The device should have capbility to support 2 displays if required.The Audio Pickup of Microphone should be atleast 15ft. | Nos | 1
C | Switching & Interface
1 | SITC of Cable cubby with 2 Universal Power Sockets with Passthrough cables 1 HDMI, 1 usb-C, 1 USB-A & 1 LAN | Nos | 1
D | Room Scheduler
1 | SITC of 10.1-inch diagonal, Anti-glare and anti-fingerprint Room Scheduling Screen, The device should Integrates with O365, Exchange and Google Calendar,Integrated wall mounting works with all types of surfaces: glass walls, brick walls or dry walls ,15° tilted angle allows for ergonomic use and accessibility, | Set | 1
E | Cables & connectors
1 | SITC of 15Mtr HDMI Cable | Nos | 1
2 | SITC of 1.8Mtr HDMI Cable | Nos | 2
3 | SITC of 4.6Mtr USB C Cable | Nos | 1
4 | SITC of Cat6A Cable | Mtr | 20
Total (Inclusive of GST)
10 PAX Meeting Room
A | Display Devices & Accessories
1 | SITC of 65" UHD resolution (3840x2160);Brightness - 500nits; Professional large format display with 3xHDMI input connectivity & built in speakers; Operating environment - 16/7 (with 3 years warranty) | Nos | 1
2 | SITC of Push Pull mount for screens from 42" upto 75". Pop-out system with load bearing capacity of 50Kg. Micro-adjustment of +/-7.5mm (0.3") at each corner Screen height adjustment: +15mm (0.6") for seamless display alignment, Integrated locking mechanism prevents accidental pop-out of mount, Safety screws to prevent unauthorised removal of screens with all mounting hardware included. | Nos | 1
B | Video Conferencing
1 | SITC all in one UC Video Bar featuring inbuilt microphones and stereo speakers. The device Should have Dual 4K Ultra HD camera and a FOV 0f 70-120. The device should be With native Teams MS teams with a 10' Touch Panel and with a BYOD capability. The device should have capability to support 2 displays if required.The Audio Pickup of Microphone should be atleast 25ft. | Nos | 1
C | Switching & Interface
1 | SITC of Cable cubby with 2 Universal Power Sockets with Passthrough cables 1 HDMI, 1 usb-C, 1 USB-A & 1 LAN | Nos | 1
2 | SITC of Wireless presentation Device to show an HDMI® output to the display (up to 4K) and various USB interfaces for wireless conferencing with all accessories and Power Supply Unit along with 1 wireless dongle | Nos | 1
3 | SITC of Universal Switcher with HDMI 2.0 and USB-C connectivity, Provides Two HDMI® input and One USB-C Input and one HDMI output. | Nos | 1
D | Room Scheduler
1 | SITC of 10.1-inch diagonal, Anti-glare and anti-fingerprint Room Scheduling Screen, The device should Integrates with O365, Exchange and Google Calendar,Integrated wall mounting works with all types of surfaces: glass walls, brick walls or dry walls ,15° tilted angle allows for ergonomic use and accessibility, | Nos | 1
E | Cables & connectors
1 | SITC of 15Mtr HDMI Cable | Nos | 1
2 | SITC of 1.8Mtr HDMI Cable | Nos | 3
3 | SITC of 1.8Mtr USB C Cable | Nos | 1
4 | SITC of 4.6Mtr USB C Cable | Nos | 1
5 | SITC of Cat6A Cable | Mtr | 20
Total (Inclusive of GST)
12 PAX Meeting Room
A | Display Devices & Accessories
1 | SITC of 65" UHD resolution (3840x2160);Brightness - 500nits; Professional large format display with 3xHDMI input connectivity & built in speakers; Operating environment - 16/7 (with 3 years warranty) | Nos | 1
2 | SITC of Push Pull mount for screens from 42" upto 75". Pop-out system with load bearing capacity of 50Kg. Micro-adjustment of +/-7.5mm (0.3") at each corner Screen height adjustment: +15mm (0.6") for seamless display alignment, Integrated locking mechanism prevents accidental pop-out of mount, Safety screws to prevent unauthorised removal of screens with all mounting hardware included. | Nos | 1
B | Video Conferencing
1 | SITC all in one UC Video Bar featuring inbuilt microphones and stereo speakers. The device Should have Dual 4K Ultra HD camera and a FOV 0f 70-120. The device should be With native Teams MS teams with a 10' Touch Panel and with a BYOD capability. The device should have capability to support 2 displays if required.The Audio Pickup of Microphone should be atleast 25ft. | Nos | 1
C | Switching & Interface
1 | SITC of Cable cubby with 2 Universal Power Sockets with Passthrough cables 1 HDMI, 1 usb-C, 1 USB-A & 1 LAN | Nos | 1
2 | SITC of Wireless presentation Device to show an HDMI® output to the display (up to 4K) and various USB interfaces for wireless conferencing with all accessories and Power Supply Unit along with 1 wireless dongle | Nos | 1
3 | SITC of Universal Switcher with HDMI 2.0 and USB-C connectivity, Provides Two HDMI® input and One USB-C Input and one HDMI output. | Nos | 1
D | Room Scheduler
1 | SITC of 10.1-inch diagonal, Anti-glare and anti-fingerprint Room Scheduling Screen, The device should Integrates with O365, Exchange and Google Calendar,Integrated wall mounting works with all types of surfaces: glass walls, brick walls or dry walls ,15° tilted angle allows for ergonomic use and accessibility, | Nos | 1
E | Cables & connectors
1 | SITC of 15Mtr HDMI Cable | Nos | 1
2 | SITC of 1.8Mtr HDMI Cable | Nos | 3
3 | SITC of 1.8Mtr USB C Cable | Nos | 1
4 | SITC of 4.6Mtr USB C Cable | Nos | 1
5 | SITC of Cat6A Cable | Mtr | 20
Total (Inclusive of GST)
Two Divisible 8 PAX Meeting Rooms
A | Display Devices & Accessories
1 | SITC of 65" UHD resolution (3840x2160);Brightness - 500nits; Professional large format display with 3xHDMI input connectivity & built in speakers;Operating environment - 16/7 (with 3 years warranty) | Nos | 2
2 | SITC of Push Pull mount for screens from 42" upto 75". Pop-out system with load bearing capacity of 50Kg. Micro-adjustment of +/-7.5mm (0.3") at each corner Screen height adjustment: +15mm (0.6") for seamless display alignment, Integrated locking mechanism prevents accidental pop-out of mount, Safety screws to prevent unauthorised removal of screens with all mounting hardware included. | Nos | 2
B | Video Conferencing
1 | SITC all in one UC Video Bar featuring inbuilt microphones and stereo speakers. The device Should have Dual 4K Ultra HD camera and a FOV of 70-120. The device should be With native Teams MS teams with a 10' Touch Panel and with a BYOD capability. The device should have capbility to support 2 displays if required.The Audio Pickup of Microphone should be atleast 25ft. | Nos | 2
C | Switching & Interface
1 | SITC of Single-gang wall mount input or output for HDMI® digital video and audio. | Nos | 2
2 | SITC of Wireless presentation Device to show an HDMI® output to the display (up to 4K) and various USB interfaces for wireless conferencing with all accessories and Power Supply Unit along with 1 wireless dongle | Nos | 2
3 | SITC of Collaboration Switcher with HDMI 2.0 and USB-C connectivity, Provides atleast Two HDMI® input and atleast Two USB-C Input and atleast Two HDMI output. | Nos | 2
D | Room Scheduler
1 | SITC of 10.1-inch diagonal, Anti-glare and anti-fingerprint Room Scheduling Screen, The device should Integrates with O365, Exchange and Google Calendar,Integrated wall mounting works with all types of surfaces: glass walls, brick walls or dry walls ,15° tilted angle allows for ergonomic use and accessibility, | Set | 2
E | Cables & connectors
1 | SITC of 15Mtr HDMI Cable | Nos. | 4
2 | SITC of 1.8Mtr HDMI Cable | Nos. | 8
3 | SITC of 1.8Mtr USB C Cable | Nos | 4
4 | SITC of 4.6Mtr USB C Cable | Nos | 4
5 | SITC of Cat6A Cable | Mtr | 40
Total (Inclusive of GST)
Two Divisible 12 PAX Meeting Room
A | Display Devices & Accessories
1 | SITC of 65" UHD resolution (3840x2160);Brightness - 500nits; Professional large format display with 3xHDMI input connectivity & built in speakers; Operating environment - 16/7 (with 3 years warranty) | Nos | 2
2 | SITC of Push Pull mount for screens from 42" upto 75". Pop-out system with load bearing capacity of 50Kg. Micro-adjustment of +/-7.5mm (0.3") at each corner Screen height adjustment: +15mm (0.6") for seamless display alignment, Integrated locking mechanism prevents accidental pop-out of mount, Safety screws to prevent unauthorised removal of screens with all mounting hardware included. | Nos | 2
B | Video Conferencing
1 | SITC of 4K Dual Lens Speaker Tracking Camera with 12x Zoom the camera Should have AI-powered Speaker tracking,Autotracking, Automframing and PIP, The camera should be able to five output via HDMI, Ethernet, 3G-SDI, USB. The camera Should include all the required Mounting Accessories. | Nos | 2
2 | Microsoft Teams Room Compute along with a 10 inch Touch Panel to integrate with 3rd Pary peripherals | Nos | 2
C | Audio System
1 | SITC of the microphone array shall use beamforming technology that automatically focuses on whoever is speaking in the room. The beam will automatically detect the position of the person speaking and will follow the person around the room at all times. A threshold for the detection shall be adjustable. Live monitoring of the horizontal and vertical angle of the position.he microphone array shall have a Dante™ interface with two RJ 45 sockets (Primary and Secondary) for digital audio output, supporting both redundant and daisy-chain modes. The microphone array shall also feature a 3-pin terminal for analog audio output. All the associated mounting accessories to be included. | Nos | 2
2 | SITC of Full rack 19” 1RU processor mainframe with sixteen user-configured card slots (16 blank cards included.Selectable 48 & 96kHz sampling rates. Integrated license-activated AEC. Dual core processing 40-bit floating DSP .Front panel OLED display with jog wheel. Rear panel includes an Ethernet module with RJ45 connector and internal power supply connection with built-in MOD-Dante-ETH module already pre- installed.Dante mainframe to provide 64x64 I/O channels of Dante network audio. Dual RJ45 Dante and single RJ45 Ethernet connectors.16ch Mic/Line inputs with selectable mic, line, mic gain, and phantom power per input. 32-bit analog to digital converters.6ch Line output. 32-bit digital to analog converters.Softwarelicense activated AEC. 8ch of AEC @ 250ms delay / 16ch @ 100ms. | Nos | 1
3 | SITC of ceiling loudspeaker is equipped with a 4" full-range driver with a coaxial diffraction waveguide. Nominal rating of 50W, max. SPL of 109 dB. The dispersion pattern should be 100° conical. The frequency response ranges from 55 Hz to 20 kHz. The flat protective grille is magnetically attached and can be removed manually. | Nos | 8
4 | SITC of Network compatible, DSP-controlled amplifier with 4 input channels and 4 output channels. CLASS D amplifier technology with 100 W output power at 4 ohm per channel. | Nos | 2
5 | SITC of USB2.0 to Dante network endpoint, PoE-powered with single CatX cable and suitable for mounting under the table or behind a display, with UC mute sync. | Nos | 2
6 | SITC of Designer IP-based wall control with recessed rotary encoder, PoE power and configurable OLED display. Mounts into single-gang Decora® cut-out (not included). | Nos | 2
C | Switching & Interface
1 | SITC of HDMI & USB‑C® wallplate for video, audio and control up to 330’ (100 m) over a shielded CAT 6A cable | Nos | 2
2 | SITC of 4K60 4:4:4 Receiver for HDMI®, RS‑232, and IR Signal Extension over CATx Cable | Nos | 2
3 | SITC of Wireless presentation Device to show an HDMI® output to the display (up to 4K), an HDMI input, and various USB interfaces for wireless conferencing with all accessories and Power Supply Unit along with 1 wireless dongle | Nos | 2
4 | SITC of Collaboration Switcher with HDMI 2.0 and USB-C connectivity, Provides atleast Two HDMI® input and atleast Two USB-C Input and atleast Two HDMI output. | Nos | 2
5 | SITC of 10' touchpanels feature capacitive, edge-to-edge glass touchscreens or high resolution LCD touchscreens that are fully-customizable to meet the User interface foe managing sources | Nos | 2
6 | SITC of high-performance control processor designed for centralized AV control and numerous integrated control ports. Thed Device should have advanced security standards and Gigabit Ethernet, which ensures compatibility with interfaces using a standard network infrastructure.The Device should include all the required license to meet the requirement | Nos | 1
7 | SITC of 8x1G PoE+ 125W 2x1G and 2xSFP Managed Switch. Additional power supply to be considered to manage the POE Budget | Nos | 1
E | Room Scheduler
1 | SITC of 10.1-inch diagonal, Anti-glare and anti-fingerprint Room Scheduling Screen, The device should Integrates with O365, Exchange and Google Calendar,Integrated wall mounting works with all types of surfaces: glass walls, brick walls or dry walls ,15° tilted angle allows for ergonomic use and accessibility, | Nos | 2
F | Racks, Cables and Connectors
1 | SITC of 15Mtr HDMI Cable | Nos | 4
2 | SITC of Two Core with Sheilded speaker Cable | Mtr | 150
3 | SITC of 1.8Mtr HDMI Cable | Nos | 6
4 | SITC of 1.8Mtr USB C Cable | Nos | 2
5 | SITC of 4.6Mtr USB C Cable | Nos | 2
6 | SITC of Control Cable | Mtr | 70
7 | SITC of Cat6A Cable | Mtr | 70
8 | SITC of 24U Rack 100%compatibility with all equipments conforming to DIN 41494 (General industrial standard for equipments) Powder coated finish with seven tank pretreatment process meeting ASTM standard,Grounding & Bonding Options,Fan module Mount provision on top cover along with other accessories | Set | 1
Total (Inclusive of GST)
9F Two Divisible 12 PAX Meeting Room
A | Display Devices & Accessories
1 | SITC of 65" UHD resolution (3840x2160);Brightness - 500nits; Professional large format display with 3xHDMI input connectivity & built in speakers; Operating environment - 16/7 (with 3 years warranty) | Nos | 2
2 | SITC of Push Pull mount for screens from 42" upto 75". Pop-out system with load bearing capacity of 50Kg. Micro-adjustment of +/-7.5mm (0.3") at each corner Screen height adjustment: +15mm (0.6") for seamless display alignment, Integrated locking mechanism prevents accidental pop-out of mount, Safety screws to prevent unauthorised removal of screens with all mounting hardware included. | Nos | 2
B | Video Conferencing
1 | SITC of 4K Dual Lens Speaker Tracking Camera with 12x Zoom the camera Should have AI-powered Speaker tracking,Autotracking, Automframing and PIP, The camera should be able to five output via HDMI, Ethernet, 3G-SDI, USB. The camera Should include all the required Mounting Accessories. | Nos | 2
2 | Microsoft Teams Room Compute along with a 10 inch Touch Panel to integrate with 3rd Pary peripherals | Nos | 2
C | Audio System
1 | SITC of the microphone array shall use beamforming technology that automatically focuses on whoever is speaking in the room. The beam will automatically detect the position of the person speaking and will follow the person around the room at all times. A threshold for the detection shall be adjustable. Live monitoring of the horizontal and vertical angle of the position.he microphone array shall have a Dante™ interface with two RJ 45 sockets (Primary and Secondary) for digital audio output, supporting both redundant and daisy-chain modes. The microphone array shall also feature a 3-pin terminal for analog audio output. All the associated mounting accessories to be included. | Nos | 2
2 | SITC of Digital signal processor (DSP) shall be open-architecture in configuration and be housed in a 4.25" width, 1U chassis. It shall offer eight (8) user-configurable card-slots for analog audio, USB, GPIO, relay and AES/EBU digital audio support. Additionally, it shall provide native Dante audio networking at 4x4 channels, and be compliant with AES67. The DSP shall feature a dual-core Linux processor with 40-bit floating point architecture.DSP must feature include advanced signal processing algorithms including (but not be limited to) various forms of mixers, equalizers, filters, crossovers, dynamics/gain controls, routers, room combiners, and delays. The program memory shall be nonvolatile and provide program security should power fail. | Nos | 1
3 | SITC of ceiling loudspeaker is equipped with a 4" full-range driver with a coaxial diffraction waveguide. Nominal rating of 50W, max. SPL of 109 dB. The dispersion pattern should be 100° conical. The frequency response ranges from 55 Hz to 20 kHz. The flat protective grille is magnetically attached and can be removed manually. | Nos | 8
4 | SITC of Network compatible, DSP-controlled amplifier with 4 input channels and 4 output channels. CLASS D amplifier technology with 100 W output power at 4 ohm per channel. | Nos | 2
5 | SITC of USB2.0 to Dante network endpoint, PoE-powered with single CatX cable and suitable for mounting under the table or behind a display, with UC mute sync. | Nos | 2
6 | SITC of Designer IP-based wall control with recessed rotary encoder, PoE power and configurable OLED display. Mounts into single-gang Decora® cut-out (not included). | Nos | 2
C | Switching & Interface
1 | SITC of HDMI & USB‑C® wallplate for video, audio and control up to 330’ (100 m) over a shielded CAT 6A cable | Nos | 2
2 | SITC of 4K60 4:4:4 Receiver for HDMI®, RS‑232, and IR Signal Extension over CATx Cable | Nos | 2
3 | SITC of Wireless presentation Device to show an HDMI® output to the display (up to 4K), an HDMI input, and various USB interfaces for wireless conferencing with all accessories and Power Supply Unit along with 1 wireless dongle | Nos | 2
4 | SITC of Universal Switcher with AVoIP enabled HDMI 2.0 and USB-C connectivity, Provides atleast Two HDMI® input and Two USB-C Input and Two HDMI output. | Nos | 2
5 | SITC of 10' touchpanels feature capacitive, edge-to-edge glass touchscreens or high resolution LCD touchscreens that are fully-customizable to meet the User interface foe managing sources | Nos | 2
6 | SITC of high-performance control processor designed for centralized AV control and numerous integrated control ports. Thed Device should have advanced security standards and Gigabit Ethernet, which ensures compatibility with interfaces using a standard network infrastructure.The Device should include all the required license to meet the requirement | Nos | 1
7 | SITC of 8x1G PoE+ 125W 2x1G and 2xSFP Managed Switch. Additional power supply to be considered to manage the POE Budget | Nos | 1
E | Room Scheduler
1 | SITC of 10.1-inch diagonal, Anti-glare and anti-fingerprint Room Scheduling Screen, The device should Integrates with O365, Exchange and Google Calendar,Integrated wall mounting works with all types of surfaces: glass walls, brick walls or dry walls ,15° tilted angle allows for ergonomic use and accessibility, | Nos | 2
F | Racks, Cables and Connectors
1 | SITC of 15Mtr HDMI Cable | Nos | 4
2 | SITC of Two Core with Sheilded speaker Cable | Mtr | 150
3 | SITC of 1.8Mtr HDMI Cable | Nos | 6
4 | SITC of 1.8Mtr USB C Cable | Nos | 2
5 | SITC of 4.6Mtr USB C Cable | Nos | 2
6 | SITC of Control Cable | Mtr | 70
7 | SITC of Cat6A Cable | Mtr | 70
8 | SITC of 24U Rack 100%compatibility with all equipments conforming to DIN 41494 (General industrial standard for equipments) Powder coated finish with seven tank pretreatment process meeting ASTM standard,Grounding & Bonding Options,Fan module Mount provision on top cover along with other accessories | Set | 1
Total (Inclusive of GST)
22 PAX Training Room
A | Display Devices & Accessories
1 | SITC of 85" UHD resolution (3840x2160);Brightness - 500nits; Professional large format display with 3xHDMI input connectivity & built in speakers; Operating environment - Min. 16/7 (with 3 years warranty) | Nos | 1
2 | SITC of Push Pull mount for screens from 65" upto 120". Pop-out system with load bearing capacity of 125Kg. Micro-adjustment of +/-7mm (0.3") at 8 points, Screen height adjustment: +15mm (0.6") for seamless display alignment, Integrated locking mechanism prevents accidental pop-out of mount, Safety screws to prevent unauthorised removal of screens with all mounting hardware included. | Nos | 1
B | Video Conferencing
1 | SITC of 4K Dual Lens Speaker Tracking Camera with 12x Zoom the camera Should have AI-powered Speaker tracking,Autotracking, Automframing and PIP, The camera should be able to five output via HDMI, Ethernet, 3G-SDI, USB. The camera Should include all the required Mounting Accessories. | Nos | 2
2 | Microsoft Teams Room Compute along with a 10 inch Touch Panel to integrate with 3rd Pary peripherals | Nos | 1
C | Audio System
1 | SITC of the microphone array shall use beamforming technology that automatically focuses on whoever is speaking in the room. The beam will automatically detect the position of the person speaking and will follow the person around the room at all times. A threshold for the detection shall be adjustable. Live monitoring of the horizontal and vertical angle of the position.he microphone array shall have a Dante™ interface with two RJ 45 sockets (Primary and Secondary) for digital audio output, supporting both redundant and daisy-chain modes. The microphone array shall also feature a 3-pin terminal for analog audio output. All the associated mounting accessories to be included. | Nos | 1
2 | SITC of Digital signal processor (DSP) shall be open-architecture in configuration and be housed in a 4.25" width, 1U chassis. It shall offer eight (8) user-configurable card-slots for analog audio, USB, GPIO, relay and AES/EBU digital audio support. Additionally, it shall provide native Dante audio networking at 4x4 channels, and be compliant with AES67. The DSP shall feature a dual-core Linux processor with 40-bit floating point architecture.DSP must feature include advanced signal processing algorithms including (but not be limited to) various forms of mixers, equalizers, filters, crossovers, dynamics/gain controls, routers, room combiners, and delays. The program memory shall be nonvolatile and provide program security should power fail. | Nos | 1
3 | SITC of ceiling loudspeaker is equipped with a 4" full-range driver with a coaxial diffraction waveguide. Nominal rating of 50W, max. SPL of 109 dB. The dispersion pattern should be 100° conical. The frequency response ranges from 55 Hz to 20 kHz. The flat protective grille is magnetically attached and can be removed manually. | Nos | 6
4 | SITC of Network compatible, DSP-controlled amplifier with 4 input channels and 4 output channels. CLASS D amplifier technology with 100 W output power at 4 ohm per channel. | Nos | 1
D | Switching & Interface
1 | SITC of Wireless presentation Device to show an HDMI® output to the display (up to 4K) and various USB interfaces for wireless conferencing with all accessories and Power Supply Unit along with 1 wireless dongle | Nos | 1
2 | SITC of wallplate USB‑C® video, HDMI, audio and control up to 330’ (100 m) over a shielded CAT 6A cable | Nos | 1
3 | SITC of Universal Switcher with HDMI 2.0 and USB-C connectivity, Provides One HDMI® input and One USB-C Input and one HDMI output. | Nos | 1
4 | SITC of 4K60 4:4:4 Transmitter for HDMI®, RS‑232, and IR Signal Extension over CATx Cable | Nos | 3
5 | SITC of 4K60 4:4:4 Receiver for HDMI®, RS‑232, and IR Signal Extension over CATx Cable | Nos | 4
6 | SITC of high-performance control processor designed for centralized AV control and numerous integrated control ports. Thed Device should have advanced security standards and Gigabit Ethernet, which ensures compatibility with interfaces using a standard network infrastructure.The Device should include all the required license to meet the requirement | Nos | 1
7 | SITC of 10' touchpanels feature capacitive, edge-to-edge glass touchscreens or high resolution LCD touchscreens that are fully-customizable to meet the User interface foe managing sources | Nos | 1
E | Room Scheduler
1 | SITC of 10.1-inch diagonal, Anti-glare and anti-fingerprint Room Scheduling Screen, The device should Integrates with O365, Exchange and Google Calendar,Integrated wall mounting works with all types of surfaces: glass walls, brick walls or dry walls ,15° tilted angle allows for ergonomic use and accessibility, | Nos | 1
F | Racks, Cables and Connectors
1 | SITC of 15Mtr HDMI Cable | Nos | 4
2 | SITC of Two Core with Sheilded speaker Cable | Mtr | 150
3 | SITC of 1.8Mtr HDMI Cable | Nos | 4
4 | SITC of 1.8Mtr USB C Cable | Nos | 2
5 | SITC of 4.6Mtr USB C Cable | Nos | 2
4 | SITC of Control Cable | Mtr | 50
5 | SITC of Cat6A Cable | Mtr | 50
6 | SITC of 15U Rack 100%compatibility with all equipments conforming to DIN 41494 (General industrial standard for equipments) Powder coated finish with seven tank pretreatment process meeting ASTM standard,Grounding & Bonding Options,Fan module Mount provision on top cover along with other accessories | Set | 1
Total (Inclusive of GST)
16 PAX Training Room
A | Display Devices & Accessories
1 | SITC of 85" UHD resolution (3840x2160);Brightness - 500nits; Professional large format display with 3xHDMI input connectivity & built in speakers; Operating environment - Min. 16/7 (with 3 years warranty) | Nos | 1
2 | SITC of Push Pull mount for screens from 65" upto 120". Pop-out system with load bearing capacity of 125Kg. Micro-adjustment of +/-7mm (0.3") at 8 points, Screen height adjustment: +15mm (0.6") for seamless display alignment, Integrated locking mechanism prevents accidental pop-out of mount, Safety screws to prevent unauthorised removal of screens with all mounting hardware included. | Nos | 1
B | Video Conferencing
1 | SITC of 4K Dual Lens Speaker Tracking Camera with 12x Zoom the camera Should have AI-powered Speaker tracking,Autotracking, Automframing and PIP, The camera should be able to five output via HDMI, Ethernet, 3G-SDI, USB. The camera Should include all the required Mounting Accessories. | Nos | 2
2 | Microsoft Teams Room Compute along with a 10 inch Touch Panel to integrate with 3rd Pary peripherals | Nos | 1
C | Audio System
1 | SITC of the microphone array shall use beamforming technology that automatically focuses on whoever is speaking in the room. The beam will automatically detect the position of the person speaking and will follow the person around the room at all times. A threshold for the detection shall be adjustable. Live monitoring of the horizontal and vertical angle of the position.he microphone array shall have a Dante™ interface with two RJ 45 sockets (Primary and Secondary) for digital audio output, supporting both redundant and daisy-chain modes. The microphone array shall also feature a 3-pin terminal for analog audio output. All the associated mounting accessories to be included. | Nos | 1
2 | SITC of Digital signal processor (DSP) shall be open-architecture in configuration and be housed in a 4.25" width, 1U chassis. It shall offer eight (8) user-configurable card-slots for analog audio, USB, GPIO, relay and AES/EBU digital audio support. Additionally, it shall provide native Dante audio networking at 4x4 channels, and be compliant with AES67. The DSP shall feature a dual-core Linux processor with 40-bit floating point architecture.DSP must feature include advanced signal processing algorithms including (but not be limited to) various forms of mixers, equalizers, filters, crossovers, dynamics/gain controls, routers, room combiners, and delays. The program memory shall be nonvolatile and provide program security should power fail. | Nos | 1
3 | SITC of ceiling loudspeaker is equipped with a 4" full-range driver with a coaxial diffraction waveguide. Nominal rating of 50W, max. SPL of 109 dB. The dispersion pattern should be 100° conical. The frequency response ranges from 55 Hz to 20 kHz. The flat protective grille is magnetically attached and can be removed manually. | Nos | 6
4 | SITC of Network compatible, DSP-controlled amplifier with 4 input channels and 4 output channels. CLASS D amplifier technology with 100 W output power at 4 ohm per channel. | Nos | 1
D | Switching & Interface
1 | SITC of Wireless presentation Device to show an HDMI® output to the display (up to 4K) and various USB interfaces for wireless conferencing with all accessories and Power Supply Unit along with 1 wireless dongle | Nos | 1
2 | SITC of wallplate USB‑C® video, HDMI, audio and control up to 330’ (100 m) over a shielded CAT 6A cable | Nos | 1
3 | SITC of Universal Switcher with HDMI 2.0 and USB-C connectivity, Provides One HDMI® input and One USB-C Input and one HDMI output. | Nos | 1
4 | SITC of 4K60 4:4:4 Transmitter for HDMI®, RS‑232, and IR Signal Extension over CATx Cable | Nos | 3
5 | SITC of 4K60 4:4:4 Receiver for HDMI®, RS‑232, and IR Signal Extension over CATx Cable | Nos | 4
6 | SITC of high-performance control processor designed for centralized AV control and numerous integrated control ports. Thed Device should have advanced security standards and Gigabit Ethernet, which ensures compatibility with interfaces using a standard network infrastructure.The Device should include all the required license to meet the requirement | Nos | 1
7 | SITC of 10' touchpanels feature capacitive, edge-to-edge glass touchscreens or high resolution LCD touchscreens that are fully-customizable to meet the User interface foe managing sources | Nos | 1
E | Room Scheduler
1 | SITC of 10.1-inch diagonal, Anti-glare and anti-fingerprint Room Scheduling Screen, The device should Integrates with O365, Exchange and Google Calendar,Integrated wall mounting works with all types of surfaces: glass walls, brick walls or dry walls ,15° tilted angle allows for ergonomic use and accessibility, | Nos | 1
F | Racks, Cables and Connectors
1 | SITC of 15Mtr HDMI Cable | Nos | 4
2 | SITC of Two Core with Sheilded speaker Cable | Mtr | 150
3 | SITC of 1.8Mtr HDMI Cable | Nos | 4
4 | SITC of 1.8Mtr USB C Cable | Nos | 2
5 | SITC of 4.6Mtr USB C Cable | Nos | 2
4 | SITC of Control Cable | Mtr | 50
5 | SITC of Cat6A Cable | Mtr | 50
6 | SITC of 15U Rack 100%compatibility with all equipments conforming to DIN 41494 (General industrial standard for equipments) Powder coated finish with seven tank pretreatment process meeting ASTM standard,Grounding & Bonding Options,Fan module Mount provision on top cover along with other accessories | Set | 1
Total (Inclusive of GST)
Hall
A | Display Devices & Accessories
1 | SITC of Indoor DVLED : 135inch diagonal(3x1.69m), Fully flip chip COB, 2.40m X 1.35m,4X4 Die-Cast aluminium cabinet configuration, Pixel Pitch: 1.5mm , 16:9 aspect ratio, Brightness: 600 cd/m² , Contrast (10000:1), Wall resolution (W X H): 1920 X 1080, IP605rated(Module), Cabinet dimensions ( W X H X D) : 600mm X 337.5mm X 29.9mm, Viewing angle degree (H 170 / V 170), LED Life (100000 hours), Refresh Rate(3840Hz), 18 bits processing, Front access 5% Spare support, 3 years warranty with required Mounting and control processsors | Nos | 4
2 | SITC of Multiple video windows can be positioned on LED, display based video walls or projector edge blends, EDID manager, custom resolution editor, HDR10, 10-bit processing, HDCP2.2, upto 64000 x 64000 pixels design space on each canvas & capable to show upto 250 windows onto a single active LED or Video wall, minimum 4 canvas, support both progressive & interlaced scan input & output resolution, dynamic labelling engine, storage of minimum 3 GB to store images (logos, Background, etc), upto 32 maps per input (create virtual / cropped sources from a single input), Output mapping, Genlock support, Modular chassis based Video processor with up to 8 x 4K60 4:4:4 HDMI input & 8 x 4K60 4:4:4 HDMI output. | Nos | 1
3 | SITC of 55" UHD resolution (3840x2160);Brightness - 500nits; Professional large format display with 3xHDMI input connectivity & built in speakers; Operating environment - 24/7 (with 3 years warranty) | Nos | 16
4 | SITC of Ceiling/Swivel mount for screens upto 65" with load bearing capacity of 50Kg. Easy swivel at 3 points (wall, central pivot, interface) & tilt adjustment upto +/-15°. Simple Hook on Installation with all mounting hardware included. | Nos | 16
B | Video Conferencing
1 | SITC of 4K AI Auto-Tracking 30x Zoom PTZ Camera with required Mounting Accessories 4K 60 Dual output 30x Zoom AI-powered motion tracking HDMI, Ethernet, 3G-SDI, USB output | Nos | 8
2 | SITC of 4K AI Auto-Tracking 20x Zoom PTZ Camera with required Mounting Accessories 4K 60 Dual output 20x Zoom AI-powered motion tracking HDMI, Ethernet, 3G-SDI, USB output | Nos | 4
3 | SITC of IP Camera Controller Controls up-to total of 255 IP-connected cameras Quick access control of exposure, white balance, focus, PTZ speed and 2 user-assignable keys Supports RTSP Preview on LCD screen Supports RS-232, RS-422, and Ethernet control Supports VISCA and VISCA Over IP control protocols | Nos | 1
4 | Microsoft Teams Room Compute along with a 10 inch Touch Panel to integrate with 3rd Pary peripherals | Nos | 4
C | Audio System
1 | SITC of Full rack 19” 1RU processor mainframe with sixteen user-configured card slots (16 blank cards included.Selectable 48 & 96kHz sampling rates. Integrated license-activated AEC. Dual core processing 40-bit floating DSP .Front panel OLED display with jog wheel. Rear panel includes an Ethernet module with RJ45 connector and internal power supply connection with built-in MOD-Dante-ETH module already pre- installed.Dante mainframe to provide 64x64 I/O channels of Dante network audio. Dual RJ45 Dante and single RJ45 Ethernet connectors.16ch Mic/Line inputs with selectable mic, line, mic gain, and phantom power per input. 32-bit analog to digital converters.6ch Line output. 32-bit digital to analog converters.Softwarelicense activated AEC. 8ch of AEC @ 250ms delay / 16ch @ 100ms. | Nos | 4
2 | SITC of Antenna with Frequency range 470 – 1075 MHz Apex angle (-3 dB) approx. 100° Front-to-back ratio > 14 dB Gain typ. 5 dBi Impedance 50 Ω Connection BNC female, Dimensions 319 x 310 mm Weight Approx. 1100 g (2.43 lbs) Operating temperature range -10 °C - +55 °C (14 °F - 131 °F) Storage temperature range - 20 °C - +85 °C (-4 °F - 185 °F) Relative humidity max. 95 % (non-condensing). | Nos | 4
3 | SITC of Active Antenna Splitter for use with Wireless Digital systems with Antenna splitter 2 x 1:4 or 1 x 1:8, active , Gain in A – out A: 0 ± 1 dB in A – out A1 ... A4: 0 ± 1 dB in B – out B1 ... B4: 0 ± 1 dB, Impedance 50 Ω , Reflection loss 10 dB (all RF outputs), Supply for receivers at A1 to A4 DC 12 V Typically 350 mA, max. 500 mA. Current consumption 210 mA; Total current consumption max. 3 A. Dim.ensions Approx. 212 x 168 x 43 mm (8.35" x 6.61" x 1.69"). Operating temperature range -10 °C - +55 °C (14 °F - 131 °F) Storage temperature range -20 °C - +70 °C (-4 °F - 158 °F) Relative humidity 5 - 95 % (non-condensing) | Nos | 4
4 | SITC of USB charger with Four slots for rechargeable battery. Includes power supply. | Nos | 4
5 | SITC of Digital wireless handheld transmitter with switch compatible with. Rugged metal housing with standard capsule interface for a wide range. Up to 12 hours of runtime, persistent E-Ink display and charging contacts for in-device charging. | Nos | 8
6 | SITC of Wireless lavalier microphone set consists of wireless bodypack transmitter and omni-directional clip-on lavalier microphone with rechargeable batteries | Nos | 4
7 | SITC of gooseneck microphone with one flexible section, an XLR connection and built-in cardioid microphone capsule and wireless table stand | Nos | 4
8 | SITC of Passive full range speaker 8" LF+1" compression driver on Rotable Horn Loaded HF with 230W @8 Ohms and SPL of 125dB and (H X V)90 X 60 or 60 X 40 dispersion angle with wooden enclosure which is ball resistant and textured paint to be provided | Nos | 32
9 | SITC of Passive stage monitor speaker, 12" / 1.4", 500 W, 131 dB SPL max., | Nos | 8
S.NO | DESCRIPTION | UNIT | QTY
10 | SITC of 4-channel digital amplifier (4*600W) with a 4 × 4 routing matrix and the following spec: frequency response : 20 Hz – 20 kHz signal/noise ratio > 103 dB/A THD+N 0,15% (1 kHz, 8 ohms, 3 dB below clipping) dynamic range > 120 dB DSP with 20 independent limiters, FIR filters, 8 × 10 fully parametric filter, 8 compressors, 8 noise gates & delays | Nos | 8
11 | SITC of 22-channel Digital Mixer with 16 Mic Preamps, 9 Motorized Faders, 9" Touchscreen, 18-in/18-out USB Audio Interface, 16-in/16-out Dante Interface, 2-in/2-out USB Recording, DAW Control, and DSP | Nos | 1
D | Control, Switching & Interface
1 | SITC of Wireless presentation Device to show an HDMI® output to the display (up to 4K) and various USB interfaces for wireless conferencing with all accessories and Power Supply Unit along with 1 wireless dongle | Nos | 4
2 | SITC of 10' touchpanels feature capacitive, edge-to-edge glass touchscreens or high resolution LCD touchscreens that are fully-customizable to meet the User interface foe managing sources | Nos | 4
3 | SITC of high-performance control processor designed for centralized AV control and numerous integrated control ports. Thed Device should have advanced security standards and Gigabit Ethernet, which ensures compatibility with interfaces using a standard network infrastructure.The Device should include all the required license to meet the requirement | Nos | 1
4 | SITC of USB‑C® video, HDMI, audio, and control up to 330’ (100 m) over a shielded CAT 6A cable | Nos | 8
5 | SITC of 4K60 4:4:4 Transmitter for HDMI®, RS‑232, and IR Signal Extension over CATx Cable | Nos | 25
6 | SITC of 4K60 4:4:4 Reciever for HDMI®, RS‑232, and IR Signal Extension over CATx Cable | Nos | 30
7 | SITC of Universal Switcher with HDMI 2.0, Provides matrix switching of Four HDMI® input Four HDMI output. | Nos | 4
8 | SITC of 24x10G and 4xSFP+ (shared) Managed Switch Half-Width 24x10G Stackable Managed Switch with 24x10GBASE-T24 Ports Copper 100M / 1G / 10G. 4 Ports SFP+ 1G / 10G (shared) 1 Modular Bay with One (1) 250W Modular PSU included APS250W 480 Gps Switching Fabric Fixed Fan Front-to-Back 37dB Management Options : Ethernet: Out-of-band 1G port (Back) Console: RJ45 RS232 (Back). Mini-USB (Front) Storage: USB (Front) | Nos | 3
9 | SITC of HDMI 4K to USB 3.0 capture card | Nos | 6
E | Cables & connectors
1 | SITC of 15Mtr HDMI Cable | Nos. | 15
2 | SITC of Two Core with Sheilded speaker Cable | Mtr | 1000
3 | SITC of 1.8Mtr HDMI Cable | Nos. | 35
4 | SITC of 1.8Mtr USB C Cable | Nos | 20
5 | SITC of 4.6Mtr USB C Cable | Nos | 20
6 | SITC of Control Cable | Mtr | 500
7 | SITC of Cat6A Cable | Mtr | 800
8 | SITC of USB-C to HDMI Female Active Adapter | Set | 4
9 | SITC of 10Mtr Type A to Type C USB active Cable | Nos. | 24
10 | SITC of 42U Rack 100%compatibility with all equipments conforming to DIN 41494 (General industrial standard for equipments) Powder coated finish with seven tank pretreatment process meeting ASTM standard,Grounding & Bonding Options,Fan module Mount provision on top cover along with other accessories | Set | 2
Total (Inclusive of GST)
Borrowers Lounge
A | Display Devices & Accessories
1 | SITC of Indoor DVLED : 135inch diagonal(3x1.69m), Fully flip chip COB, 2.40m X 1.35m, Die-Cast aluminium cabinet configuration, Pixel Pitch: 1.5mm , 16:9 aspect ratio, Brightness Min of 600 cd/m² , Contrast Atleast: (10000:1), Wall resolution (W X H): 1920 X 1080, IP605rated(Module), Viewing angle degree (H 170 / V 170), LED Life (100000 hours), Refresh Rate(3840Hz), 18 bits processing, Front access 5% Spare support, 3 years warranty with required Mounting and control processsors | Nos | 1
2 | SITC of H.265, Full Hd and 4k Video, Html5, Graphics & Digital Audio, Hdmi Out, Ideal For Looping Video, Simple Html5 Widgets And Animation And Single Touchscreen | Nos | 1
B | Audio System
1 | SITC of ceiling loudspeaker is equipped with a 4" full-range driver with a coaxial diffraction waveguide. Nominal rating of 50W, max. SPL of 109 dB. The dispersion pattern should be 100° conical. The frequency response ranges from 55 Hz to 20 kHz. The flat protective grille is magnetically attached and can be removed manually. | Nos | 6
2 | SITC of Network compatible, DSP-controlled amplifier with 4 input channels and 4 output channels. CLASS D amplifier technology with 100 W output power at 4 ohm per channel. | Nos | 1
C | Switching & Interface
1 | SITC of Wireless presentation Device to show an HDMI® output to the display (up to 4K) and various USB interfaces for wireless conferencing with all accessories and Power Supply Unit along with 1 wireless dongle | Nos | 1
Name of Work: AUDIO & VISUAL SYSTEMS
S.NO | DESCRIPTION | UNIT | QTY | UNIT PRICE | TOTAL PRICE
2 | SITC of 10' touchpanels feature capacitive, edge-to-edge glass touchscreens or high resolution LCD touchscreens that are fully-customizable to meet the User interface foe managing sources | Nos | 1
3 | SITC of high-performance control processor designed for centralized AV control and numerous integrated control ports. Thed Device should have advanced security standards and Gigabit Ethernet, which ensures compatibility with interfaces using a standard network infrastructure.The Device should include all the required license to meet the requirement | Nos | 1
4 | SITC of USB‑C® video, HDMI, audio, and control up to 330’ (100 m) over a shielded CAT 6A cable | Nos | 1
5 | SITC of Collaboration Switcher with HDMI 2.0 and USB-C connectivity, Provides atleast Two HDMI® input and atleast One USB-C Input and atleast one HDMI output. | Nos | 1
6 | SITC of 4K60 4:4:4 Transmitter for HDMI®, RS‑232, and IR Signal Extension over CATx Cable | Nos | 2
7 | SITC of 4K60 4:4:4 Recievers for HDMI®, RS‑232, and IR Signal Extension over CATx Cable | Nos | 3
D | Room Scheduler
1 | SITC of 10.1-inch diagonal, Anti-glare and anti-fingerprint Room Scheduling Screen, The device should Integrates with O365, Exchange and Google Calendar,Integrated wall mounting works with all types of surfaces: glass walls, brick walls or dry walls ,15° tilted angle allows for ergonomic use and accessibility, | Set | 1
E | Cables & connectors
1 | SITC of 15Mtr HDMI Cable | Nos. | 4
2 | SITC of Two Core with Sheilded speaker Cable | Mtr | 150
3 | SITC of 1.8Mtr HDMI Cable | Nos. | 15
4 | SITC of 1.8Mtr USB C Cable | Nos | 2
5 | SITC of 4.6Mtr USB C Cable | Nos | 2
6 | SITC of Control Cable | Mtr | 100
7 | SITC of Cat6A Cable | Mtr | 150
Total (Inclusive of GST)
1 | SITC of 65" UHD resolution (3840x2160);Brightness - 500nits; Professional large format display with 3xHDMI input connectivity & built in speakers; Operating environment - 24/7 (with 3 years warranty) | Nos | 1
2 | SITC of Push Pull mount for screens from 42" upto 75". Pop-out system with load bearing capacity of 50Kg. Micro-adjustment of +/-7.5mm (0.3") at each corner Screen height adjustment: +15mm (0.6") for seamless display alignment, Integrated locking mechanism prevents accidental pop-out of mount, Safety screws to prevent unauthorised removal of screens with all mounting hardware included. | Nos | 1
B | Switching & Interface
1 | SITC of Single-gang wall mount input or output for HDMI® digital video and audio. | Nos | 1
2 | SITC of Wireless presentation Device to show an HDMI® output to the display (up to 4K) and various USB interfaces for wireless conferencing with all accessories and Power Supply Unit along with 1 wireless dongle | Nos | 1
3 | SITC of Collaboration Switcher with HDMI 2.0 and USB-C connectivity, Provides One HDMI® input and One USB-C Input and one HDMI output. | Nos | 1
C | Room Scheduler
1 | SITC of 10.1-inch diagonal, Anti-glare and anti-fingerprint Room Scheduling Screen, The device should Integrates with O365, Exchange and Google Calendar,Integrated wall mounting works with all types of surfaces: glass walls, brick walls or dry walls ,15° tilted angle allows for ergonomic use and accessibility, | Set | 1
D | Cables & connectors
1 | SITC of 15Mtr HDMI Cable | Nos. | 2
2 | SITC of 1.8Mtr HDMI Cable | Nos. | 4
3 | SITC of 1.8Mtr USB C Cable | Nos | 2
4 | SITC of 4.6Mtr USB C Cable | Nos | 2
5 | SITC of Cat6A Cable | Mtr | 20
Total (Inclusive of GST)
ED Cabin
A | Display Devices & Accessories
1 | SITC of 65" UHD resolution (3840x2160);Brightness - 500nits; Professional large format display with 3xHDMI input connectivity & built in speakers; Operating environment - 24/7 (with 3 years warranty) | Nos | 1
2 | SITC of Push Pull mount for screens from 42" upto 75". Pop-out system with load bearing capacity of 50Kg. Micro-adjustment of +/-7.5mm (0.3") at each corner Screen height adjustment: +15mm (0.6") for seamless display alignment, Integrated locking mechanism prevents accidental pop-out of mount, Safety screws to prevent unauthorised removal of screens with all mounting hardware included. | Nos | 1
B | Video Conferencing
1 | SITC all in one UC Video Bar featuring inbuilt microphones and stereo speakers. The device Should have a 4K Ultra HD camera and a maximum of 120 degree FOV. The device should be with a BYOD capability. The device should have capbility to support 2 displays if required.The Audio Pickup of Microphone should be atleast 15ft. | Nos | 1
C | Switching & Interface
1 | SITC of Single-gang wall mount input or output for HDMI® digital video and audio. | Nos | 1
2 | SITC of Wireless presentation Device to show an HDMI® output to the display (up to 4K), an HDMI input, and various USB interfaces for wireless conferencing with all accessories and Power Supply Unit along with 1 wireless dongle | Nos | 1
3 | SITC of Collaboration Switcher with HDMI 2.0 and USB-C connectivity, Provides atleast One HDMI® input and atleast One USB-C Input and atleast one HDMI output. | Nos | 1
D | Cables & connectors
1 | SITC of 1.8Mtr HDMI Cable | Nos. | 4
2 | SITC of 1.8Mtr USB C Cable | Nos | 2
3 | SITC of CAT6A Cable | Mtr | 20
Total (Inclusive of GST)
CafeteriaTownhall
A | Display Devices & Accessories
1 | SITC of 5000 lumen, 4K UHD, 1DLP laser projector, fixed motorized zoom lens,High contrast ratio: 3,000,000:1 | Nos | 1
2 | SITC of Tab tensioned Motorized projection Drop downscreen with 135" inches with 16:10 apect ratio, and silent motor for rolling function The screen should be able to be to controlled by Switch or a RF Remote or Rs232 trigger. | Nos | 1
3 | SITC of 65" UHD resolution (3840x2160);Brightness - 500nits; Professional large format display with 3xHDMI input connectivity & built in speakers; Operating environment - 24/7 (with 3 years warranty) | Nos | 4
4 | SITC of Ceiling Swivel mount for screens upto 65" with load bearing capacity of 50Kg. Easy swivel at 3 points (wall, central pivot, interface) & tilt adjustment upto +/-15°. Simple Hook on Installation with all mounting hardware included. | Nos | 4
B | Video Conferencing
1 | SITC of 4K Dual Lens Speaker Tracking Camera with 12x Zoom the camera Should have AI-powered Speaker tracking,Autotracking, Automframing and PIP, The camera should be able to five output via HDMI, Ethernet, 3G-SDI, USB. The camera Should include all the required Mounting Accessories. | Nos | 2
Name of Work: AUDIO & VISUAL SYSTEMS
S.NO | DESCRIPTION | UNIT | QTY | UNIT PRICE | TOTAL PRICE
2 | Microsoft Teams Room Compute along with a 10 inch Touch Panel to integrate with 3rd Pary peripherals | Nos | 1
C | Audio System
1 | SITC of Digital signal processor (DSP) shall be open-architecture in configuration and be housed in a 4.25" width, 1U chassis. It shall offer eight (8) user-configurable card-slots for analog audio, USB, GPIO, relay and AES/EBU digital audio support. Additionally, it shall provide native Dante audio networking at 4x4 channels, and be compliant with AES67. The DSP shall feature a dual-core Linux processor with 40-bit floating point architecture.DSP must feature include advanced signal processing algorithms including (but not be limited to) various forms of mixers, equalizers, filters, crossovers, dynamics/gain controls, routers, room combiners, and delays. The program memory shall be nonvolatile and provide program security should power fail. | Nos | 1
2 | SITC of Antenna with Frequency range 470 – 1075 MHz Apex angle (-3 dB) approx. 100° Front-to-back ratio > 14 dB Gain typ. 5 dBi Impedance 50 Ω Connection BNC female, Dimensions 319 x 310 mm Weight Approx. 1100 g (2.43 lbs) Operating temperature range -10 °C - +55 °C (14 °F - 131 °F) Storage temperature range - 20 °C - +85 °C (-4 °F - 185 °F) Relative humidity max. 95 % (non-condensing). | Nos | 1
3 | SITC of USB charger with Four slots for rechargeable battery. Includes power supply. | Nos | 1
4 | SITC of Digital wireless handheld transmitter with switch compatible with. Rugged metal housing with standard capsule interface for a wide range. Up to 12 hours of runtime, persistent E-Ink display and charging contacts for in-device charging. | Nos | 2
5 | SITC of Wireless lavalier microphone set consists of wireless bodypack transmitter and omni-directional clip-on lavalier microphone with rechargeable batteries | Nos | 1
6 | SITC of Passive full range speaker 8" LF+1" compression driver on Rotable Horn Loaded HF with 230W @8 Ohms and SPL of 125dB and (H X V)90 X 60 or 60 X 40 dispersion angle with wooden enclosure which is ball resistant and textured paint to be provided | Nos | 4
7 | SITC of 4-channel digital amplifier (4*600W) with a 4 × 4 routing matrix and the following spec: frequency response : 20 Hz – 20 kHz signal/noise ratio > 103 dB/A THD+N 0,15% (1 kHz, 8 ohms, 3 dB below clipping) dynamic range > 120 dB DSP with 20 independent limiters, FIR filters, 8 × 10 fully parametric filter, 8 compressors, 8 noise gates & delays | Nos | 1
D | Control, Switching & Interface
1 | SITC of H.265, Full Hd And 4k Video, Html5, Graphics & Digital Audio, Hdmi Out, Ideal For Looping Video, Simple Html5 Widgets And Animation And Single Touchscreen | Nos | 1
2 | SITC of Wireless presentation Device to show an HDMI® output to the display (up to 4K) and various USB interfaces for wireless conferencing with all accessories and Power Supply Unit along with 1 wireless dongle | Nos | 1
3 | SITC of 10' touchpanels feature capacitive, edge-to-edge glass touchscreens or high resolution LCD touchscreens that are fully-customizable to meet the User interface foe managing sources | Nos | 1
4 | SITC of high-performance control processor designed for centralized AV control and numerous integrated control ports. Thed Device should have advanced security standards and Gigabit Ethernet, which ensures compatibility with interfaces using a standard network infrastructure.The Device should include all the required license to meet the requirement | Nos | 1
5 | SITC of Wall Plate Tx for HDMI & USB‑C® video, audio and control up to 330’ (100 m) over a shielded CAT 6A cable | Nos | 2
6 | SITC of 4K60 4:4:4 Transmitter for HDMI®, RS‑232, and IR Signal Extension over CATx Cable | Nos | 6
7 | SITC of 4K60 4:4:4 Reciever for HDMI®, RS‑232, and IR Signal Extension over CATx Cable | Nos | 8
8 | SITC of Switcher enabled 8 HDMI 2.0 inputs and Eight HDMI output. | Nos | 1
9 | SITC of 24x10G and 4xSFP+ (shared) Managed Switch Half-Width 24x10G Stackable Managed Switch with 24x10GBASE-T24 Ports Copper 100M / 1G / 10G. 4 Ports SFP+ 1G / 10G (shared) 1 Modular Bay with One (1) 250W Modular PSU included APS250W 480 Gps Switching Fabric Fixed Fan Front-to-Back 37dB Management Options : Ethernet: Out-of-band 1G port (Back) Console: RJ45 RS232 (Back). Mini-USB (Front) Storage: USB (Front) | Nos | 1
10 | SITC of HDMI 4K to USB 3.0 capture card | Nos | 1
E | Racks, Cables and Connectors
1 | SITC of 15Mtr HDMI Cable | Nos. | 6
2 | SITC of Two Core with Sheilded speaker Cable | Mtr | 150
3 | SITC of 1.8Mtr HDMI Cable | Nos. | 16
4 | SITC of 1.8Mtr USB C Cable | Nos | 2
5 | SITC of Control Cable | Mtr | 100
6 | SITC of Cat6A Cable | Mtr | 150
7 | SITC of 24U Rack 100%compatibility with all equipments conforming to DIN 41494 (General industrial standard for equipments) Powder coated finish with seven tank pretreatment process meeting ASTM standard,Grounding & Bonding Options,Fan module Mount provision on top cover along with other accessories | Nos | 1
Total (Inclusive of GST)
Executive Dining
A | Display Devices & Accessories
1 | SITC of 75" UHD resolution (3840x2160);Brightness - 500nits; minimum Haze level of 25% Professional large format display with 3xHDMI input connectivity & built in speakers;Operating environment - 24/7 (with 3 years warranty) | Nos | 1
2 | SITC of Push Pull mount for screens from 42" upto 75". Pop-out system with load bearing capacity of 50Kg. Micro-adjustment of +/-7.5mm (0.3") at each corner Screen height adjustment: +15mm (0.6") for seamless display alignment, Integrated locking mechanism prevents accidental pop-out of mount, Safety screws to prevent unauthorised removal of screens with all mounting hardware included. | Nos | 1
B | Audio System
3 | SITC of Ceiling loudspeaker is equipped with a 4" full-range driver with a coaxial diffraction waveguide. With a short-term power rating of up to 200 W, the loudspeaker produces a maximum sound pressure of 109 dB. The dispersion pattern is 100° conical. The frequency response ranges from 55 Hz to 20 kHz | Nos | 2
4 | SITC of Network compatible, DSP-controlled amplifier with 4 input channels and 4 output channels. CLASS D amplifier technology with 100 W output power at 4 ohm per channel. | Nos | 1
C | Control & Interface
1 | SITC of H.265, Full Hd And 4k Video, Html5, Graphics & Digital Audio, Hdmi Out, Ideal For Looping Video, Simple Html5 Widgets And Animation And Single Touchscreen | Nos | 2
D | Cables & connectors
1 | SITC of Two Core with Sheilded speaker Cable | Mtr | 150
2 | SITC of 1.8Mtr HDMI Cable | Nos. | 4
3 | SITC of Control Cable | Mtr | 50
4 | SITC of Cat6A Cable | Mtr | 50
Total (Inclusive of GST)
Dealing Room
A | Display Devices & Accessories
1 | SITC of 43" UHD resolution (3840x2160);Brightness - 500nits; Professional large format display with 3xHDMI input connectivity & built in speakers; Operating environment - 16/7 (with 3 years warranty) | Nos | 4
2 | SITC of Push Pull mount for screens from 42" upto 75". Pop-out system with load bearing capacity of 50Kg. Micro-adjustment of +/-7.5mm (0.3") at each corner Screen height adjustment: +15mm (0.6") for seamless display alignment, Integrated locking mechanism prevents accidental pop-out of mount, Safety screws to prevent unauthorised removal of screens with all mounting hardware included. | Nos | 4
B | Switching & Interface
1 | #REF! | Nos | 1
2 | SITC of Cable cubby with 2 Universal Power Sockets with Passthrough cables 1 HDMI, 1 usb-C, 1 USB-A & 1 LAN | Nos | 2
C | Cables & connectors
1 | SITC of 5Mtr HDMI Cable | Nos | 4
2 | SITC of 1.8Mtr HDMI Cable | Nos | 4
3 | SITC of 4.6Mtr USB C Cable | Nos | 2
4 | SITC of Cat6A Cable | Mtr | 20
Total (Inclusive of GST)
Multipurpose Room
A | Display Devices & Accessories
1 | SITC of 55" UHD resolution (3840x2160);Brightness - 500nits; Professional large format display with 3xHDMI input connectivity & built in speakers; Operating environment - 24/7 (with 3 years warranty) | Nos | 2
2 | SITC of Push Pull mount for screens from 42" upto 75". Pop-out system with load bearing capacity of 50Kg. Micro-adjustment of +/-7.5mm (0.3") at each corner Screen height adjustment: +15mm (0.6") for seamless display alignment, Integrated locking mechanism prevents accidental pop-out of mount, Safety screws to prevent unauthorised removal of screens with all mounting hardware included. | Nos | 2
B | Audio
1 | SITC of Karaoke set up | Nos | 1
C | Cables & connectors
1 | SITC of 15Mtr HDMI Cable | Nos. | 1
2 | SITC of Two Core with Sheilded speaker Cable | Mtr | 50
3 | SITC of 1.8Mtr HDMI Cable | Nos. | 4
4 | SITC of 1.8Mtr USB C Cable | Nos | 2
5 | SITC of 4.6Mtr USB C Cable | Nos | 2
6 | SITC of CAT6A Cable | Mtr | 50
Total (Inclusive of GST)
Podcast Room
A | Display Devices & Accessories
1 | SITC of 24" iMac with Apple M3 Chip, 16GB Ram, 512GB SSD along with Power Adaptor and Full Version of Final Cut Pro Video Editing Software to Edit the recorded videos with wireless keyboard and mouse. | Nos | 1
B | Video
1 | SITC of Auto Tracking, 12x optical zoom, 80.5 degree 2160p60/59.94/30/29.97/25; 1080p60/59.94/50/29.97/25; 720p60/50/30/25; NDI®¦HX2+HDMI2.0+3G-SDI+USB2.0+Line In PSU, RS232 cable, USB cable, Remote Controller | Nos | 2
2 | SITC of Tripod | Nos | 2
3 | SITC of 8 x IP video inputs via NDI®, resolution-independent, NDI inputs supporting video input in any combination of standard formats, resolutions, and frame rates 4 x independent IP video mix outputs via NDI® 2 x streaming video output, independently configurable, with simultaneous stream archive 4 x mini display port with output adapters 3 x of the outputs support multiple viewers using standard display resolutions 4 x M/E buses supporting video re-entry • 1 x Mix/Effect channel per bus with support for up to 2 sources • 2 x KEY layers per bus 2 x DSK channels 4 x recording channels from either NDI® inputs or Mix outputs. Records and retains alpha channel data Integrated waveform and vectorscope, full field rate with digital calibration, color preview and support for ITU- R Rec. 709 Storage • Capacity varies by format, resolution and file specification • Supports recording to external storage via USB 250GB SSD4 & 4 PoE+ (802.3at) Ports, 60 Watt power capability 2 x 1 Gigabit NIC | Nos | 1
C | Audio System
1 | SITC of Lavalier microphones set that include Bodypack Transmitter, Receiver,02 Rod antenna with Power Supply | Nos | 2
2 | SITC of Dynamic Microphone | Nos | 2
3 | SITC of Microphone stand | Nos | 2
4 | SITC of Digital Audio Mixing Desk | Nos | 1
5 | SITC of Control room audio moniter headphones with mounting accessories | Nos | 1
D | Switching & Interface
1 | SITC of 8x1G PoE+ 125W 2x1G and 2xSFP Managed Switch. Additional power supply to be considered to manage the POE Budget | Nos | 1
E | Room Scheduler
1 | SITC of 10.1-inch diagonal, Anti-glare and anti-fingerprint Room Scheduling Screen, The device should Integrates with O365, Exchange and Google Calendar,Integrated wall mounting works with all types of surfaces: glass walls, brick walls or dry walls ,15° tilted angle allows for ergonomic use and accessibility, | Nos | 1
F | Cables & connectors
1 | SITC of 15Mtr HDMI Cable | Nos. | 4
2 | SITC of 1.8Mtr HDMI Cable | Nos. | 15
3 | SITC of 1.8Mtr USB C Cable | Nos | 2
4 | SITC of 4.6Mtr USB C Cable | Nos | 2
3 | SITC of Control Cable | Mtr | 100
4 | SITC of CAT6A Cable | Mtr | 150
5 | SITC of USB-C to HDMI Female Active Adapter | Set | 1
6 | SITC of Two Core with Sheilded speaker Cable | Mtr | 50
7 | SITC of 24U Rack 100%compatibility with all equipments conforming to DIN 41494 (General industrial standard for equipments) Powder coated finish with seven tank pretreatment process meeting ASTM standard,Grounding & Bonding Options,Fan module Mount provision on top cover | Set | 1
Total (Inclusive of GST)
Chief Vigilance Office
A | Display Devices & Accessories
1 | SITC of 65" UHD resolution (3840x2160);Brightness - 500nits; Professional large format display with 3xHDMI input connectivity & built in speakers; Operating environment - 16/7 (with 3 years warranty) | Nos | 1
2 | SITC of Push Pull mount for screens from 42" upto 75". Pop-out system with load bearing capacity of 50Kg. Micro-adjustment of +/-7.5mm (0.3") at each corner Screen height adjustment: +15mm (0.6") for seamless display alignment, Integrated locking mechanism prevents accidental pop-out of mount, Safety screws to prevent unauthorised removal of screens with all mounting hardware included. | Nos | 1
B | Video Conferencing
1 | SITC all in one UC Video Bar featuring inbuilt microphones and stereo speakers. The device Should have a 4K Ultra HD camera and a maximum of 120 degree FOV. The device should be With native Teams MS teams with a 10' Touch Panel and with a BYOD capability. The device should have capbility to support 2 displays if required.The Audio Pickup of Microphone should be atleast 15ft. | Nos | 1
C | Switching & Interface
1 | SITC of Cable cubby with 2 Universal Power Sockets with Passthrough cables 1 HDMI, 1 usb-C, 1 USB-A & 1 LAN | Nos | 1
2 | SITC of Wireless presentation Device to show an HDMI® output to the display (up to 4K), an HDMI input, and various USB interfaces for wireless conferencing with all accessories and Power Supply Unit along with 1 wireless dongle | Nos | 1
3 | SITC of Collaboration Switcher with HDMI 2.0 and USB-C connectivity, Provides atleast One HDMI® input and atleast One USB-C Input and atleast one HDMI output. | Nos | 1
D | Cables & connectors
1 | SITC of 15Mtr HDMI Cable | Nos | 2
2 | SITC of 1.8Mtr HDMI Cable | Nos | 4
3 | SITC of 1.8Mtr USB C Cable | Nos | 2
4 | SITC of 4.6Mtr USB C Cable | Nos | 2
5 | SITC of Cat6A Cable | Mtr | 20
Total (Inclusive of GST)
Functional Director Cabin
A | Display Devices & Accessories
1 | SITC of 65" UHD resolution (3840x2160);Brightness - 500nits; Professional large format display with 3xHDMI input connectivity & built in speakers; Operating environment - 16/7 (with 3 years warranty) | Nos | 1
2 | SITC of Push Pull mount for screens from 42" upto 75". Pop-out system with load bearing capacity of 50Kg. Micro-adjustment of +/-7.5mm (0.3") at each corner Screen height adjustment: +15mm (0.6") for seamless display alignment, Integrated locking mechanism prevents accidental pop-out of mount, Safety screws to prevent unauthorised removal of screens with all mounting hardware included. | Nos | 1
B | Video Conferencing
1 | SITC all in one UC Video Bar featuring inbuilt microphones and stereo speakers. The device Should have a 4K Ultra HD camera and a maximum of 120 degree FOV. The device should be With native Teams MS teams with a 10' Touch Panel and with a BYOD capability. The device should have capbility to support 2 displays if required.The Audio Pickup of Microphone should be atleast 15ft. | Nos | 1
C | Switching & Interface
1 | SITC of Cable cubby with 2 Universal Power Sockets with Passthrough cables 1 HDMI, 1 usb-C, 1 USB-A & 1 LAN | Nos | 1
2 | SITC of Wireless presentation Device to show an HDMI® output to the display (up to 4K), an HDMI input, and various USB interfaces for wireless conferencing with all accessories and Power Supply Unit along with 1 wireless dongle | Nos | 1
3 | SITC of Collaboration Switcher with HDMI 2.0 and USB-C connectivity, Provides atleast One HDMI® input and atleast One USB-C Input and atleast one HDMI output. | Nos | 1
D | Cables & connectors
1 | SITC of 15Mtr HDMI Cable | Nos | 2
2 | SITC of 1.8Mtr HDMI Cable | Nos | 4
3 | SITC of 1.8Mtr USB C Cable | Nos | 2
4 | SITC of 4.6Mtr USB C Cable | Nos | 2
5 | SITC of Cat6A Cable | Mtr | 20
Total (Inclusive of GST)
CMD Cabin
A | Display Devices & Accessories
1 | SITC of 85" UHD resolution (3840x2160);Brightness - 500nits; Professional large format display with 3xHDMI input connectivity & built in speakers; Operating environment - Min. 16/7 (with 3 years warranty) | Nos | 1
2 | SITC of 75" UHD resolution (3840x2160);Brightness - 500nits; Professional large format display with 3xHDMI input connectivity & built in speakers; Operating environment - 24/7 (with 3 years warranty) | Nos | 1
3 | SITC of Push Pull mount for screens from 65" upto 120". Pop-out system with load bearing capacity of 125Kg. Micro-adjustment of +/-7mm (0.3") at 8 points, Screen height adjustment: +15mm (0.6") for seamless display alignment, Integrated locking mechanism prevents accidental pop-out of mount, Safety screws to prevent unauthorised removal of screens with all mounting hardware included. | Nos | 2
B | Video Conferencing
1 | SITC all in one UC Video Bar featuring inbuilt microphones and stereo speakers. The device Should have Dual 4K Ultra HD camera and a FOV of 70-120. The device should be With native Teams MS teams with a 10' Touch Panel and with a BYOD capability. The device should have capbility to support 2 displays if required.The Audio Pickup of Microphone should be atleast 25ft. | Nos | 1
C | Switching & Interface
1 | SITC of Cable cubby with 2 Universal Power Sockets with Retractable cables 1 HDMI, 1 usb-C, 1 USB-A & 1 LAN | Nos | 2
2 | SITC of Wireless presentation Device to show an HDMI® output to the display (up to 4K), an HDMI input, and various USB interfaces for wireless conferencing with all accessories and Power Supply Unit along with 1 wireless dongle | Nos | 1
3 | SITC of Universal Switcher with HDMI 2.0 and USB-C connectivity, Provides Two HDMI® input and two USB-C Input and one HDMI output. | Nos | 2
D | Cables & connectors
1 | SITC of 15Mtr HDMI Cable | Nos | 2
2 | SITC of 1.8Mtr HDMI Cable | Nos | 6
3 | SITC of 1.8Mtr USB C Cable | Nos | 4
4 | SITC of CAT6A Cable | Mtr | 20
Total (Inclusive of GST)
25 PAX Boardroom
A | Display Devices & Accessories
1 | SITC of Indoor DVLED : 135inch diagonal(3x1.69m), Fully flip chip COB, 2.40m X 1.35m,4X4 Die-Cast aluminium cabinet configuration, Pixel Pitch: 1.2mm , 16:9 aspect ratio, Brightness: 600 cd/m² , Contrast (10000:1), Wall resolution (W X H): 1920 X 1080, IP605rated(Module), Cabinet dimensions ( W X H X D) : 600mm X 337.5mm X 29.9mm, Viewing angle degree (H 170 / V 170), LED Life (100000 hours), Refresh Rate(3840Hz), 18 bits processing, Front access 5% Spare support, 3 years warranty with required Mounting and control processsors | Nos | 1
3 | SITC of 65" UHD resolution (3840x2160);Brightness - 500nits; Professional large format display with 3xHDMI input connectivity & built in speakers; Operating environment - 24/7 (with 3 years warranty) | Nos | 5
4 | SITC of Push Pull mount for screens from 42" upto 75". Pop-out system with load bearing capacity of 50Kg. Micro-adjustment of +/-7.5mm (0.3") at each corner Screen height adjustment: +15mm (0.6") for seamless display alignment, Integrated locking mechanism prevents accidental pop-out of mount, Safety screws to prevent unauthorised removal of screens with all mounting hardware included. | Nos | 5
5 | SITC of 4K60 4:4:4 Transmitter for HDMI®, RS‑232, and IR Signal Extension over CATx Cable | Nos | 5
6 | SITC of 4K60 4:4:4 Receiver for HDMI®, RS‑232, and IR Signal Extension over CATx Cable | Nos | 5
B | Video Conferencing
1 | SITC of 4K dual lens camera with a 20X Total zoom PTZ camera and a second AI lens with 95˚FOV. Equipped with built-in audio sensor the camera should detects human voices up to 10M and offers audio tracking function. AI technology such as Smart Gallery and gesture control can capture every attendees up-close with premium video quality | Nos | 5
2 | AI based Camera Switcher which uses directional audio data with preset camera positions to focus on the active speaker. | Nos | 1
3 | Microsoft Teams Room Compute along with a 10 inch Touch Panel to integrate with 3rd Pary peripherals | Nos | 1
C | Audio System
1 | SITC of the microphone array shall use beamforming technology that automatically focuses on whoever is speaking in the room. The beam will automatically detect the position of the person speaking and will follow the person around the room at all times. A threshold for the detection shall be adjustable. Live monitoring of the horizontal and vertical angle of the position.he microphone array shall have a Dante™ interface with two RJ 45 sockets (Primary and Secondary) for digital audio output, supporting both redundant and daisy-chain modes. The microphone array shall also feature a 3-pin terminal for analog audio output. All the associated mounting accessories to be included. | Nos | 3
2 | SITC of Full rack 19” 1RU processor mainframe with sixteen user-configured card slots (16 blank cards included.Selectable 48 & 96kHz sampling rates. Integrated license-activated AEC. Dual core processing 40-bit floating DSP .Front panel OLED display with jog wheel. Rear panel includes an Ethernet module with RJ45 connector and internal power supply connection with built-in MOD-Dante-ETH module already pre- installed.Dante mainframe to provide 64x64 I/O channels of Dante network audio. Dual RJ45 Dante and single RJ45 Ethernet connectors.16ch Mic/Line inputs with selectable mic, line, mic gain, and phantom power per input. 32-bit analog to digital converters.6ch Line output. 32-bit digital to analog converters.Softwarelicense activated AEC. 8ch of AEC @ 250ms delay / 16ch @ 100ms. | Nos | 1
3 | SITC of Ceiling loudspeaker is equipped with a 4" full-range driver with a coaxial diffraction waveguide. With a short-term power rating of up to 200 W, the loudspeaker produces a maximum sound pressure of 109 dB. The dispersion pattern is 100° conical. The frequency response ranges from 55 Hz to 20 kHz | Nos | 12
4 | SITC of 4-channel digital amplifier (4*600W) with a 4 × 4 routing matrix and the following spec: frequency response : 20 Hz – 20 kHz, signal/noise ratio > 103 dB/A THD+N 0,15% (1 kHz, 8 ohms, 3 dB below clipping) dynamic range > 120 dB, DSP with 20 independent limiters, FIR filters, 8 × 10 fully parametric filter, 8 compressors, 8 noise gates & delays | Nos | 2
D | Control, Switching & Interface
1 | SITC of Cable cubby with 2 Universal Power Sockets with Electrical Retractable cables 1 HDMI, 1 usb-C, 1 USB- A & 1 LAN (Only 3 will be AV Enabled) | Nos | 8
2 | SITC of Wireless presentation Device to show an HDMI® output to the display up to 4K and various USB interfaces for wireless conferencing with all accessories and Power Supply Unit along with atleast 1 wireless dongle | Nos | 1
3 | SITC of AVoIP enabled Encoder & Decoder pair or switcher with HDMI 2.0 and USB-C connectivity, Provides atleast Two HDMI® input and Two USB-C Input and Two HDMI output. Bundled Solution | Nos | 3
4 | SITC of 10' touchpanels feature capacitive, edge-to-edge glass touchscreens or high resolution LCD touchscreens that are fully-customizable to meet the User interface foe managing sources | Nos | 1
5 | SITC of high-performance control processor designed for centralized AV control and numerous integrated control ports. Thed Device should have advanced security standards and Gigabit Ethernet, which ensures compatibility with interfaces using a standard network infrastructure.The Device should include all the required license to meet the requirement | Nos | 1
6 | SITC of Switcher with 8 HDMI 2.0 inputs and 8 HDMI output. | Nos | 1
E | Room Scheduler
1 | SITC of 10.1-inch diagonal, Anti-glare and anti-fingerprint Room Scheduling Screen, The device should Integrates with O365, Exchange and Google Calendar,Integrated wall mounting works with all types of surfaces: glass walls, brick walls or dry walls ,15° tilted angle allows for ergonomic use and accessibility, | Nos | 1
F | Cables & connectors
1 | SITC of 15Mtr HDMI Cable | Nos | 6
2 | SITC of Two Core with Sheilded speaker Cable | Mtr | 150
3 | SITC of 1.8Mtr HDMI Cable | Nos | 15
4 | SITC of 1.8Mtr USB C Cable | Nos | 4
5 | SITC of 4.6Mtr USB C Cable | Nos | 4
6 | SITC of Control Cable | Mtr | 100
7 | SITC of CAT6A Cable | Mtr | 150
8 | SITC of 10Mtr Type A to Type C USB active Cable | Nos | 6
9 | SITC of 42U Rack 100%compatibility with all equipments conforming to DIN 41494 (General industrial standard for equipments) Powder coated finish with seven tank pretreatment process meeting ASTM standard,Grounding & Bonding Options,Fan module Mount provision on top cover | Set | 1
Total (Inclusive of GST)
Ante Room Lounge
A | Display Devices & Accessories
1 | SITC of 75" UHD resolution (3840x2160);Brightness - 500nits; Professional large format display with 3xHDMI input connectivity & built in speakers; Operating environment - 24/7 (with 3 years warranty) | Nos | 1
2 | SITC of Push Pull mount for screens from 42" upto 75". Pop-out system with load bearing capacity of 50Kg. Micro-adjustment of +/-7.5mm (0.3") at each corner Screen height adjustment: +15mm (0.6") for seamless display alignment, Integrated locking mechanism prevents accidental pop-out of mount, Safety screws to prevent unauthorised removal of screens with all mounting hardware included. | Nos | 1
B | Control & Interface
1 | SITC of H.265, Full Hd And 4k Video, Html5, Graphics & Digital Audio, Hdmi Out, Ideal For Looping Video, Simple Html5 Widgets And Animation And Single Touchscreen | Nos | 1
C | Switching & Interface
1 | SITC of Single-gang wall mount input or output for HDMI® digital video and audio. | Nos | 1
2 | SITC of Wireless presentation Device to show an HDMI® output to the display (up to 4K), an HDMI input, and various USB interfaces for wireless conferencing with all accessories and Power Supply Unit along with 1 wireless dongle | Nos | 1
3 | SITC of Universal Switcher with HDMI 2.0 and USB-C connectivity, Provides Two HDMI® input and two USB-C Input and one HDMI output. | Nos | 1
D | Cables & connectors
1 | SITC of 1.8Mtr HDMI Cable | Nos | 3
2 | SITC of 1.8Mtr USB C Cable | Nos | 2
3 | SITC of CAT6A Cable | Mtr | 40
Total (Inclusive of GST)
Pre-Function Area
A | Display Devices & Accessories
1 | SITC of 75" UHD resolution (3840x2160);Brightness - 500nits; Professional large format display with 3xHDMI input connectivity & built in speakers; Operating environment - 24/7 (with 3 years warranty) | Nos | 1
2 | SITC of Push Pull mount for screens from 42" upto 75". Pop-out system with load bearing capacity of 50Kg. Micro-adjustment of +/-7.5mm (0.3") at each corner Screen height adjustment: +15mm (0.6") for seamless display alignment, Integrated locking mechanism prevents accidental pop-out of mount, Safety screws to prevent unauthorised removal of screens with all mounting hardware included. | Nos | 1
B | Control & Interface
1 | SITC of H.265, Full Hd And 4k Video, Html5, Graphics & Digital Audio, Hdmi Out, Ideal For Looping Video, Simple Html5 Widgets And Animation And Single Touchscreen | Nos | 1
C | Cables & connectors
1 | SITC of 1.8Mtr HDMI Cable | Nos | 1
2 | SITC of CAT6A Cable | Mtr | 80
Total (Inclusive of GST)
GYM
A | Display Devices & Accessories
1 | SITC of 55" UHD resolution (3840x2160);Brightness - 500nits; Professional large format display with 3xHDMI input connectivity & built in speakers; Operating environment - 24/7 (with 3 years warranty) | Nos | 4
2 | SITC of Push Pull mount for screens from 42" upto 75". Pop-out system with load bearing capacity of 50Kg. Micro-adjustment of +/-7.5mm (0.3") at each corner Screen height adjustment: +15mm (0.6") for seamless display alignment, Integrated locking mechanism prevents accidental pop-out of mount, Safety screws to prevent unauthorised removal of screens with all mounting hardware included. | Nos | 4
B | Control & Interface
1 | SITC of H.265, Full Hd And 4k Video, Html5, Graphics & Digital Audio, Hdmi Out, Ideal For Looping Video, Simple Html5 Widgets And Animation And Single Touchscreen | Nos | 4
C | Audio System
1 | SITC of Passive full range speaker 8" LF+1" compression driver on Rotable Horn Loaded HF with 230W @8 Ohms and SPL of 125dB and (H X V)90 X 60 or 60 X 40 dispersion angle with wooden enclosure which is ball resistant and textured paint to be provided | Nos | 4
2 | SITC of 4-channel digital amplifier (4*600W) with a 4 × 4 routing matrix and the following spec: frequency response : 20 Hz – 20 kHz signal/noise ratio > 103 dB/A THD+N 0,15% (1 kHz, 8 ohms, 3 dB below clipping) dynamic range > 120 dB DSP with 20 independent limiters, FIR filters, 8 × 10 fully parametric filter, 8 compressors, 8 noise gates & delays | Nos | 1
3 | Wireless Streaming Preamplifier, In addition to Wi-Fi, this preamp should also support Bluetooth® and AirPlay®, | Nos | 1
D | Cables & connectors
1 | SITC of 1.8Mtr HDMI Cable | Nos | 4
2 | SITC of CAT6A Cable | Mtr | 80
3 | SITC of Two Core with Sheilded speaker Cable | Mtr | 150
Total (Inclusive of GST)
JumbaYoga & Meditation Room
A | Display Devices & Accessories
1 | SITC of 85" UHD resolution (3840x2160);Brightness - 500nits; Professional large format display with 3xHDMI input connectivity & built in speakers; Operating environment - 16/7 (with 3 years warranty) | Nos | 2
2 | SITC of Push Pull mount for screens from 65" upto 120". Pop-out system with load bearing capacity of 125Kg. Micro-adjustment of +/-7mm (0.3") at 8 points, Screen height adjustment: +15mm (0.6") for seamless display alignment, Integrated locking mechanism prevents accidental pop-out of mount, Safety screws to prevent unauthorised removal of screens with all mounting hardware included. | Nos | 2
B | Control & Interface
1 | SITC of H.265, Full Hd And 4k Video, Html5, Graphics & Digital Audio, Hdmi Out, Ideal For Looping Video, Simple Html5 Widgets And Animation And Single Touchscreen | Nos | 2
C | Audio System
1 | SITC of Passive full range speaker 8" LF+1" compression driver on Rotable Horn Loaded HF with 230W @8 Ohms and SPL of 125dB and (H X V)90 X 60 or 60 X 40 dispersion angle with wooden enclosure which is ball resistant and textured paint to be provided | Nos | 4
2 | SITC of 4-channel digital amplifier (4*600W) with a 4 × 4 routing matrix and the following spec: frequency response : 20 Hz – 20 kHz signal/noise ratio > 103 dB/A THD+N 0,15% (1 kHz, 8 ohms, 3 dB below clipping) dynamic range > 120 dB DSP with 20 independent limiters, FIR filters, 8 × 10 fully parametric filter, 8 compressors, 8 noise gates & delays | Nos | 1
3 | Wireless Streaming Preamplifier, In addition to Wi-Fi, this preamp should also support Bluetooth® and AirPlay®, | Nos | 2
D | Cables & connectors
1 | SITC of 1.8Mtr HDMI Cable | Nos | 2
2 | SITC of CAT6A Cable | Mtr | 160
3 | SITC of Two Core with Sheilded speaker Cable | Mtr | 200
Total (Inclusive of GST)
Creche
A | Display Devices & Accessories
1 | SITC of 65" UHD resolution (3840x2160);Brightness - 500nits; Professional large format display with 3xHDMI input connectivity & built in speakers; Operating environment - 24/7 (with 3 years warranty) | Nos | 2
2 | SITC of Push Pull mount for screens from 42" upto 75". Pop-out system with load bearing capacity of 50Kg. Micro-adjustment of +/-7.5mm (0.3") at each corner Screen height adjustment: +15mm (0.6") for seamless display alignment, Integrated locking mechanism prevents accidental pop-out of mount, Safety screws to prevent unauthorised removal of screens with all mounting hardware included. | Nos | 2
B | Audio System
1 | SITC of Ceiling loudspeaker is equipped with a 4" full-range driver with a coaxial diffraction waveguide. With a short-term power rating of up to 200 W, the loudspeaker produces a maximum sound pressure of 109 dB. The dispersion pattern is 100° conical. The frequency response ranges from 55 Hz to 20 kHz | Nos | 8
2 | SITC of Network compatible, DSP-controlled amplifier with 4 input channels and 4 output channels. CLASS D amplifier technology with 100 W output power at 4 ohm per channel. | Nos | 1
C | Control & Interface
1 | SITC of H.265, Full Hd And 4k Video, Html5, Graphics & Digital Audio, Hdmi Out, Ideal For Looping Video, Simple Html5 Widgets And Animation And Single Touchscreen | Nos | 2
D | Cables & connectors
1 | SITC of 15Mtr HDMI Cable | Nos. | 2
2 | SITC of Two Core with Sheilded speaker Cable | Mtr | 150
3 | SITC of 1.8Mtr HDMI Cable | Nos. | 2
4 | SITC of Control Cable | Mtr | 50
5 | SITC of Cat6A Cable | Mtr | 50
Total (Inclusive of GST)
SOC
A | Display Devices & Accessories
1 | SITC of Indoor Active LED : 110 inch diagonal(2.4 x 1.35m), Fully flip chip COB, Die-Cast aluminium cabinet configuration, Pixel Pitch: 1.2mm, 16:9 aspect ratio, minimum Brightness: 600 cd/m² , upto Contrast (10000:1), Wall resolution (W X H): 1920 X 1080, IP605rated(Module), Viewing angle degree (H 170 / V 170), LED Life range of 100000 hours, Refresh Rate(3840Hz), 18 bits processing, Front access 5% Spare support, 3 years warranty with required Mounting and controls | Nos | 2
B | Video Conferencing
1 | SITC of 4K Dual Lens Speaker Tracking Camera with 12x Zoom the camera Should have AI-powered Speaker tracking,Autotracking, Automframing and PIP, The camera should be able to five output via HDMI, Ethernet, 3G-SDI, USB. The camera Should include all the required Mounting Accessories. | Nos | 1
2 | Microsoft Teams Room Compute along with a 10 inch Touch Panel to integrate with 3rd Pary peripherals | Nos | 1
C | Audio System
1 | SITC of the microphone array shall use beamforming technology that automatically focuses on whoever is speaking in the room. The beam will automatically detect the position of the person speaking and will follow the person around the room at all times. A threshold for the detection shall be adjustable. Live monitoring of the horizontal and vertical angle of the position.he microphone array shall have a Dante™ interface with two RJ 45 sockets (Primary and Secondary) for digital audio output, supporting both redundant and daisy-chain modes. The microphone array shall also feature a 3-pin terminal for analog audio output. All the associated mounting accessories to be included. | Nos | 1
2 | SITC of digital signal processor (DSP) which shall be open-architecture in configuration. It shall offer 16 user- configurable card-slots for analog audio, USB, GPIO, relay and AES/EBU digital audio support. and shall provide optional Dante audio networking at 64x64 channels, and be compliant with AES67.The DSP shall feature a dual-core Linux processor with 40-bit floating point architecture. It Should handle up-to 64x64 bi- directional channels of audio over Dante™, using standard CatX cable with no proprietary switches | Nos | 1
3 | SITC of Ceiling loudspeaker is equipped with a 4" full-range driver with a coaxial diffraction waveguide. With a short-term power rating of up to 200 W, the loudspeaker produces a maximum sound pressure of 109 dB. The dispersion pattern is 100° conical. The frequency response ranges from 55 Hz to 20 kHz | Nos | 4
4 | SITC of Network compatible, DSP-controlled amplifier with 4 input channels and 4 output channels. CLASS D amplifier technology with 100 W output power at 4 ohm per channel. | Nos | 1
D | Switching & Interface
1 | SITC of Network based Video Wall Controller with 8 x HDMI Inputs, 04 x UHD HDMI Outputs, Web URL based Inputs, Network based PC Inputs and Wall Management Software | Nos | 1
2 | SITC of Wireless presentation Device to show an HDMI® output to the display (up to 4K) and various USB interfaces for wireless conferencing with all accessories and Power Supply Unit along with 1 wireless dongle | Nos | 1
3 | SITC of HDMI & USB‑C® wallplate for video, audio and control up to 330’ (100 m) over a shielded CAT 6A cable | Nos | 1
4 | SITC of Collaboration Switcher with HDMI 2.0 and USB-C connectivity, Provides atleast Two HDMI® input and atleast Two USB-C Input and atleast Two HDMI output. | Nos | 1
5 | SITC of 4K60 4:4:4 Transmitter for HDMI®, RS‑232, and IR Signal Extension over CATx Cable | Nos | 3
6 | SITC of 4K60 4:4:4 Receiver for HDMI®, RS‑232, and IR Signal Extension over CATx Cable | Nos | 4
7 | SITC of high-performance control processor designed for centralized AV control and numerous integrated control ports. Thed Device should have advanced security standards and Gigabit Ethernet, which ensures compatibility with interfaces using a standard network infrastructure.The Device should include all the required license to meet the requirement | Nos | 1
E | Racks, Cables and Connectors
1 | SITC of 15Mtr HDMI Cable | Nos | 6
2 | SITC of Two Core with Sheilded speaker Cable | Mtr | 200
3 | SITC of 1.8Mtr HDMI Cable | Nos | 8
4 | SITC of 1.8Mtr USB C Cable | Nos | 2
5 | SITC of 4.6Mtr USB C Cable | Nos | 2
6 | SITC of Control Cable | Mtr | 50
7 | SITC of Cat6A Cable | Mtr | 80
8 | SITC of 15U Rack 100%compatibility with all equipments conforming to DIN 41494 (General industrial standard for equipments) Powder coated finish with seven tank pretreatment process meeting ASTM standard,Grounding & Bonding Options,Fan module Mount provision on top cover along with other accessories | Set | 1
NOC
A | Display Devices & Accessories
1 | SITC of Indoor DVLED : 135inch diagonal(3x1.69m), Fully flip chip COB, 2.40m X 1.35m,4X4 Die-Cast aluminium cabinet configuration, Pixel Pitch: 1.5mm , 16:9 aspect ratio, Brightness: 600 cd/m² , Contrast (10000:1), Wall resolution (W X H): 1920 X 1080, IP605rated(Module), Cabinet dimensions ( W X H X D) : 600mm X 337.5mm X 29.9mm, Viewing angle degree (H 170 / V 170), LED Life (100000 hours), Refresh Rate(3840Hz), 18 bits processing, Front access 5% Spare support, 3 years warranty with required Mounting and control processsors | Nos | 1
B | Video Conferencing
1 | SITC of 4K Dual Lens Speaker Tracking Camera with 12x Zoom the camera Should have AI-powered Speaker tracking,Autotracking, Automframing and PIP, The camera should be able to five output via HDMI, Ethernet, 3G-SDI, USB. The camera Should include all the required Mounting Accessories. | Nos | 1
2 | Microsoft Teams Room Compute along with a 10 inch Touch Panel to integrate with 3rd Pary peripherals | Nos | 1
C | Audio System
1 | SITC of the microphone array shall use beamforming technology that automatically focuses on whoever is speaking in the room. The beam will automatically detect the position of the person speaking and will follow the person around the room at all times. A threshold for the detection shall be adjustable. Live monitoring of the horizontal and vertical angle of the position.he microphone array shall have a Dante™ interface with two RJ 45 sockets (Primary and Secondary) for digital audio output, supporting both redundant and daisy-chain modes. The microphone array shall also feature a 3-pin terminal for analog audio output. All the associated mounting accessories to be included. | Nos | 1
2 | SITC of digital signal processor (DSP) which shall be open-architecture in configuration. It shall offer 16 user- configurable card-slots for analog audio, USB, GPIO, relay and AES/EBU digital audio support. and shall provide optional Dante audio networking at 64x64 channels, and be compliant with AES67.The DSP shall feature a dual-core Linux processor with 40-bit floating point architecture. It Should handle up-to 64x64 bi- directional channels of audio over Dante™, using standard CatX cable with no proprietary switches | Nos | 1
3 | SITC of Ceiling loudspeaker is equipped with a 4" full-range driver with a coaxial diffraction waveguide. With a short-term power rating of up to 200 W, the loudspeaker produces a maximum sound pressure of 109 dB. The dispersion pattern is 100° conical. The frequency response ranges from 55 Hz to 20 kHz | Nos | 4
4 | SITC of Network compatible, DSP-controlled amplifier with 4 input channels and 4 output channels. CLASS D amplifier technology with 100 W output power at 4 ohm per channel. | Nos | 1
D | Switching & Interface
1 | SITC of Network based Video Wall Controller with 8 x HDMI Inputs, 04 x UHD HDMI Outputs, Web URL based Inputs, Network based PC Inputs and Wall Management Software | Nos | 1
2 | SITC of Wireless presentation Device to show an HDMI® output to the display (up to 4K) and various USB interfaces for wireless conferencing with all accessories and Power Supply Unit along with 1 wireless dongle | Nos | 1
3 | SITC of HDMI & USB‑C® wallplate for video, audio and control up to 330’ (100 m) over a shielded CAT 6A cable | Nos | 1
4 | SITC of Collaboration Switcher with HDMI 2.0 and USB-C connectivity, Provides atleast Two HDMI® input and atleast Two USB-C Input and atleast Two HDMI output. | Nos | 1
5 | SITC of 4K60 4:4:4 Transmitter for HDMI®, RS‑232, and IR Signal Extension over CATx Cable | Nos | 3
6 | SITC of 4K60 4:4:4 Receiver for HDMI®, RS‑232, and IR Signal Extension over CATx Cable | Nos | 8
7 | SITC of high-performance control processor designed for centralized AV control and numerous integrated control ports. Thed Device should have advanced security standards and Gigabit Ethernet, which ensures compatibility with interfaces using a standard network infrastructure.The Device should include all the required license to meet the requirement | Nos | 1
E | Racks, Cables and Connectors
1 | SITC of 15Mtr HDMI Cable | Nos | 6
2 | SITC of Two Core with Sheilded speaker Cable | Mtr | 200
3 | SITC of 1.8Mtr HDMI Cable | Nos | 8
4 | SITC of 1.8Mtr USB C Cable | Nos | 2
5 | SITC of 4.6Mtr USB C Cable | Nos | 2
6 | SITC of Control Cable | Mtr | 50
7 | SITC of Cat6A Cable | Mtr | 80
8 | SITC of 15U Rack 100%compatibility with all equipments conforming to DIN 41494 (General industrial standard for equipments) Powder coated finish with seven tank pretreatment process meeting ASTM standard,Grounding & Bonding Options,Fan module Mount provision on top cover along with other accessories | Set | 1
Displays on Trolley
A | Display Devices & Accessories
1 | SITC of 55" UHD resolution (3840x2160);Brightness - 500nits; Professional large format display with 3xHDMI input connectivity & built in speakers; Operating environment - 24/7 (with 3 years warranty) | Nos | 1
2 | SITC of Trolley based mount for screens upto 60" with load bearing capacity of 50Kg. It can mount screens in landscape & potrait orientation. Easy to move with non-marking 3” locking/braked castors & alternative levelling feet. It must have cable management holes with all mounting hardware included. | Nos | 1
B | Cables & connectors
1 | SITC of 5Mtr HDMI Cable | Nos | 1
Total (Inclusive of GST)
Workplace Signage
A | Display Devices & Accessories
1 | SITC of 55" UHD resolution (3840x2160);Brightness - 500nits; Professional large format display with 3xHDMI input connectivity & built in speakers; Operating environment - 24/7 (with 3 years warranty) | Nos | 1
2 | SITC of Push Pull mount for screens from 42" upto 75". Pop-out system with load bearing capacity of 50Kg. Micro-adjustment of +/-7.5mm (0.3") at each corner Screen height adjustment: +15mm (0.6") for seamless display alignment, Integrated locking mechanism prevents accidental pop-out of mount, Safety screws to prevent unauthorised removal of screens with all mounting hardware included. | Nos | 1
B | Control & Interface
1 | SITC of H.265, Full Hd And 4k Video, Html5, Graphics & Digital Audio, Hdmi Out, Ideal For Looping Video, Simple Html5 Widgets And Animation And Single Touchscreen | Nos | 1
C | Cables & connectors
1 | SITC of 1.8Mtr HDMI Cable | Nos | 1
2 | SITC of CAT6A Cable | Mtr | 80
Total (Inclusive of GST)
Workplace Signage Software
A | Display Devices & Accessories
1 | SITC of CMS License for 1 organisation With license for upto 100 players with Support package for upto 3 years | Nos | 1
Total (Inclusive of GST)
Outdoor Signage
A | Display Devices & Accessories
1 | SITC of OUTdoor DVLED : Aluminium profile, Pixel Pitch: 4mm or bettter ,Brightness: ≥4500 nits, IP65, Viewing angle degree (H 160 / V 90), Refresh Rate(3840Hz)Front & Rear access ,5% Spare support, 5 years warranty with required Mounting and LED controller to display Quad image/video (The final size Will be as measurement based on final size deployed) | SQft | 1008
B | Control & Interface
1 | SITC of H.265, Full Hd And 4k Video, Html5, Graphics & Digital Audio, Hdmi Out, Ideal For Looping Video, Simple Html5 Widgets And Animation And Single Touchscreen | Nos | 1
2 | SITC of Multiple video windows can be positioned on LED, display based video walls or projector edge blends, displaying any of the sources connected to Processor, Up-Down-Cross Conversion, EDID manager, custom resolution editor, Modular chassis based Ultra-compact processor with Integrated front button panel for up to 4 x 4K HDMI input & 2 x 4K HDMI output | Nos | 1
3 | SITC of 4K60 4:4:4 Transmitter for HDMI®, RS‑232, and IR Signal Extension over CATx Cable | Nos | 2
4 | SITC of 4K60 4:4:4 Receiver for HDMI®, RS‑232, and IR Signal Extension over CATx Cable | Nos | 2
C | Cables & connectors
1 | SITC of 15Mtr HDMI Cable | Nos | 2
2 | SITC of 1.8Mtr HDMI Cable | Nos | 2
Total (Inclusive of GST)
25 PAX Boardroom - OPTION 2
A | Display Devices & Accessories
1 | SITC of Indoor DVLED : 135inch diagonal(3x1.69m), Fully flip chip COB, 2.40m X 1.35m,4X4 Die-Cast aluminium cabinet configuration, Pixel Pitch: 1.2mm , 16:9 aspect ratio, Brightness: 600 cd/m² , Contrast (10000:1), Wall resolution (W X H): 1920 X 1080, IP605rated(Module), Cabinet dimensions ( W X H X D) : 600mm X 337.5mm X 29.9mm, Viewing angle degree (H 170 / V 170), LED Life (100000 hours), Refresh Rate(3840Hz), 18 bits processing, Front access 5% Spare support, 3 years warranty with required Mounting and control processsors | Nos | 1
3 | SITC of 65" UHD resolution (3840x2160);Brightness - 500nits; Professional large format display with 3xHDMI input connectivity & built in speakers; Operating environment - 24/7 (with 3 years warranty) | Nos | 5
4 | SITC of Push Pull mount for screens from 42" upto 75". Pop-out system with load bearing capacity of 50Kg. Micro-adjustment of +/-7.5mm (0.3") at each corner Screen height adjustment: +15mm (0.6") for seamless display alignment, Integrated locking mechanism prevents accidental pop-out of mount, Safety screws to prevent unauthorised removal of screens with all mounting hardware included. | Nos | 5
5 | SITC of 4K60 4:4:4 Transmitter for HDMI®, RS‑232, and IR Signal Extension over CATx Cable | Nos | 5
6 | SITC of 4K60 4:4:4 Receiver for HDMI®, RS‑232, and IR Signal Extension over CATx Cable | Nos | 5
B | Video Conferencing
1 | SITC of 4K dual lens camera with a 20X Total zoom PTZ camera and a second AI lens with 95˚FOV. Equipped with built-in audio sensor the camera should detects human voices up to 10M and offers audio tracking function. AI technology such as Smart Gallery and gesture control can capture every attendees up-close with premium video quality | Nos | 5
2 | AI based Camera Switcher which uses directional audio data with preset camera positions to focus on the active speaker. | Nos | 1
3 | Microsoft Teams Room Compute along with a 10 inch Touch Panel to integrate with 3rd Pary peripherals | Nos | 1
C | Audio System
1 | SITC of Wired table boundary microphone with half-cardioid pickup pattern & integrated mute buttom. It's sturdy housing and high-quality microphone capsule guarantees optimum speech intelligibility with required XLR wiring and accessories. Additional required analog audio input card rated at 48V for powering up the microphone based on final make of DSP. | Nos | 13
2 | SITC of Full rack 19” 1RU processor mainframe with sixteen user-configured card slots (16 blank cards included.Selectable 48 & 96kHz sampling rates. Integrated license-activated AEC. Dual core processing 40-bit floating DSP .Front panel OLED display with jog wheel. Rear panel includes an Ethernet module with RJ45 connector and internal power supply connection with built-in MOD-Dante-ETH module already pre- installed.Dante mainframe to provide 64x64 I/O channels of Dante network audio. Dual RJ45 Dante and single RJ45 Ethernet connectors.16ch Mic/Line inputs with selectable mic, line, mic gain, and phantom power per input. 32-bit analog to digital converters.6ch Line output. 32-bit digital to analog converters.Softwarelicense activated AEC. 8ch of AEC @ 250ms delay / 16ch @ 100ms. | Nos | 2
3 | SITC of Ceiling loudspeaker is equipped with a 4" full-range driver with a coaxial diffraction waveguide. With a short-term power rating of up to 200 W, the loudspeaker produces a maximum sound pressure of 109 dB. The dispersion pattern is 100° conical. The frequency response ranges from 55 Hz to 20 kHz | Nos | 12
4 | SITC of 4-channel digital amplifier (4*600W) with a 4 × 4 routing matrix and the following spec: frequency response : 20 Hz – 20 kHz, signal/noise ratio > 103 dB/A THD+N 0,15% (1 kHz, 8 ohms, 3 dB below clipping) dynamic range > 120 dB, DSP with 20 independent limiters, FIR filters, 8 × 10 fully parametric filter, 8 compressors, 8 noise gates & delays | Nos | 2
D | Control, Switching & Interface
1 | SITC of Cable cubby with 2 Universal Power Sockets with Electrical Retractable cables 1 HDMI, 1 usb-C, 1 USB- A & 1 LAN (Only 3 will be AV Enabled) | Nos | 8
2 | SITC of Wireless presentation Device to show an HDMI® output to the display up to 4K and various USB interfaces for wireless conferencing with all accessories and Power Supply Unit along with atleast 1 wireless dongle | Nos | 1
3 | SITC of AVoIP enabled Encoder & Decoder pair or switcher with HDMI 2.0 and USB-C connectivity, Provides atleast Two HDMI® input and Two USB-C Input and Two HDMI output. Bundled Solution | Nos | 3
4 | SITC of 10' touchpanels feature capacitive, edge-to-edge glass touchscreens or high resolution LCD touchscreens that are fully-customizable to meet the User interface foe managing sources | Nos | 1
5 | SITC of high-performance control processor designed for centralized AV control and numerous integrated control ports. Thed Device should have advanced security standards and Gigabit Ethernet, which ensures compatibility with interfaces using a standard network infrastructure.The Device should include all the required license to meet the requirement | Nos | 1
6 | SITC of Switcher with 8 HDMI 2.0 inputs and 8 HDMI output. | Nos | 1
E | Room Scheduler
1 | SITC of 10.1-inch diagonal, Anti-glare and anti-fingerprint Room Scheduling Screen, The device should Integrates with O365, Exchange and Google Calendar,Integrated wall mounting works with all types of surfaces: glass walls, brick walls or dry walls ,15° tilted angle allows for ergonomic use and accessibility, | Nos | 1
F | Cables & connectors
1 | SITC of 15Mtr HDMI Cable | Nos | 6
2 | SITC of Two Core with Sheilded speaker Cable | Mtr | 150
3 | SITC of 1.8Mtr HDMI Cable | Nos | 15
4 | SITC of 1.8Mtr USB C Cable | Nos | 4
5 | SITC of 4.6Mtr USB C Cable | Nos | 4
6 | SITC of Control Cable | Mtr | 100
7 | SITC of CAT6A Cable | Mtr | 150
8 | SITC of 10Mtr Type A to Type C USB active Cable | Nos | 6
9 | SITC of 42U Rack 100%compatibility with all equipments conforming to DIN 41494 (General industrial standard for equipments) Powder coated finish with seven tank pretreatment process meeting ASTM standard,Grounding & Bonding Options,Fan module Mount provision on top cover | Set | 1
Total (Inclusive of GST)

## SUMMARY OF Kitchen Work BOQ
Name of Project: “Interior Fit-out work in the office space of Power Finance Corporation Limited, Tower-H, World Trade Centre, Nauroji Nagar, New Delhi-110029 including Operation & Maintenance for 06 years”
SUMMARY OF Kitchen Work BOQ
S no. | AREAS | Amount (In Rs.)
Original Scope
1 | WHITE GOODS ALL FLOORS ( GF+FF+2F+3F+4F+5F+6F+8F+9F)
2 | KITCHEN EQUIPMENT 7TH FLOOR +BASEMENT
3 | PNG Gas Pipeline
4 | Total Amount

## PNG PIPELINE
Bill of Quantities
Name of Project: “Interior Fit-out work in the office space of Power Finance Corporation Limited, Tower-H, World Trade Centre, Nauroji Nagar, New Delhi-110029 including Operation & Maintenance for 06 years”
Name of Work: PNG PIPELINE
Sr. No. | Product / Item Description | Unit | Qty | RATE | AMOUNT
1 | Bourdon Type Pressure Gauge in 100mm dial size of pressure range 0-4,14kgf/cm2 with valve.(HGuru) - 5 Nos. | Job | 1
2 | Burner Pipe: 4 feet (surksha) - 16 Nos.
3 | Needle Compact valve: (3/8"X3/8") - 21 nos.
4 | Nut Bullnose '1'- 4 Nos.
5 | CS Ball Valve Size: 40mm (L&T)- 5 Nos.
6 | Ball Valve CS 1.5" #150 Make Pune Gas- 3 nos.
7 | Ball Valve CS 1/2" Thread, Make Pune Gas-16 nos.
8 | Ms Meter Flange - 1 Nos.
9 | ASTM-A-106 Schedule 40 C Class Pipe with forged fitting duly welded and Including all fitting material(socket,clamp,tee,short bend, etc.) Size :40mm | Per MTR. (Appro x.) | 180
10 | Testing ,Painting & Installation & THIRD PARTY INSEPECTION WITH REPORTS | Job | 1
11 | SOLONOID VALVE 25MM (MADAS)
GAS DETECTION SYSTEM
12 | GAS LEAK DETECTOR SENSOR (GASVIGIL)-15 nos. MULTIPLE SENSOR PANEL 4 ZONE (GASVIGIL)- 2 Nos.,HOOTER (4 nos.), WIRE 4 CORE FOR CONNECTION WITH CONDUIT (300 mtr approx), Ms Meter Flange (1No.), | Job | 1
13 | INSTALLATION CHARGES FOR GAS DETECTION SYSTEM
14 | Third Party Inspection
Sub-Total