## SUMMARY
S.NO. | ITEM DESCRIPTION | SUPPLY AMOUNT (INR) | INSTALLATION AMOUNT (INR) | TOTAL AMOUNT (INR)
1 | AC & Ventilation Equipment | 322060 | 62700 | 384760
2 | Air filtration & Monitor | 1204560 | 40800 | 1245360
3 | PIPING & ACCESSERIES | 104680 | 18755 | 123435
4 | DUCTING & AIR TERMINAL WORKS | 2009480 | 461538 | 2471018
5 | INSULATION | 658000 | 145200 | 803200
6 | VFD & Starter Panel | 172580 | 6500 | 179080
7 | VRF SYSTEM FOR CRITICAL AREA | 1246716 | 145130 | 1391846
8 | VAV BOXES | 1338830 | 150700 | 1489530
9 | HYDROGEN EXHAUST | 181020 | 11150 | 192170
| TOTAL AMOUNT (INR) | 7237926 | 1042473 | 8280399

## BOQ
S. NO | Item Description | UOM | Total Qty | Supply Rate | Install Rate | Supply Amount | Install Amount
1 | EQUIPMENTS
1.1 | AIR HANDLING UNITS FLOOR MOUNTED OR CEILING SUSPENDED
Supply, installation, testing and commissioning of factory fabricated Double Skinned Chilled Water Air- handling unit floor mounted (Horizontal / Vertical to suit site) or ceiling suspended horizontal type, fabricated out of extruded aluminium section with 0.6mm pre-plasticized / pre-coated Galvanised steel sheet outside & 0.6 mm plain Galvanised steel sheet inside with EC Plug Fans IE5 type motor, 4/6/8 Row cooling coil made of Aluminium finned Copper tube with coil section of copper header and MS adaptor, filter section with filters as mentioned below,UV section of 200 mm in length complete with UV lamps, polished stainless steel drain pan made out of 20 G sheet duly insulated. Drain pan insulation shall be minimum 19mm closed cell nitrile. The AHU panels shall be insulated with 48 mm thick & 48 Kg/m³ density PU foam. The maximum permissible sound pressure level of the AHU shall not exceed 50-60 dbA measured at 1.5 m from AHU surface for the recommended range of operation. The motor & fan assembly shall be mounted on Aluminium extruded section only. The complete AHU shall conform to standard specification. AHU shall be supplied with commissioning filter of both type wherever applicable as specified above which shall be replaced with actual pre and esp filters. The capacity of Air-handlers shall be as follows. Mixing box with aluminium volume control dampers for return air and fresh air complete as per specifications and drawings.
The AHU panel shall be insulated with 48 mm thick injected fire retardant PUF of density 40+/-2 Kg/m³ . Marine light with limit switch shall be provided . The complete AHU shall conform to standard spec.The face velocity across cooling / heating coil, filters should not exceed 500 FPM. The capacities of air handling shall be as follows, All paint shall be Low VOC
The polished stainless steel drain pan of 1.25 mm (18 G) thick duly insulated with 13 mm thick nitrile rubber under cooling coil shall be provided. Motor & belt drive package/ direct driven arrangement, belt guard etc for belt driven blower without face and bypass dampers.
NOTE (1) The Air velocity across the filter should not be more then 500 FPM. (2) CSU- Ceiling Suspended Units ¦ FM- Floor Mounted (3) All CSU shall be provided with drain Pumps (4) All AHUs shall be with S.A damper. (5) Chilled water coil should have inlet and outlet temperature as 6.7°C & 12.2°C respectively. (6) Suitable Rubber bellow required for chilled water pipes to avoid the direct contact . (7) All fans should be AMCA certified. (8) All AHUs shall be provided with EC Plug Fan & ESP filter (Electrostatic Precipitator) of suitable capacity
1.1.4 | CSU AHU -3000 CFM, 12.0 TR with 50mm S.P. with MERV-7 filters, with 4 row deep cooling Coil. For Cafeteria | Nos | 1 | 200000 | 25000 | 200000 | 25000
1.2 | Electronic Thermostat BMS compatible
Supply of Electronic Heating and Cooling Thermostat (AC 220 V and DC 24 V) with LCD display with necessary control cabling for AHUs & FCUs complete as required. The thermostat shall have provision of setting of space temperature and display of the same, fixing of suitable transformer complete with interconnecting wiring between 2 way modulating valve and thermostat.
1.2.1 | Supply, Installation & Testing Temperature control with Wiring complete as required for AHU's. All Thermostats for Summer/Winter System of AHUs/ CSUs Shall be Heat Cool with change over. | Nos | 1 | 5500 | 450 | 5500 | 450
2 | FLEXIBLE CANVASS CONNECTIONS
| Supply, Installation, Testing of 125mm deep antivibration flexible joints at the outlet of air handling units/inline fans. Flexible connections shall be constructed using imported fire retardant fabric with extruded aluminium frame/flange on both sides of approved make. | RM | 25 | 1450 | 1200 | 36250 | 30000
1.3 | Box Type Inline Fan
Supply, Installation, Testing & Commissioning of inline fans complete with sheet metal casing, 25mm thick open cell nitrile rubber acoustic insulation, direct driven centrifugal fan, motor with proper protection and inspection door. Fan shall be suitable for operation on 220+6 % volts, 50 Hz,1 phase AC power supply. Flanges to be provided on both sides to facilitate duct connections. Fan shall be installed as shown in the drawings and will be of following characteristics : All single phase inline fans shall be provided with factory fitted speed regulators. All Fans Should be complete with Plug Top & necessary power cable. Fans shall have low noise level in rage of 35-40dBA @3m and shall be suitable for indoor installations.
1.3.1 | 2700 CFM @ 25 mm wg(For Gents Toilet) | Nos. | 1 | 36450 | 2250 | 36450 | 2250
1.3.2 | 1600 CFM @ 25 mm wg(For Ladies Toilet) | Nos. | 1 | 29800 | 2000 | 29800 | 2000
1.3.3 | 400 CFM @ 15 mm wg(For Cafeteria) | Nos. | 1 | 7560 | 1500 | 7560 | 1500
1.3.4 | 350 CFM @ 15 mm wg(For Hand wash) | Nos. | 1 | 6500 | 1500 | 6500 | 1500
| TOTAL ITEM NO. 1 (AC & Ventilation Equipment) |  |  |  |  | 322060 | 62700
2.1 | CO2 SENSOR for rooms with display
| SITC of CO2 Sensor for rooms only with display with (Wi-Fi Enable/BMS Compatible) | Nos | 2 | 11130 | 850 | 22260 | 1700
2.2 | INDOOR AIR QUALITY MONITOR WITHOUT DISPLAY
| Supply, Installation, Testing & commissioning of IAQ Monitor to measure the levels of PM 2.5, VOCs, CO2, Temperature, Humidity on a real time basis. The IAQ Monitor shall be RS485 enabled and should be capable of getting connected with Wi-Fi. Units should have dedicated data browse i.e. sim card etc. The Monitor should be capable of sending the indoor air quality information on display Screen/Mobile/Workstation as per Client's requirement. The Monitor should indicate the quality of air through changing the colours as per the NAAQS standards and should meet the WELL building standards. Quoted price shall be inclusive of all necessary arrangement as required to make the unit proper functional. (LED Screen not included.) Quoted shall also be inclusive of individual network arrangement as required for monitoring/integration. | Nos | 1 | 42000 | 1100 | 42000 | 1100
Central Air Cleaner for AHUs
Electrically Charged Filter Supply, Installation, Testing & Commissioning of hybrid Air purification for ceiling suspended Ductable indoor units and AHU The air purification system should be suitable to reduce harmful pollutants like particulate matter (PMx), PM 2.5, allergens, pollen, smoke, bacteria, pathogens etc. based on below principle technology viz; Impingement, Polarisation and Agglomeration as a passive air purification It should be a slim structured unit specifically designed for integration in Return Air path of ceiling suspended indoor units/AHU to centrally capture. It should be equivalent to Merv-14 or Higher efficiency for AHU and Ductable* Units with low pressure drop. It should have 3x working principles and it should be aluminium based or powder coated steel casing and should be self-contained. It should be a US patented technology with UL certified components. Unit shall be suitable for the air quantity similar to AHUs. It should have pre-filter, polarizer grid, e-filter, run hour meter, clogging indicator light for filters. CAC shall be suitable for operation on 220±6 % volts, 50 Hz,1 phase AC power supply. The units shall meet ANSI/ASHRAE 52.2 standards and have valid test report to verify filtration efficiency. The Basic Media of Electric Filter shall Carry Class 2 Fire Rating Listing by UL.The EAC filter/Electrostatic precipitator (ESP), which have Metal based collection plate shall not be accepted. The Supplier shall carry UL2998 certification or at least Acknowledgement letter from UL2998 for testing against Zero Ozone Emission. The system shall be integrated with the existing pre-section filter area of AHU. The test report for pressure drop need to be submitted for passive air purification and the same shall be demonstrated at site."
Electronic filters should consist of an Internet of Things (IoT) based Smart Filtration option employing a 3-Tier Architecture. This architecture would serve to identify pressure drops across the filter, indicating when a cleaning & replacement is necessary due to clogged filters.
Vendor to study local ambient air data and quality of air before proposing & finalizing air cleaner. Unit should be suitable to meet all IAQ parameters i.e. PM 2.5, PM-10 etc. as per ASHRAE/ANSI/ NEA & OSHA etc.
Technical submittals with supported catalogue shall be submitted for approval prior to procurement. Quoted price shall be inclusive of all necessary arrangement as required for fixing of filter section within AHU and control wiring etc.
a. | 15000 CFM Floor Mounted AHU | Nos | 2 | 357000 | 10000 | 714000 | 20000
b. | 3000 CFM Ceiling Suspended AHU | Nos | 1 | 210000 | 5000 | 210000 | 5000
2.3 | BIO POLAR IONISER
The Active Air Purification system should consist of Supply, Installation, Testing and commissioning of Bipolar Ionisation System. The Bipolar Ionisation System must be a combination of Tube Based Model and Needle Point Model (Needle Point should have Nitinol (nickel titanium) Needles) and Carbon Fibre Brush Model, System should produce positive and negative ions for creating a Bio Climate rich in ions and hence neutralising harmful pollutants including pathogens, Volatile Organic Compounds and Particulate Matter.
Manufacturers shall provide Test report from Internationally/Nationally recognized Lab for proven efficacy on below pathogens with minimum kill rates for the following pathogens given the allotted time and in a space condition: a) SARS-CoV-2 (COVID-19) Human Strain b) MS2 Bacteriophage (Surrogates COVID-19) c) Omicron Variant of SARS-CoV-2 d) H1N1 e) Total Bacterial Count Reduction rate of more than 90% from NABL Accredited Lab f) Yeas & Mold/Total fungal count Reduction rate of more than 90% from NABL Accredited Lab
Total Nos. of ionisers shall be as per air quantity distributed in individual duct drawn from main plenum/ AHUs in approved shop drawing.
a. | 15000 CFM Floor Mounted AHU | Nos | 2 | 98000 | 5000 | 196000 | 10000
b. | 3000 CFM Ceiling Suspended AHU | Nos | 1 | 20300 | 3000 | 20300 | 3000
| TOTAL ITEM NO. 2 (Air filtration & Monitor) |  |  |  |  | 1204560 | 40800
3 | M.S. CHILLED WATER PIPING
Supply, Installation, Testing and Commissioning of following nominal sizes of M.S. E.R.W. tube (black steel) heavy class Chilled water piping (with necessary clamps, vibration isolators and fitttings but excluding valves, strainers, gauges) duly insulated with 25mm/32mm thick closed cell elastomeric insulation in tubing form Class O as per specifications and drawings covered with a layer of 120 gm/sqm polythene sheet (vapour barrier) and finally applying 0.5mm aluminium sheet cladding complete with type 3, grade I roofing felt strip (as per IS:1322 as amended upto date) at the joints repairing of damage to building etc. as per specifications and as required. (Gripple Wire & Hangers can be used at site for support) The following insulation thickness shall be followed : a) pipes size upto 150 mm-32 mm insulation thickness b) pipes size upto 200 mm to 300 mm-50 mm insulation thickness c) pipes size above 300 mm-75 mm insulation thickness Adhesive shall be selected as per IGBC guidelines
Note:- The pipes size 150 mm & below shall be M.S. `C' class as per IS:1239 and pipes size above 150 mm shall be black steel pipe heavy class as per IS:3589, from minimum 6.0 mm thick M.S. sheet for pipes from 200mm dia upto 400 mm dia.
3.1 | 40 MM | RMT |  |  |  | 0 | 0
3.2 | 50 MM | RMT | 25 | 1170 | 400 | 29250 | 10000
Note:- Actual qty as per site
4 | BUTTERFLY VALVE
Supply, installation, testing and commissioning of butterfly valves along with flanges as per specifications and drawings. (PN-16)
4.1 | 40 MM | No |  |  |  | 0 | 0
4.2 | 50 MM | No | 2 | 2850 | 450 | 5700 | 900
5 | PIBC VALVE FOR AHU
Supply, installation, testing and commissioning of PIBC Valves with CI body SS disc nitrile rubber seal & O - ring & PN 16 pressure rating, confirm to BS 5155, IS 13095, with IP-55 actuator, capable of accepting up to 24 VAC and upto 20mA electric signal and providing similar transduced feed back output to control system as required & as specified.
The valve actuator shall be electronic type with brushless DC motor. The actuator's angle of rotation shall be 900. It shall be without any limit switches and shall be overload proof. It shall have an indicator to indicate the position and push-button to disengage the gear train for manual operation. All related electrical connection and accessories required shall be inclusive.
| 40mm Dia, Maximum | No |  |  |  | 0 | 0
| 50mm Dia, Maximum | No | 1 | 50750 | 5000 | 50750 | 5000
6 | Y-STRAINER
Supply, installation, testing and commissioning of Y - strainer along with flanges connection complete as per specifications and drawings. (PN-16)
a | 40 MM | No |  |  |  | 0 | 0
b. | 50 MM | No | 1 | 3780 | 755 | 3780 | 755
7 | PRESSURE GUAGE
| Pressure Gauge 6" Dial ( 0 To 6 Kg/CM2 ) with approved ball valve. Industrial type pressure gauges with SS syphon, gun metal / brass valves complete as required | No | 2 | 3400 | 400 | 6800 | 800
8 | THERMOMETERS WITH THERMOWELL
| Providing and fixing thermometer Mercury filled V form type complete as per specifications and drawings. | No | 2 | 3200 | 400 | 6400 | 800
9 | AUTOMATIC AIR VENTS
| Providing and fixing auto air vent purging valve complete as per specification and drawings. | No | 1 | 2000 | 500 | 2000 | 500
| TOTAL ITEM NO. 3 (PIPING & ACCESSERIES) |  |  |  |  | 104680 | 18755
10 | FACTORY FABRICATED DUCTING
Supply hollow partial pieces, Assembling, installation, testing and commissioning of 120 GSM G.S.S. metal ducting & as per ISI specifications & tender drawings. The price shall include with rolamite / TDF Corner flanges with nut bolt, cleat for clamping, self adhesive gasket / sealant (neoprene gasket) & supports Wire Rope Hangers or as per Duct size standard manufacturer etc. (Gripple Wire & Hangers can be used at site for support)
| 24 G (0.60 mm) - 1 mm to 750 mm | SMT | 345 | 880 | 240 | 303600 | 82800
| 22 G (0.80 mm) - 751 mm to 1500 mm | SMT | 268 | 970 | 240 | 259960 | 64320
| 20 G (1.0 mm) - 1501 mm to 2250 mm | SMT |  |  |  | 0 | 0
| 18 G (1.2 mm) - 2250 mm to Above & Plenum | SMT | 62 | 1200 | 240 | 74400 | 14880
11 | SITE FABRICATED DUCTING
Supply GSS sheets, fabricate ducting at site, installation, testing and commissioning of 120 GSM G.S.S. metal ducting & as per ISI specifications & tender drawings. The price shall include with rolamite / TDF Corner flanges with nut bolt, cleat for clamping, self adhesive gasket / sealant (neoprene gasket) & supports Wire Rope Hangers etc. (Gripple Wire & Hangers can be used at site for support)
| 24 G (0.60 mm) - 1 mm to 750 mm | SMT | 34 | 880 | 240 | 29920 | 8160
| 22 G (0.80 mm) - 751 mm to 1500 mm | SMT | 26 | 970 | 240 | 25220 | 6240
| 20 G (1.0 mm) - 1501 mm to 2250 mm | SMT |  |  |  | 0 | 0
| 18 G (1.2 mm) - 2250 mm to Above & Plenum | SMT | 6 | 1200 | 240 | 7200 | 1440
12 | Flat Oval Spiral Duct
Supply hollow partial pieces, Assembling, installation, testing and commissioning of G.S.S. metal ducting & as per ISI specifications & tender drawings. The price shall include with rolamite / TDF Corner flanges with nut bolt, cleat for clamping, self adhesive gasket / sealant (neoprene gasket) & supports (GI Threaded Rod & Chilly clamp (Thickness & Width shall be as per manufacturer Standard) by or Wire Rope Hangers etc. (Gripple Wire & Hangers can be used at site for support)
With 13 mm thick internal insulation
| 22 G (0.80 mm) | SMT | 215 | 1470 | 260 | 316050 | 55900
| 20 G (1.0 mm) | SMT | 0 |  |  | 0 | 0
13 | DUCO PAINT (For Flat Oval Exposed Duct)
| Supply and Application of minimum two coats of Duco Paint of colour and shade as approved by the Architects for exposed flat oval spiral/round ducts. Quoted price shall be inclusive of primer before paint and all necessary arrangement as required for providing the paint over duct. | SMT | 215 | 260 | 160 | 55900 | 34400
14 | Supply, Installation and Testing of extruded aluminium powder coated Air Transfer Grilles to be provided at the door of toilets/pantry. | SqM | 2 | 8950 | 3500 | 17900 | 7000
15 | Supply, installation, testing & commissioning of Powder coated Aluminium extruded grilles for supply air normal flow, 0° / 15° deflection one way as per specification & the sizes will be as per tender drawing mention: | SqM | 15 | 9630 | 3500 | 144450 | 52500
16 | Supply, installation, testing & commissioning of Powder coated Aluminium extruded Curved grilles for supply air normal flow, 0° / 15° deflection one way as per specification & the sizes will be as per tender drawing mention: | SqM | 7 | 10730 | 3500 | 75110 | 24500
17 | 3 slot/2slot, powder coated extruded aluminium diffusers of approved colour & shade for supply / Return air with Hit & Miss type dampers | SqM | 0 |  |  | 0 | 0
18 | Supply, Installation, Testing and Balancing of round supply air diffusers with removable key operated butterfly volume control dampers as per the approved shop drawings and specifications. The diffusers shall be anti-smudge flush type as approved by the interior designer. Diffuser shall be complete with GI cone with circular connection at the rear.
With Volume Control Dampers
| 300mm dia round diffuser with GI cone | NOS | 0 |  |  | 0 | 0
| 250mm dia round diffuser with GI cone | NOS | 3 | 1400 | 400 | 4200 | 1200
19 | Supply, installation, testing & commissioning of Powder coated Aluminium extruded Multicone ceiling square diffusers 4 way deflection with anti smudge ring ( removal core type ) for supply / return air required as per the tender drawings. | SqM | 19 | 4000 | 1000 | 76000 | 19000
20 | Supply, installation, testing & commissioning of Plaque type diffusers for S/A & R/A with rectangular base plate, made out of powder coated Extruded Al.using removable core type with plenum box. | SqM | 0 |  |  | 0 | 0
21 | Supply, installation, testing and commissioning of Aluminium extruded volume control dampers with key operated of anodised black painted matt finished in supply / return( if required) air collars. | SqM | 10 | 6525 | 1800 | 65250 | 18000
22 | Supply, installation, testing and commissioning of 16 G GSS constructed opposed blade volume control dampers complete with brass bush & manual operating handles within ducts to be provided with suitable links, levers and quadrants for control of volume of air flow for proper air balancing | SqM | 6 | 6525 | 1800 | 39150 | 10800
23 | Supplying & fixing of 18 G thick Aluminium extruded powder coated Fresh / Exhaust air weather protected louvers with VCD & Bird screen type i.e. louvers blade shall be at 45° inclination with blade pitch 40 mm (with Aluminium frames if required) for ventilation. as per specification and sizes will be as per tender drawing mentioned. | SqM | 1 | 7250 | 3500 | 7250 | 3500
24 | Supply, fixing, testing and commissioning of 16 G GSS constructed fire dampers with fire resistance rating 1.5 Hrs at 250°C with 450 mm sleeves in main ducts (supply / return) and return air path at AHU Room's wall & where required of required sizes including control wiring. The damper shall be motorized and spring return so as to close the damper in the event of power failure automatically and open the same in case of power being restored. The spring return action shall be built mechanism and not externally mounted. The damper shall also be closed in the event of a fire signal which shall be provided by Fire Alarm System in each AHU's/ Smoke extract fans panel etc. as per specifications as required.
| a) Fire damper | SqM | 5 | 11528 | 2000 | 57640 | 10000
| b) Actuator with Control Panel | Each | 10 | 12910 | 1500 | 129100 | 15000
25 | Return Air Baffles
| Supply, Fabrication, Installation and Testing of return air baffles made of 24 G GS sheet metal (class VIII-120GSM Zinc Coating) ducts with 12 mm open cell Nitrile Rubber foam within 160-180 Kg/m3 density acoustic insulation, hanging arrangements in accordance with the approved shop drawings and specifications. | SMT | 47 | 6000 | 500 | 282000 | 23500
26 | GI Spigot and Butterfly Dampers
Supply & Installation of GI Spigot and Butterfly Dampers. The damper shall be made of 18G GSS sheet. The blade shall have rubber gasket beading for air tightness. Spigots to have dual notch for firmly fixing the flexible ducts. Spigots to be wrapped with Polythene covers and supplied to the site.
| 250mm dia | Nos | 4 | 1305 | 261 | 5220 | 1044
| 200 mm dia | Nos | 8 | 1015 | 203 | 8120 | 1624
27 | GI Round Duct (22SWG)
Supply & Installation of GI Round Duct (22G)of Following sizes complete with connecting rings and supports in accordance with the approved shop drawings and technical specifications of the following sizes.
| 250mm dia | Rmt | 10 | 840 | 205 | 8400 | 2050
| 200 mm dia | Rmt | 6 | 672 | 164 | 4032 | 984
28 | Insulated flexible Ducting
Supply & Installation of Insulated flexible ducting, complete with connecting rings, aluminium foil tape, duct supports etc. The flexible duct shall be made of triple lamination of aluminium foil, polyester and Metalized Polyester film permanently bonded to a coated spring steel wire helix. The exterior shall be wrapped with 25mm thick 32 kg / m3 fibreglass insulation. The outer insulation jacket / vapour barrier shall be made of fibreglass reinforced Metalized Polyester film laminate. etc. in accordance with the approved shop drawings and technical specifications of the following sizes.
| 250mm dia | Rmt | 10 | 816 | 164 | 8160 | 1640
| 200 mm dia | Rmt | 8 | 656 | 132 | 5248 | 1056
| TOTAL ITEM NO. 4 (DUCTING & AIR TERMINAL WORKS) |  |  |  |  | 2009480 | 461538
29 | INSULATION
29.1 | ACOUSTIC LINING OF DUCTS
Using Open Cell Nitrile Rubber
Supply and Application of internal acoustic lining of supply air ducting using open cell nitrile rubber insulation with density within 140-180 Kg/m3 as per the approved shop drawings and specifications. Insulation material shall be bonded with the ducts using metal screw and washers to facilitate grip to the GI sheet.
| 15 mm thick lining | SqM | 60 | 1220 | 220 | 73200 | 13200
29.2 | ACOUSTIC LINING OF AHU ROOM
Using Open Cell Nitrile Rubber
Supply and Application of internal acoustic lining of supply air ducting using open cell nitrile rubber insulation with density within 140-180 Kg/m3 as per the approved shop drawings and specifications. Insulation material shall be bonded with the ducts using metal screw and washers to facilitate grip to the GI sheet.
| 25 mm thick lining | SqM | 200 | 1769 | 220 | 353800 | 44000
29.3 | THERMAL INSULATION OF DUCTS
(Class 'O' Fire Retardant Properties Closed Cell Elastomeric insulation)
Supply and Application of external thermal insulation of supply /return air ducting using closed cell elastomeric nitrile rubber insulation with class 'O' fire retardant properties as per the specifications and drawings. Insulation should have antimicrobial protection. Quoted price shall be inclusive of insulation wrapped-up (200-300mm wide) over each duct flanges with same insulation material. Tape wherever required for joint or else shall be of same material having Class 'O' properties. Material shall have fire performance acc. to BS 476 Part 7 & Part 6. Self Adhesive 3 mm thick PVC insulation tape should be wrapped at each insulation material joints Adhesive shall be selected as per IGBC guidelines
| 13 mm thick insulation | SqM | 550 | 420 | 160 | 231000 | 88000
29.4 | UNDERCDECK INSULATION
| Supplying & fixing of Underdeck insulation on RCC slab ceiling with approved sample of Class "O" closed cell Nitrile Rubber Insulation with 25 mm Thickness & density 40-55 Kg/Cum .Thermal Conductivity not exceeding 0.035 W/mK at an average Temperature of 0°C. Material shall have fire performance acc. to BS 476 Part 7 & Part 6, water vapour diffusion resistance ( μ factor ) shall be greater than 7000 & tested from third party for the parameteres.Insulation material shall be factory laminated with Aluminium Foil Adhesive shall be selected as per IGBC guidelines | SqM | 0 |  |  | 0 | 0
| TOTAL ITEM NO. 5 (INSULATION) |  |  |  |  | 658000 | 145200
30 | ELELCTRICAL
Power Distribution of HVAC System Shall be covered in main electrical package
Incoming power supply shall be provided by main electrical contractor/
electrical consultant at each HVAC Equipment
along with a TPN MCCB and earthing.
30.1 | VARIABLE FREQUENCY DRIVES
Supply, Installation, Testing and Commissioning of variable frequency drives for following Air Handling Units. Variable frequency drives shall be provided with necessary sensors and transmitters complete with control wiring in all respect as required and as per specifications. VFDs shall have built-in harmonic filters. The drives shall be suitable for the following motor rating. VFDs shall be housed in precoated, vandal proof enclosure with On/Off Push Buttons, Phase indication lights, A/M Switch and with adequate provisions for ventilation using a fan. The VFDs shall be able to receive the signals from multiple/combination of duct static pressure sensors/Temp. sensors and to ramp the speed of the motor.VFDs shall be suitable to take feed back and connectivity from all the DPS as mentioned below against each motor rating to facilitate averaging activity by VFD. Quoted price shall be inclusive of return air temperature sensor and necessary electrical switches including change over switch & copper cabling for integration with the AHU panel. VFDs shall be installed within Electrical panels as described under Section 'Electrical Works'. Overall protection of VFDs with Panels shall be IP-54.
| 11.0 KW for F/M 15000 CFM FM AHU | Nos | 2 | 75040 | 2500 | 150080 | 5000
30.2 | STARTER PANEL FOR CSAHU
Supply, installation, testing & commissioning of the following starters in a sheet metal enclosure complete as required and as per site conditions:
DOL/Star Delta Starter of following rating with Auto/ Manual selector switch, MPCB/MCCB, over load relay, single phasing preventor, ON/OFF/ Trip indication lamps, Ammeters with CTs, ON/OFF push Buttons, contractor and suitable No. of Potential free contacts for remote / local operations, indication, interlocking with Fire Alarm panel and Building Management system. (Starter shall have MPCB/MCCB in the incomer as per type -2 coordination for fuse less type feeders.)
a | 2.2 KW For DOL Starter | Nos | 1 | 22500 | 1500 | 22500 | 1500
TOTAL (AIR DISTRIBUTION) Rs. | TOTAL ITEM NO. 6 ( VFD & Starter Panel) |  |  |  |  | 172580 | 6500
VRV SYSTEM FOR CRITICAL AREAS
1.0 | EQUIPMENT
Supply, Installation, Testing and Commissioning of Variable Refrigerant Volume type multi unit air-conditioning system complete with indoor and outdoor units with individual controller for cooling & heating application as per the specifications and drawings. The quoted price should include clearances charges, local taxes, freight etc. Quoted price shall also be inclusive of loading, unloading, lifting & shifting on outdoor location near Service Staircase at same floor level or other suitable location as per drawing, positioning charges besides including charges towards structural steel supports, MS base frame duly painted & vibration isolation arrangement etc.
OUTDOOR UNITS
Supply, Installation, Testing and Commissioning of air cooled variable refrigerant flow modular type Heat Pumps, each comprising of energy efficient multiple scroll compressors, full charge of R-410a refrigerant gas and all accessories as per the specifications. All compressors shall be inverter type. The condensing units shall be suitable to work on cooling as well as heating mode. The condensing units shall be suitable for operation on 415 ±10% volts, 50Hz, 3 phase AC power supply and complete with auto check function for connection error, auto address setting, etc. The outdoor units shall be low noise type. Quoted price shall be inclusive of Power Cable from MCCB to Outdoor unit & MS frame duly applied with 2 coat of primer & one coat of black enamel paint. The outdoor units shall be of following capacities :
| 14 HP nominal capacity high COP outdoor unit of single module. (Cooling & heating Type) (1W+1S) | No | 1 | 405240 | 14000 | 405240 | 14000
INDOOR UNITS
Supply, Installation, Testing and Commissioning of variable refrigerant volume modular type indoor units comprising of EEV & all accessories as per the specifications. The indoor units shall be suitable to work on cooling as well as heating mode. The indoor units shall be suitable for operation on 220 ±6% volts, 50Hz, 1 phase AC power supply. Ductable indoor units shall be suitable to handle extent of ductwork as shown in the design drawings and dehumidified air quantity as mentioned in the heat load summary sheet under "Special Conditions" and the indoor units shall be of following capacities. All Indoor Units shall have inbuilt Drain Pumps. Quoted price shall be inclusive of Plug Top & necessary power cable.
| Hi-Wall unit Type- 2.0 TR (2W+2S) For Server room | No. | 4 | 23520 | 1500 | 94080 | 6000
| Hi-Wall unit Type- 1.6 TR (2W+2S) For UPS room | No. | 4 | 23200 | 1500 | 92800 | 6000
| Hi-Wall unit Type- 1.6 TR (1W+1S) For Battery room | No. | 2 | 23200 | 1500 | 46400 | 3000
| Hi-Wall unit Type- 0.8 TR Stand by For BMS room | No. | 1 | 18240 | 1500 | 18240 | 1500
REMOTE CONTROLS
| Supply of Cordless handset type remote controls for the above indoor units. | No |  |  |  | 0 | 0
| Supply of Corded remote controls for the above indoor units. | No | 11 | 3500 | 500 | 38500 | 5500
| Supply & Installation of GI Drain tray duly insulated with 13mm thick closed cell elastomeric insulation with class 'O' fire retardant properties below Hi wall Split Units in Technical Spaces. Trays to be provided below Hi wall units coming over panels or other Equipments. Drain tray to be connected with drain piping. | No | 11 | 3000 | 500 | 33000 | 5500
DRAIN PUMP
Supply, Installation, Testing & Commissioning of Condensate
Drain Pump with adequate Sump for Hi-wall units
complete with water level sensor and accessories as
required. Quoted price shall be inclusive of controller,
NRVs & water sensors and associated wiring etc. to
make installation complete. Drain Pump shall be suitable
for operation on 220+6 % volts 50 Hz, 1phase
AC power supply.
Drain pumps shall automatically ON/Off based on
water level.
| Drain pump for Hi-wall units | Nos. | 11 | 4500 | 500 | 49500 | 5500
| Supply, Installation, Testing & Commissioning of PLC Based Panel for sequencing & operational for VRF Units for UPS, Battery & Server Room | Nos. | 3 | 22500 | 2500 | 67500 | 7500
| TOTAL ITEM NO. 7 (EQUIPMENT) |  |  |  |  | 845260 | 54500
2.0 | PIPING
COPPER REFRIGERANT PIPING
Supply, Installation, Testing & Commissioning of high pressure copper refrigerant piping including R410a refrigerant of suitable size as required and duly insulated with19mm/13mm thick closed cell elastomeric insulation with class 'O' fire retardant properties in tubing form. External Refrigerant piping shall be laid on GI covered ladder type cable trays. Piping inside occupied spaces shall be supported using MS hangers duly painted with black enamel paint. Entire refrigerant piping work shall be carried out in accordance with the specifications.MS sleeves of requisite size shall be provided at wall crossing. Quoted price shall be inclusive of necessary glass cloth and minimum two layers of UV protection paint to be applied over insulation for all exposed pipes of approved make. Piping shall be of following sizes :
Internal Refrigerant piping in exposed ceiling area & external refrigerant piping shall be laid on Ladder type cable trays. Cable trays used for external refrigerant piping shall be covered with GI cover.
Pipe Size Thickness of CSE
(O.D.) Insulation
| 28.6 mm 19 mm | RM |  |  |  | 0 | 0
| 25.4 mm 19 mm | RM |  |  |  | 0 | 0
| 22.2 mm 19 mm | RM | 45 | 1428 | 260 | 64260 | 11700
| 19.1 mm 13 mm | RM |  |  |  | 0 | 0
| 15.9 mm 13 mm | RM | 52 | 1008 | 240 | 52416 | 12480
| 12.7 mm 13 mm | RM | 15 | 900 | 240 | 13500 | 3600
| 9.5 mm 13 mm | RM | 110 | 768 | 230 | 84480 | 25300
| 6.4 mm 13 mm | RM | 15 | 720 | 230 | 10800 | 3450
| G.I. Covered Cable Tray (300mmx65mmx65mm) | Rmt. | 20 | 1090 | 165 | 21800 | 3300
| G.I. Open Cable Tray (300mmx50mm) | Rmt. | 100 | 670 | 165 | 67000 | 16500
FITTINGS
Supply, Installation, Testing & Commissioning of following
imported copper fittings to be provided in
refrigerant pipe line.
| Refnet Joints (Y- Joints) | No | 6 | 5000 | 500 | 30000 | 3000
| Refnet Headers | No |  |  |  | 0 | 0
CONDENSATE DRAIN PIPING -cPVC
Supply, Installation, Testing and Commissioning of CPVC pipes cut to required lengths and installed for condensate drain. Quoted price shall be inclusive of supply and fixing in position the necessary fittings like elbows, tees reducers etc., and supporting arrangement in accordance with the approved shop drawings and specifications. Pipes shall be insulated with 9mm thick closed cell elastomeric insulation with class 'O' fire retardant properties in tubing form . Pipes shall be of following sizes :
| 40mm dia | RM |  |  |  | 0 | 0
| 32mm dia | RM | 30 | 200 | 50 | 6000 | 1500
| 25mm dia | RM | 45 | 180 | 40 | 8100 | 1800
| TOTAL ITEM NO. 9(PIPING) |  |  |  |  | 358356 | 82630
ELECTRICAL WORKS
| PANELS-For VRV System | Shall be covered in main electrical package |  |  |  | 0 | 0
Supply, Installation, Testing and Commissioning of the following cubical type panels made out of 14 gauge CRCA structure, base channel, complete with, moulded case circuit breakers, meters, indicating lamps, current transformer etc. Complete in all respects, insulated bus bars with heat shrinkable PVC sleeve in suitable bus chambers , interconnection, small wiring, name plate, danger plate, earth bus etc. & comprising of compartments with hinged door for each feeder & its accessories, cable alley with hinged doors, bus chamber with bolted door etc. The panel being of dust & vermin proof construction with rubber gasket attractively powder coating etc. The panel shall be free standing type / wall mounted type having IP-65 Protection suitable for outdoor installation as per relevant drawing and comprising with the following:
Notes :
1. All MCCBs shall be with operating handle.
2. CTs burden shall be 15VA & accuracy class 1.0
3. CTs shall be cast resin type .
4. All MCCBs shall be with thermal magnetic
release.
5. All indication lights shall be LED type.
6. All meter shall be digital type.
7. The outgoing starter feeders for pumps, AHUS
& ventilation fans shall be provided
with push buttons & indicating lamps for
status indication.
8. Proper isolation switches to be
provided near air handling units and
ventilation fans in weather proof enclosure.
9. Bimetal overload relay for all the
starters shall have built-in single
phasing prevention feature.
10. Electrical interlocking wiring shall be
provided as per system requirement.
11. Power cabling/wiring with necessary
earthing from source to each panel
and each exhaust fan shall be
provided by other agencies.
Note :
Incoming power supply shall be provided by main
electrical contractor/electrical consultant at each VRV
outdoor unit along with a TPN MCCB and earthing.
CONTROL & TRANSMISSION WIRING
Supply, laying, affecting connections and
Testing of the following sizes of control
cum transmission wiring to be laid in MS
conduits between indoor units and outdoor
units.
| 4C x2.5 Sqmm copper wiring | RM | 120 | 280 | 50 | 33600 | 6000
CONTROLLER WIRING
Supply, laying, affecting connections and
Testing of the following sizes of control
cum transmission wiring to be laid in MS
conduits between indoor units and their wired
remotes.
| 2C x1.5 Sqmm copper wiring | RM | 50 | 190 | 40 | 9500 | 2000
| TOTAL ITEM NO.7 (VRF SYSTEM FOR CRITICAL AREA) |  |  |  |  | 1246716 | 145130
VAV BOXES WORKS
1 | VAV BOX Recengular Type
Supply, Installation, Testing & commissioning of VAV boxes consists airflow measuring console consisting of honey-comb pattern airflow straightener of thickness of minimum 60 microns and rapid average pitot tube for accurate airflow measurement. The console has framework of heavy gauge extruded aluminium. The console is followed by Low leak extruded air foil multiblade Volume Control Dampers for modulation of airflow. Made out of heavy gauge extruded aluminium air foil blades and C type 115 mm deep frame with flange of 25 mm, complete with exposed gear drive, EPDM blade seal, with extended shaft suitable for Actuator mounting. EachVAV Box shall be comprising of the following complete as per specification and as required
Microprocessor based Controller with BACnet/IP communication protocol The controller is BTL certified, UL certified and CE certified. The controller should have atleast 4 UI, 1UO, 4 DO. The controller has internal performance assessment control charts for parameters based on temperature, airflow & pressure. The Actuator shall be with 5 n/m torque. The Actuator is built in controller casing only & has brushless motor. The Actuator has integrated position feedback. Noise of actuator shall be less than 35 dB (A). The airflow sensor is mounted on board only with range of negative 500 pascal to positive 500 pascal. The accuracy of on board sensor shall be +-0.2 pascals.
communicating room temperature sensors with communication jack, a backlit-display and configurable graphic menus. The occupants can set temperature.
Digital differential pressure sensor, Modbus communication & necessary power supply circuit suitable for 220V. Contractor to take the power supply near to the differential pressure switch.
Max. Air Qty. Min. Air Qty. Location
(Cfm) (Cfm)
a. | Upto 500 50 As shown on Drg. | No | 18 | 22000 | 2500 | 396000 | 45000
b. | From 525 to 1000 From 50 to 100 As shown on Drg. | No | 3 | 22500 | 2500 | 67500 | 7500
c. | From 1025 to 1500 From 100 to 150 As shown on Drg. | No | 1 | 23000 | 2500 | 23000 | 2500
d. | From 1525 to 2000 From 150 to 200 As shown on Drg. | No |  |  |  | 0 | 0
e. | From 2025 to 2500 From 200 to 250 As shown on Drg. | No |  |  |  | 0 | 0
f. | From 2525 to 3000 From 250 to 300 As shown on Drg. | No |  |  |  | 0 | 0
g. | From 3025 to 3500 From 300 to 350 As shown on Drg. | No |  |  |  | 0 | 0
h. | From 3525 to 4000 From 350 to 400 As shown on Drg. | No |  |  |  | 0 | 0
i. | From 4025 to 4500 From 400 to 450 As shown on Drg. | No |  |  |  | 0 | 0
VAV BOX- Oval Shape
Supply, Installation, Testing & commissioning of VAV boxes consists airflow measuring console consisting of honey-comb pattern airflow straightener of thickness of minimum 60 microns and rapid average pitot tube for accurate airflow measurement. The console has framework of heavy gauge extruded aluminium. The console is followed by Low leak extruded air foil multiblade Volume Control Dampers for modulation of airflow. Made out of heavy gauge extruded aluminium air foil blades and C type 115 mm deep frame with flange of 25 mm, complete with exposed gear drive, EPDM blade seal, with extended shaft suitable for Actuator mounting. EachVAV Box shall be comprising of the following complete as per specification and as required
Microprocessor based Controller with BACnet/IP communication protocol The controller is BTL certified, UL certified and CE certified. The controller should have atleast 4 UI, 1UO, 4 DO. The controller has internal performance assessment control charts for parameters based on temperature, airflow & pressure. The Actuator shall be with 5 n/m torque. The Actuator is built in controller casing only & has brushless motor. The Actuator has integrated position feedback. Noise of actuator shall be less than 35 dB (A). The airflow sensor is mounted on board only with range of negative 500 pascal to positive 500 pascal. The accuracy of on board sensor shall be +-0.2 pascals.
communicating room temperature sensors with communication jack, a backlit-display and configurable graphic menus. The occupants can set temperature.
Digital differential pressure sensor, Modbus communication & necessary power supply circuit suitable for 220V. Contractor to take the power supply near to the differential pressure switch.
VAV should be integrated with in the ducts i.e. VAV Size should be same as of Duct it would be installed in. VAV Controller shall be within VAV casing. It shouldn't be visible from outside.
Max. Air Qty. Min. Air Qty. Location
(Cfm) (Cfm)
a. | Upto 500 50 As shown on Drg. | No | 1 | 23000 | 2500 | 23000 | 2500
b. | From 525 to 1000 From 50 to 100 As shown on Drg. | No | 11 | 23000 | 2500 | 253000 | 27500
c. | From 1025 to 1500 From 100 to 150 As shown on Drg. | No | 5 | 24188 | 2500 | 120940 | 12500
d. | From 1525 to 2000 From 150 to 200 As shown on Drg. | No | 2 | 26125 | 2500 | 52250 | 5000
e. | From 2025 to 2500 From 200 to 250 As shown on Drg. | No |  |  |  | 0 | 0
f. | From 2525 to 3000 From 250 to 300 As shown on Drg. | No | 0 |  |  | 0 | 0
g. | From 3025 to 3500 From 300 to 350 As shown on Drg. | No |  |  |  | 0 | 0
h. | From 3525 to 4000 From 350 to 400 As shown on Drg. | No |  |  |  | 0 | 0
i. | From 4025 to 4500 From 400 to 450 As shown on Drg. | No |  |  |  | 0 | 0
DUCT PRESSURE / TEMPRATURE SENSORS
2 | Supply, Installation and Testing of pressure sensors to be installed in supply air ducts. Quoted price shall be inclusive of necessary conduting, copper control cabling from the sensors to the respective VFDs as per "Approved Shop Drawings". | No | 4 | 10710 | 950 | 42840 | 3800
3 | Supply, Installation, Testing & Commissioning of 2C x 1.5 Sq.mm twisted shielded power cable with conduit for VAV controller | RM | 400 | 119 | 20 | 47600 | 8000
4 | Supply, Installation, Testing & Commissioning of Cat-6 cable with conduit for communication between thermostat to VAV. | RM | 300 | 35 | 10 | 10500 | 3000
5 | Supply, Installation and Testing of controller for BACnet integration above VAV Boxes with BMS. Controller should be suitable to be integrated with minimum 18Nos. of VAV Boxes. Integrator shall be capable of soft integration with BMS system. | No | 3 | 75000 | 5000 | 225000 | 15000
6 | Supply, laying, affecting connections and Testing of all necessary copper control wiring/ daisy chain cabling etc. as required for proper functioning & integration of VAVs with above controller. All cabling to be laid in MS conduits. Quoted price shall be inclusive of all necessary arrangement to make system complete & functional. | RM | 400 | 193 | 46 | 77200 | 18400
| TOTAL ITEM NO. 8 (VAV BOXES) |  |  |  |  | 1338830 | 150700
HYDROGEN EXHAUST
1 | INLINE FANS - For Hydrogen Exhaust
Supply, Installation, Testing and Commissioning of circular inline fans for exhaust complete with sheet metal casing, direct driven centrifugal fan constructed out of GSS, class "B" insulated motor with proper protection and inspection door. Fan shall be suitable for operation on 415 ±10% volts, 50Hz, 3 phase AC power supply. Flanges to be provided on both sides to facilitate duct connections. Fan shall be provided with factory fitted speed regulation arrangement. Fan shall be Explosion Proof Type. Fan shall be installed as shown in the drawings and will be of following characteristics :
Quoted price shall be inclusive of gravity louvers.
Fan Capacity S.P Area to
No. (Cfm) (mmWG) to be exhausted
| IF-1,2 150 15-16 Battery Room | No | 1 | 75000 | 2000 | 75000 | 2000
2 | HYDROGEN SENSORS
| Supply, Fixing and Testing of H2 Sensors. Sensors should be capable to give command directly to Inline fan panel after increasing of H2 level beyond certain specified levels. Quoted price shal be inclusive of Power cabling and control cabling as required between sensor & panels etc. Sensors should be able to automatically switch ON/OFF the Fans after increasing/control of H2 level beyond certain specified levels respectively. Price shall also be inclusive of all accessories required to make installation complete whether specified or not. H2 sensors shall be capable for BMS Integration as well. | No | 1 | 22500 | 800 | 22500 | 800
3 | Panels - Hydrogen Exhaust
Supply, Installation, Testing and Commissioning of the following cubical type panels made out of 14 gauge CRCA structure, base channel, complete with, moulded case circuit breakers, meters, indicating lamps, current transformer etc. Complete in all respects, insulated bus bars with heat shrinkable PVC sleeve in suitable bus chambers, interconnection, small wiring, name plate, danger plate, earth bus etc. & comprising of compartments with hinged door for each feeder & its accessories, cable alley with hinged doors, bus chamber with bolted door etc. The panel being of dust & vermin proof construction with rubber gasket attractively powder coating etc. The panel shall be free standing type / wall mounted type as per relevant drawing and comprising with the following:
Notes :
1. All MCCBs shall be with operating handle.
2. CTs burden shall be 15VA & accuracy class 1.0
3. CTs shall be cast resin type .
4. All MCCBs shall be with thermal magnetic
release.
5. All indication lights shall be LED type.
6. All meter shall be digital type.
7. The outgoing starter feeders for pumps, HUS
& ventilation fans shall be provided
with push buttons & indicating lamps for
status indication.
8. Proper isolation switches to be
provided near air handling units and
ventilation fans in weather proof enclosure.
9. Bimetal overload relay for all the
starters shall have built-in single
phasing prevention feature.
10. Electrical interlocking wiring shall be
provided as per system requirement.
11. Power cabling/wiring with necessary
earthing from source to each panel
and each exhaust fan shall be
provided by other agencies.
12. All HVAC equipment shall be compatible with
BMS and necessary provisions to be made
in each panel.
3.1 | Explosion Proof Fan Panel-1 (Location : Near Fan) | No | 1 | 47250 | 2500 | 47250 | 2500
For Battery Room - 90W
1x150Cfm Fan
10 Amps ,TP MCB -- 1set
(0-500) V digital Voltmeter with built in Selector
switch -- 1set
Digital Ammeter with built in selector
switch- 1set
Current Transformers - 1set
LED type RYB phase indication lights- 1set
LED type ON & OFF indication lights -- 1set
START-STOP Push Buttons -- 1set
90 Watt DOL starter with built-in single phasing
preventer & overload relay -- 1 set
Auto-Manual type selector switch
to facilitate auto start of Fans
after restoration of power -- 01 set.
Timer for Scheduled On/Off-- 01 set.
Contactors, Potential Free Contacts, Control wiring and
safety circuit as required with start-stop push buttons
stay put or lockable type -1 set.
(Panel to be integrated with Hydrogen Sensor for ON/Off operation).
4 | CABLING
4.1 | Supply, laying, affecting connections and Testing of the following sizes of 1.1 KV armoured PVC insulated copper/ aluminium conductor cables. Cables shall be inclusive of all clamps, saddles, screws, cable identification tags, cable terminal joints including terminal lugs, insulating tapes, affecting terminal connections to the equipment as per the specifications and as required. Quoted price shall be inclusive of perforated duly painted 2mm thick MS trays and 8 SWG copper earth wire for AHUs.
All cables shall be FRLS type.
a. | 3 C x 2.5 Sqmm cable (Copper) | RM | 195 | 186 | 30 | 36270 | 5850
| TOTAL ITEM NO. 9(HYDROGEN EXHAUST) |  |  |  |  | 181020 | 11150

## Make list
HVAC Works
No | Item | Make / Brand
A | VENTILATION/EXHAUST FANS
1 | Fresh/Exhaust air fan (Inline/cabinet/floor mounted) | Kruger / Systemair / Caryaire
B | HVAC Units
1 | VRF unit | Daikin / Bluestar
2 | VRF ODU Footing System | Diamond Walraven / Big Foot
3 | EC Fans | EBM Past / ZiehlAbegg
4 | VAV unit | Dynacraft with Belimo / Eneffen-KMC
5 | DX unit | Daikin / Bluestar
6 | Split Units | Daikin / Bluestar
7 | Sequence controller | Mapro / Starline / Titanix
8 | Variable Frequency Drives | Danfoss / ABB / Schneider
9 | Motors | ABB / Crompton / GEC
C | DUCTS & AIR TERMINALS
1 | Galvanized Sheet Steel | Sail / Jindal / TATA
2 | Eliptical/SS duct fabricator | Zeco / Devduct / Spiraltube
3 | Duct fabricator | Zeco / Devduct / Spiraltube
4 | Supply/Return air diffusers | Dynacraft / Systemair
5 | Linear Grills/Diffusers | Dynacraft / Systemair
6 | 300/450mm-Dia Circular diffuser | Dynacraft / Systemair
7 | Toilet Exhaust air disc-200mm Dia | Kruger/ Systemair
8 | Circular ducts for Supply air diffuser or grille | Dynacraft / Systemair
9 | Flexible ducts | UP Twiga / Supaflex
10 | Plenum | Edgetech / Zeco
11 | Anti-vibration Pads | Resisto Flex
D | PIPES/CONDUITS
1 | Copper pipes | Rajco / Parasmani
2 | CPVC/UPVC drain piping | Supreme / Astral / Ashirwad
3 | PVC FRLS / PVC Reinforced flexible conduits | National / Universal / Precision
E | INSULATIONS / FILTERS
1 | Acoustic/Thermal Insulations | K-flex / Arma-flex
2 | Pipe Insulations | K-flex / Arma-flex
3 | Nitrile rubber (class-0) insulation | K-flex / Arma-flex
4 | AHU plant room fiber glass insulation | UP Twiga / Supaflex
5 | Sound attenuator | Systemair / Cosmos
6 | Glass wool Insulation | UP Twiga / Owens corning
7 | Fire Sealant | 3M / Hilti
8 | MERV Filters | Spectrum / Camfil
F | DAMPERS/ACTUATORS
1 | Dampers (VCD, FLFD) | Dynacraft / Systemair
2 | Motorised actuators | Belimo / Honeywell
3 | Extruded Aluminum, Powder Coated Non-Vision louver | Dynacraft / Systemair
G | CABLETRAYS/CABLES/CONDUITS
1 | GI Ladder cable tray | Cable-Tech / Pushpak / Profab
2 | Welding rod | Atlas / Diamond Arc
3 | Rectangular/Eliptical duct support | Gripple / Hilti
4 | Threaded rod support | Profab / Kapson / Unistrut
5 | Cables | Power-Flex / Polycab / Varsha