## Summary
Project: Societe Generale_Bangalore
Subject: Summary of Electrical works
Date: 26-02-2026
Summary
SL.No | Description | Amount | Remarks
1 | Electrical works | 12304547.45
2 | LMS works | 4658556.6
3 | LEED | 0
| Total Basic Amount | 16963104.05 |  | 16963104.05 | TRUE

## BOQ_Electrical Low side
Project :M/s Societe Generale Scope Electrical Low Side BOQ
SL.No | Description | Unit | Voyager (Qty) | Victor (Qty) |  | Total Qty. | Rate |  | Amount |  | Total Amount | Remarks
|  |  | Ground +MF | Level-02 Office | Level-02 Cafeteria |  | Supply | Installation | Supply | Installation
1 | LT PANELS
Supply, Installation, Testing and Commissioning of 415V, 3 phase, 4W, 50 Hz floor / wall mounting type, Cubicle Compartmentalized LT distribution boards as per enclosed Single line diagram. Note: The required Floor Stands & other accessories to mount the panel to be considered in Costing
ALL PANELS SHALL COMPLIANCE TO IE 61439 STANDARD , IE 60439 STANDARD
1 | Main RP Panel with CQRS system | Nos | 1 | 1 | RO | 2 | 474426 | 23000 | 948852 | 46000 | 994852 |  | 994852
2 | Wall mount WS Raw Power Panel with CQRS system | Nos | 1 | RO | RO | 1 | 0 | 0 | 0 | 0 | 0 | *SLD Required | 0
3 | Kitchen / Cafeteria Panel with CQRS system | Nos | RO | 1 | RO | 1 | 0 | 0 | 0 | 0 | 0 | *SLD Required | 0
4 | TAP-OFF BOX: 200A , 4 Wire Tap off box with 200A, 4P, 36kA, MCCB, spreaders, with BMS compatibility and necessary accessories. | Nos | RO | RO | RO | 0 | 28000 | 3500 | 0 | 0 | 0 |  | 0
5 | SPREADER BOX: 200A , 4 Wire Tap off box with 200A, 4P, 36kA, MCCB, spreaders, with BMS compatibility and necessary accessories. | Nos | RO | RO | RO | 0 |  |  | 0 | 0 | 0 |  | 0
6 | TAP-OFF BOX: 630A , 4 Wire Tap off box with 630A, 4P, 36kA, MCCB, spreaders, with BMS compatibility and necessary accessories. | Nos | RO | RO | RO | 0 | 45000 | 5000 | 0 | 0 | 0 |  | 0
7 | SPREADER BOX: 630A , 4 Wire Tap off box with 630A, 4P, 36kA, MCCB, spreaders, with BMS compatibility and necessary accessories. | Nos | RO | RO | RO | 0 |  |  | 0 | 0 | 0 |  | 0
8 | 100A , TPN Isolator with indicating lamps in enclosure | Nos | RO | RO | 2 | 2 | 10249 | 1546 | 20498 | 3092 | 23590 | *Quoted for MCCB | 23590
9 | 63A , 4P MCB with necessary accessories , indicating lamps , ON/OFF/TRIP status indicators etc in the available Spare compartment at exiting UPS O/P Panel. | Nos | 1 | RO | RO | 1 | 2788 | 460 | 2788 | 460 | 3248 |  | 3248
10 | 63A , 4P MCCB with necessary accessories , indicating lamps , ON/OFF/TRIP status indicators etc in the available Spare compartment at exiting UPS O/P Panel. | Nos | 1 | RO | RO | 1 | 10176 | 1472 | 10176 | 1472 | 11648 |  | 11648
| Total for LT Panels | [7 empty] | 982314 | 51024 | 1033338 |  | 0
0
2 | LT CABLES & END TERMINATIONS | [11 empty] | 0
| LT CABLES | [11 empty] | 0
| Supply, Laying, Testing and Commissioning of 1.1 kV grade, Aluminum/copper conductor XLPE/ PVC insulated armoured PVC sheathed LT power/control cables placed at different locations and different lengths in cable trays, complete with all necessary consumables, fixing clamps, identification tags. Etc. | [7 empty] | 0 | 0 |  |  | 0
| END TERMINATIONS | [7 empty] | 0 | 0 |  |  | 0
| Copper conductor cables 1.1kV grade type Cables termination using Single/double compression brass cable glands with earth tags, crimping type tinned copper lugs, earthing clamps consumables for the following size of cables. | [7 empty] | 0 | 0 |  |  | 0
| (Note: 120Sq.mm & above Size cable should have double compression cable glands ) | [7 empty] | 0 | 0 |  |  | 0
2.1 | XLPE / PVC insulated / FRLS sheathed, steel armoured, aluminum conductor 3.5 Core and 4 core cables. | [7 empty] | 0 | 0 |  |  | 0
| All Cables shall be XLPE insulated cables | [7 empty] | 0 | 0 |  |  | 0
2.11 | 3.5 Core X 240 Sqmm | Mts | RO | RO | RO | 0 | 1599 | 130 | 0 | 0 | 0 |  | 0
2.12 | End terminations | Nos. | RO | RO | RO | 0 | 2610 | 660 | 0 | 0 | 0 |  | 0
2.12 | 3.5 Core X 185 Sqmm | Mts | RO | RO | RO | 0 | 1274 | 130 | 0 | 0 | 0 |  | 0
2.13 | End terminations | Nos. | RO | RO | RO | 0 | 2100 | 530 | 0 | 0 | 0 |  | 0
2.13 | 3.5 Core X 150 Sqmm | Mts | RO | RO | RO | 0 | 1006 | 120 | 0 | 0 | 0 |  | 0
2.14 | End terminations | Nos. | RO | RO | RO | 0 | 1640 | 410 | 0 | 0 | 0 |  | 0
2.13 | 3.5C x 120 Sq Mm XLPE Al. Cable | Mts | RO | RO | RO | 0 | 850 | 100 | 0 | 0 | 0 |  | 0
2.14 | End terminations | Nos. | RO | RO | RO | 0 | 1420 | 360 | 0 | 0 | 0 |  | 0
2.15 | 3.5C x 95 Sq Mm XLPE Al. Cable | Mts | RO | 19 | 60 | 79 | 619 | 83 | 48901 | 6557 | 55458 |  | 55458
2.16 | End terminations | Nos. | RO | 2 | 4 | 6 | 1049 | 267 | 6294 | 1602 | 7896 |  | 7896
0.01 | 3.5 Core X 70 Sq Mm | Mts | 38 | 19 | 40 | 97 | 493 | 83 | 47821 | 8051 | 55872 |  | 55872
0.02 | End Terminations | Nos. | 4 | 2 | 4 | 10 | 976 | 249 | 9760 | 2490 | 12250 |  | 12250
2.13 | 3.5 Core X 50 Sqmm | Mts | RO | RO | RO | 0 | 398 | 90 | 0 | 0 | 0 |  | 0
2.14 | End Terminations | Nos. | RO | RO | RO | 0 | 1050 | 270 | 0 | 0 | 0 |  | 0
2.15 | 4 Core X 35 Sq Mm | Mts | 250 | 24 | 45 | 319 | 309 | 65 | 98571 | 20735 | 119306 |  | 119306
2.16 | End terminations | Nos. | 2 | 2 | 2 | 6 | 746 | 194 | 4476 | 1164 | 5640 |  | 5640
2.17 | 4 Core X 25 Sq Mm | Mts | 275 | 162 | RO | 437 | 238 | 56 | 104006 | 24472 | 128478 |  | 128478
2.18 | End Terminations | Nos. | 18 | 16 | RO | 34 | 120 | 37 | 4080 | 1258 | 5338 |  | 5338
2.19 | 4 Core X 16 Sqmm | Mts | RO | RO | RO | 0 | 198 | 40 | 0 | 0 | 0 |  | 0
2.2 | End Terminations | Nos. | RO | RO | RO | 0 | 130 | 40 | 0 | 0 | 0 |  | 0
2.21 | 4 Core X 10 Sqmm | Mts | 35 | RO | RO | 35 | 171 | 37 | 5985 | 1295 | 7280 |  | 7280
2.22 | End Terminations | Nos. | 2 | RO | RO | 2 | 83 | 28 | 166 | 56 | 222 |  | 222
2.23 | 3 Core X 6 Sqmm | Mts | RO | RO | RO | 0 | 114 | 30 | 0 | 0 | 0 |  | 0
2.24 | End Terminations | Nos. | RO | RO | RO | 0 | 70 | 20 | 0 | 0 | 0 |  | 0
[6 empty] | 0 |  |  | 0 | 0 | 0 |  | 0
2.2 | PVC Insulated & Un Armoured Copper Conductor cables (YY Type) |  |  |  |  | 0 |  |  | 0 | 0 | 0 |  | 0
[6 empty] | 0 |  |  | 0 | 0 | 0 |  | 0
2.21 | 1 Core x 50 Sq. mm | Mts | RO | RO | RO | 0 | 1100 | 40 | 0 | 0 | 0 |  | 0
2.22 | End Terminations | Nos. | RO | RO | RO | 0 | 430 | 110 | 0 | 0 | 0 |  | 0
2.22 | 1 Core x 35 Sq. mm | Mts | RO | 45 | RO | 45 | 640 | 37 | 28800 | 1665 | 30465 |  | 30465
2.23 | End Terminations | Nos. | RO | 4 | RO | 4 | 359 | 92 | 1436 | 368 | 1804 |  | 1804
2.24 | 1C x 25 Sqmm Cu unArmoured Cable | Mts | RO | 45 | RO | 45 | 459 | 28 | 20655 | 1260 | 21915 |  | 21915
2.25 | End Terminations | Nos. | RO | 4 | RO | 4 | 120 | 37 | 480 | 148 | 628 |  | 628
2.26 | 1C x 16 Sqmm Cu unArmoured Cable | Mts | RO | 45 | RO | 45 | 295 | 28 | 13275 | 1260 | 14535 |  | 14535
2.27 | End Terminations | Nos. | RO | 2 | RO | 2 | 74 | 19 | 148 | 38 | 186 |  | 186
2.28 | 1 Core x 6 Sq. mm | Mts | 18 | 140 | RO | 158 | 108 | 19 | 17064 | 3002 | 20066 |  | 20066
2.29 | End Terminations | Nos. | 6 | 6 | RO | 12 | 74 | 19 | 888 | 228 | 1116 |  | 1116
2.3 | PVC Insulated & Un Armoured Copper Conductor cables (YY Type) 1 Core x 150 Sq. mm | Mtrs | RO | RO | RO | 0 | 3379 | 60 | 0 | 0 | 0 |  | 0
2.31 | End Terminations | Nos. | RO | RO | RO | 0 | 960 | 240 | 0 | 0 | 0 |  | 0
[6 empty] | 0 |  |  | 0 | 0 | 0 |  | 0
2.3 | PVC Insulated & Steel Armoured Copper Conductor cables (YFY Type) |  |  |  |  | 0 |  |  | 0 | 0 | 0 |  | 0
[6 empty] | 0 |  |  | 0 | 0 | 0 |  | 0
2.31 | 3 Core x 10 Sq. mm | Mts | RO | RO | RO | 0 | 642 | 40 | 0 | 0 | 0 |  | 0
2.32 | End Terminations | Nos. | RO | RO | RO | 0 | 80 | 20 | 0 | 0 | 0 |  | 0
2.33 | 3 Core x 6 Sq. mm | Mts | 114 | 23 | 125 | 262 | 363 | 28 | 95106 | 7336 | 102442 |  | 102442
2.34 | End Terminations | Nos. | 4 | 2 | 4 | 10 | 74 | 19 | 740 | 190 | 930 |  | 930
2.35 | 3 Core x 4 Sq. mm | Mts | RO | RO | RO | 0 | 274 | 30 | 0 | 0 | 0 |  | 0
2.36 | End Terminations | Nos. | RO | RO | RO | 0 | 70 | 20 | 0 | 0 | 0 |  | 0
2.37 | 3 Core x 2.5Sq. mm | Mts | RO | RO | RO | 0 | 186 | 30 | 0 | 0 | 0 |  | 0
2.38 | End Terminations | Nos. | RO | RO | RO | 0 | 70 | 20 | 0 | 0 | 0 |  | 0
2.39 | 4 Core x 16 Sq. mm | Mts | 38 | RO | RO | 38 | 1139 | 37 | 43282 | 1406 | 44688 |  | 44688
2.4 | End Terminations | Nos. | 2 | RO | RO | 2 | 129 | 37 | 258 | 74 | 332 |  | 332
2.41 | 4 Core x 10 Sq. mm | Mts | 61 | 66 | 70 | 197 | 771 | 28 | 151887 | 5516 | 157403 |  | 157403
2.42 | End Terminations | Nos. | 4 | 4 | 4 | 12 | 92 | 28 | 1104 | 336 | 1440 |  | 1440
2.43 | 4 Core x 6 Sq. mm | Mts | 36 | 38 | 40 | 114 | 474 | 28 | 54036 | 3192 | 57228 |  | 57228
2.44 | End Terminations | Nos. | 2 | 2 | 2 | 6 | 92 | 28 | 552 | 168 | 720 |  | 720
2.45 | 4 Core x 4 Sq. mm | Mts | 26 | 28 | 30 | 84 | 322 | 28 | 27048 | 2352 | 29400 |  | 29400
2.46 | End Terminations | Nos. | 4 | 4 | 4 | 12 | 74 | 19 | 888 | 228 | 1116 |  | 1116
[6 empty] | 0 |  |  | 0 | 0 | 0 |  | 0
2.4 | PVC Insulated Unarmoured Copper Conductor cables (YY Type) |  |  |  |  | 0 |  |  | 0 | 0 | 0 |  | 0
[6 empty] | 0 |  |  | 0 | 0 | 0 |  | 0
2.41 | 3 Core x 10 Sq. mm | Mts | RO | RO | 15 | 15 | 575 | 120 | 8625 | 1800 | 10425 |  | 10425
2.42 | End Terminations | Nos. | RO | RO | 2 | 2 | 74 | 19 | 148 | 38 | 186 |  | 186
2.43 | 3 Core x 6 Sq. mm | Mts | RO | RO | 25 | 25 | 330 | 28 | 8250 | 700 | 8950 |  | 8950
2.44 | End Terminations | Nos. | RO | RO | 2 | 2 | 74 | 19 | 148 | 38 | 186 |  | 186
2.45 | 3 Core x 4 Sq. mm | Mts | 42 | RO | 35 | 77 | 224 | 46 | 17248 | 3542 | 20790 |  | 20790
2.46 | End Terminations | Nos. | 6 | RO | 2 | 8 | 65 | 19 | 520 | 152 | 672 |  | 672
2.47 | 4 Core x 10 Sq. mm | Mts | RO | RO | 45 | 45 | 759 | 148 | 34155 | 6660 | 40815 |  | 40815
2.48 | End Terminations | Nos. | RO | RO | 2 | 2 | 74 | 19 | 148 | 38 | 186 |  | 186
2.49 | 4 Core x 6 Sq. mm | Mts | RO | RO | 45 | 45 | 437 | 28 | 19665 | 1260 | 20925 |  | 20925
2.5 | End Terminations | Nos. | RO | RO | 2 | 2 | 74 | 19 | 148 | 38 | 186 |  | 186
2.51 | 4 Core x 4 Sq. mm | Mts | RO | RO | 95 | 95 | 299 | 28 | 28405 | 2660 | 31065 |  | 31065
2.52 | End Terminations | Nos. | RO | RO | 6 | 6 | 65 | 19 | 390 | 114 | 504 |  | 504
[6 empty] | 0 |  |  | 0 | 0 | 0 |  | 0
| Total for LT Cables and End Terminations | [7 empty] | 905557 | 113487 | 1019044 |  | 0
[6 empty] | 0 | [6 empty] | 0
3 | MCB DISTRIBUTION BOARDS (DB) |  |  |  |  | 0 | [6 empty] | 0
[6 empty] | 0 | [6 empty] | 0
| Supply, Installation, Testing and Commissioning of MCB Distribution board as per approved installation dwgs. |  |  |  |  | 0 |  |  | 0 | 0 | 0 |  | 0
| Wall mounted MCB DBs with MS wire way box on top / bottom & on sides. MCBs shall be rated for 10kA with current limiting feature. Dummy ways to be covered with blank plates. All outgoing ways shall be labelled & laminated. |  |  |  |  | 0 |  |  | 0 | 0 | 0 |  | 0
| Enclosure:1.2mm CRCA Sheet Steel, Powder Coated |  |  |  |  | 0 |  |  | 0 | 0 | 0 |  | 0
| Door : Double Door |  |  |  |  | 0 |  |  | 0 | 0 | 0 |  | 0
| Protection : IP 42 |  |  |  |  | 0 |  |  | 0 | 0 | 0 |  | 0
| Cable Entry : Top & Bottom |  |  |  |  | 0 |  |  | 0 | 0 | 0 |  | 0
| For UPS distribution RCCB shall be harmonic resistant (SI Series) |  |  |  |  | 0 |  |  | 0 | 0 | 0 |  | 0
| Bus bar : Shall be tinned Copper and 200% rating for UPS DB Neutral Link |  |  |  |  | 0 |  |  | 0 | 0 | 0 |  | 0
| MCB's : 10kA 'C' Curve for Lighting & cafeteria Raw power, 10kA 'D' Curve for UPS Distribution & Raw power |  |  |  |  | 0 |  |  | 0 | 0 | 0 |  | 0
| Note: |  |  |  |  | 0 |  |  | 0 | 0 | 0 |  | 0
| 1) Separate Earth bus/Neutral bus for each phase |  |  |  |  | 0 |  |  | 0 | 0 | 0 |  | 0
| 2) Each Circuit shall have yellow ferrules with circuit number. |  |  |  |  | 0 |  |  | 0 | 0 | 0 |  | 0
| 3) Accessories required for installation of DB's on Wall/Column/Gyp Board shall be considered |  |  |  |  | 0 |  |  | 0 | 0 | 0 |  | 0
| 4) DB's shall be covered with powder coated (paint should match with DB Color) wire ways all around and up to ceiling to receive incoming circuits |  |  |  |  | 0 |  |  | 0 | 0 | 0 |  | 0
| 5) Laminated A3 OR A4 size SLD copy shall be pasted inside DB door |  |  |  |  | 0 |  |  | 0 | 0 | 0 |  | 0
| 6) Safe shroud for Neutral link shall be provided |  |  |  |  | 0 |  |  | 0 | 0 | 0 |  | 0
[6 empty] | 0 |  |  | 0 | 0 | 0 |  | 0
3.1 | LDB |  |  |  |  | 0 |  |  | 0 | 0 | 0 |  | 0
[6 empty] | 0 |  |  | 0 | 0 | 0 |  | 0
3.11 | 12 way TPN MCB DB similar to SCHNEIDER DB cat no. A9HFD440 with provision of below mentioned items |  |  |  |  | 0 |  |  | 0 | 0 | 0 |  | 0
| Incomer : 1No. 63A, 4P,MCB |  |  |  |  | 0 |  |  | 0 | 0 | 0 |  | 0
| & 3 Nos 63A ,DP,30mA RCCB |  |  |  |  | 0 |  |  | 0 | 0 | 0 |  | 0
| Outgoing : 36 Nos. 10A SP MCB of 'C' curve | Nos | 1 | 1 | RO | 2 | 21722 | 1380 | 43444 | 2760 | 46204 |  | 46204
[6 empty] | 0 |  |  | 0 | 0 | 0 |  | 0
3.12 | 8 way TPN MCB DB similar to SCHNEIDER cat no. A9HFD336 with provision of below mentioned items |  |  |  |  | 0 |  |  | 0 | 0 | 0 |  | 0
| Incomer : 1No. 40A, 4P,MCB |  |  |  |  | 0 |  |  | 0 | 0 | 0 |  | 0
| & 3 Nos 40A ,DP,30mA RCCB |  |  |  |  | 0 |  |  | 0 | 0 | 0 |  | 0
| Outgoing : 24 Nos. 10A SP MCB of 'C' curve | Nos | RO | RO | RO | 0 | 17650 | 1500 | 0 | 0 | 0 |  | 0
[6 empty] | 0 |  |  | 0 | 0 | 0 |  | 0
3.13 | 6 way TPN MCB similar to SCHNEIDER cat no. A9HPGD06 with provision of below mentioned items |  |  |  |  | 0 |  |  | 0 | 0 | 0 |  | 0
| Incomer : 1No. 63A, 4P,MCB |  |  |  |  | 0 |  |  | 0 | 0 | 0 |  | 0
| & 3 Nos 40A ,DP,30mA RCCB |  |  |  |  | 0 |  |  | 0 | 0 | 0 |  | 0
| Outgoing : 18 Nos. 10A SP MCB of 'C' curve | Nos | 1 | 1 | RO | 2 | 14463 | 1173 | 28926 | 2346 | 31272 |  | 31272
[6 empty] | 0 |  |  | 0 | 0 | 0 |  | 0
3.2 | ELDB's : |  |  |  |  | 0 |  |  | 0 | 0 | 0 |  | 0
3.21 | 18 Way SPN MCB DB |  |  |  |  | 0 |  |  | 0 | 0 | 0 |  | 0
| Incomer : 1No. 25A, DP, RCCB with 30mA |  |  |  |  | 0 |  |  | 0 | 0 | 0 |  | 0
| Outgoing : 16 Nos. 10A SP MCB of 'C' curve | Nos | 1 | 1 | RO | 2 | 6726 | 1012 | 13452 | 2024 | 15476 |  | 15476
[6 empty] | 0 |  |  | 0 | 0 | 0 |  | 0
3.3 | Other service UPS DB |  |  |  |  | 0 |  |  | 0 | 0 | 0 |  | 0
3.31 | 18 Way SPN MCB DB |  |  |  |  | 0 |  |  | 0 | 0 | 0 |  | 0
| Incomer : 1No.40A DP MCB |  |  |  |  | 0 |  |  | 0 | 0 | 0 |  | 0
| Outgoing : 16 Nos. 10 SP MCB of 'D' curve | Nos | 1 | 1 | RO | 2 | 6882 | 1040 | 13764 | 2080 | 15844 |  | 15844
[6 empty] | 0 |  |  | 0 | 0 | 0 |  | 0
3.4 | Server Room |  |  |  |  | 0 |  |  | 0 | 0 | 0 |  | 0
3.41 | 16 Way SPN MCB DB |  |  |  |  | 0 |  |  | 0 | 0 | 0 |  | 0
| Incomer : 1No. 63A, DP,MCB of 'D' Curve |  |  |  |  | 0 |  |  | 0 | 0 | 0 |  | 0
| Outgoing : 7 Nos. 20A DP MCB of 'D' Curve | Nos | RO | RO | RO | 0 | 7740 | 750 | 0 | 0 | 0 |  | 0
[6 empty] | 0 |  |  | 0 | 0 | 0 |  | 0
3.5 | HUB Room / ISP room |  |  |  |  | 0 |  |  | 0 | 0 | 0 |  | 0
3.51 | 8 Way SPN MCB DB |  |  |  |  | 0 |  |  | 0 | 0 | 0 |  | 0
| Incomer : 1No. 40A, DP,MCB of 'D' Curve |  |  |  |  | 0 |  |  | 0 | 0 | 0 |  | 0
| Outgoing : 3 Nos. 20A DP MCB of 'D' Curve | Nos | RO | RO | RO | 0 | 4400 | 750 | 0 | 0 | 0 |  | 0
[6 empty] | 0 |  |  | 0 | 0 | 0 |  | 0
3.52 | 8 way TPN MCB DB similar to SCHNEIDER DB cat no. A9HTND08 with provision of below mentioned items |  |  |  |  | 0 |  |  | 0 | 0 | 0 |  | 0
| Incomer : 1No. 40A, 4P,MCB |  |  |  |  | 0 |  |  | 0 | 0 | 0 |  | 0
| & 3 Nos 40A ,DP,MCB |  |  |  |  | 0 |  |  | 0 | 0 | 0 |  | 0
| Outgoing : 9 Nos. 20A DP MCB of 'D' curve | Nos | 2 | RO | RO | 2 | 13902 | 1380 | 27804 | 2760 | 30564 |  | 30564
[6 empty] | 0 |  |  | 0 | 0 | 0 |  | 0
3.6 | UDB's : |  |  |  |  | 0 |  |  | 0 | 0 | 0 |  | 0
3.61 | 12 way TPN TPN MCB DB similar to SCHNEIDER DB cat no. A9HFD456 with provision of below mentioned items |  |  |  |  | 0 |  |  | 0 | 0 | 0 |  | 0
| Incomer : 1No. 63A, TP+2N,MCB |  |  |  |  | 0 |  |  | 0 | 0 | 0 |  | 0
| & 3 Nos 63A ,DP,30mA, Si, Series RCB'O |  |  |  |  | 0 |  |  | 0 | 0 | 0 |  | 0
| Outgoing : 36 Nos. 16A SP MCB of 'D' curve | Nos | 1 | 1 | RO | 2 | 26754 | 1380 | 53508 | 2760 | 56268 |  | 56268
[6 empty] | 0 |  |  | 0 | 0 | 0 |  | 0
3.62 | 8 way TPN MCB TPN DB similar to SCHNEIDER DB cat no. A9HFD440 with provision of below mentioned items |  |  |  |  | 0 |  |  | 0 | 0 | 0 |  | 0
| Incomer : 1No. 40A, TP+2N,MCB |  |  |  |  | 0 |  |  | 0 | 0 | 0 |  | 0
| & 3 Nos 40A ,DP,30mA, Si, Series RCB'O |  |  |  |  | 0 |  |  | 0 | 0 | 0 |  | 0
| Outgoing : 24 Nos. 10A SP MCB of 'D' curve | Nos | 1 | RO | RO | 1 | 20498 | 1380 | 20498 | 1380 | 21878 |  | 21878
[6 empty] | 0 |  |  | 0 | 0 | 0 |  | 0
3.7 | RDB's : |  |  |  |  | 0 |  |  | 0 | 0 | 0 |  | 0
3.71 | 12 way TPN MCB DB similar to SCHNEIDER DB cat no. A9HPGD12 with provision of below mentioned items |  |  |  |  | 0 |  |  | 0 | 0 | 0 |  | 0
| Incomer : 1No. 63A, 4P,MCB |  |  |  |  | 0 |  |  | 0 | 0 | 0 |  | 0
| & 3 Nos 40A ,DP,30mA RCCB |  |  |  |  | 0 |  |  | 0 | 0 | 0 |  | 0
| Outgoing : 24 Nos. 16A SP MCB of 'C' curve | Nos | RO | 1 | RO | 1 | 18235 | 1380 | 18235 | 1380 | 19615 |  | 19615
[6 empty] | 0 |  |  | 0 | 0 | 0 |  | 0
3.72 | 8 way TPN MCB DB similar to SCHNEIDER DB cat no.A9HTNS08 with provision of below mentioned items |  |  |  |  | 0 |  |  | 0 | 0 | 0 |  | 0
| Incomer : 1No. 40A, 4P,MCB |  |  |  |  | 0 |  |  | 0 | 0 | 0 |  | 0
| & 3 Nos 40A ,DP,30mA RCCB |  |  |  |  | 0 |  |  | 0 | 0 | 0 |  | 0
| Outgoing : 18 Nos. 16A SP MCB of 'C' curve | Nos | 2 | 1 | RO | 3 | 15199 | 1380 | 45597 | 4140 | 49737 |  | 49737
[6 empty] | 0 |  |  | 0 | 0 | 0 |  | 0
3.73 | 12 way TPN MCB DB similar to SCHNEIDER DB cat no.A9HTNS08 with provision of below mentioned items for Height Adjustable table |  |  |  |  | 0 |  |  | 0 | 0 | 0 |  | 0
| Incomer : 1No. 63A, 4P,MCB |  |  |  |  | 0 |  |  | 0 | 0 | 0 |  | 0
| & 3 Nos 63A ,DP,30mA RCCB, 1.5kV , SPD |  |  |  |  | 0 |  |  | 0 | 0 | 0 |  | 0
| Outgoing : 36 Nos. 16A SP MCB of 'C' curve | Nos | 1 | 1 | RO | 2 | 21722 | 1380 | 43444 | 2760 | 46204 |  | 46204
[6 empty] | 0 |  |  | 0 | 0 | 0 |  | 0
3.74 | 8 Way SPN MCB DB for HVAC |  |  |  |  | 0 |  |  | 0 | 0 | 0 |  | 0
| Incomer : 1No. 25A, DP, 30mA RCCB of 'C' Curve |  |  |  |  | 0 |  |  | 0 | 0 | 0 |  | 0
| Outgoing : 6 Nos. 16A SP MCB of 'C' Curve | Nos | RO | RO | RO | 0 | 4560 | 750 | 0 | 0 | 0 |  | 0
[6 empty] | 0 |  |  | 0 | 0 | 0 |  | 0
3.75 | Redressing of DB cabinet for additional or new circuit as per latest ID layout | Lot | RO | 1 | RO | 1 | 0 | 13800 | 0 | 13800 | 13800 | *Details Required | 13800
[6 empty] | 0 |  |  | 0 | 0 | 0 |  | 0
| Total for MCB Distribution boards | [7 empty] | 308672 | 38190 | 346862 |  | 0
[6 empty] | 0 |  |  | 0 | 0 | 0 |  | 0
4 | CIRCUIT MAINS |  |  |  |  | 0 |  |  | 0 | 0 | 0 |  | 0
[6 empty] | 0 |  |  | 0 | 0 | 0 |  | 0
| Circuit mains using 1.1kV grade PVC insulated copper conductor FRLS wires / PVC insulated PVC sheathed single core cables drawn in 2mm thick PVC conduit or in existing tray/raceway. Rates quoted shall include supply of wires & other accessories. Circuit mains shall be measured from respective DB to the nearest point. All circuit terminations shall be provided with solderless crimping type copper sockets / lugs, ferrules indicating source code on load side & load code on source side. There shall not be any joints in the circuits, only looping is allowed in terminal blocks & at points. |  |  |  |  | 0 |  |  | 0 | 0 | 0 |  | 0
| NOTE: |  |  |  |  | 0 |  |  | 0 | 0 | 0 |  | 0
| 1) Conduits running above false ceiling in multiples shall be supported by Slotted GI 'C' channel at distance not more than 0.5mtrs intervals. OR else with spacers & saddles at an intervals of 0.5mtrs |  |  |  |  | 0 |  |  | 0 | 0 | 0 |  | 0
| 2) Accessories shall includes Bends, Collars, junction boxes, Spacers, saddles, screws, Flexibles |  |  |  |  | 0 |  |  | 0 | 0 | 0 |  | 0
| 3) Conduits shall be ISI marked |  |  |  |  | 0 |  |  | 0 | 0 | 0 |  | 0
| 4) The number of wires drawn in each conduit shall be as per IS 694 code. |  |  |  |  | 0 |  |  | 0 | 0 | 0 |  | 0
| 5) No different phases shall be drawn in same conduit |  |  |  |  | 0 |  |  | 0 | 0 | 0 |  | 0
| 6) Conduit joints shall be done with threading proper accessories only |  |  |  |  | 0 |  |  | 0 | 0 | 0 |  | 0
[6 empty] | 0 |  |  | 0 | 0 | 0 |  | 0
4.1 | POWER CIRCUIT |  |  |  |  | 0 |  |  | 0 | 0 | 0 |  | 0
4.11 | 3 Core - 2.5 sq.mm flexible FRLS copper conductor cables in already laid conduit / raceway. (For Rawpower & UPS) (Colour for cable - Black for Raw power & White for UPS) | Mtrs | 5035 | 3650 | RO | 8685 | 148 | 28 | 1285380 | 243180 | 1528560 |  | 1528560
4.12 | 3 Core - 4 sq.mm flexible FRLS copper cables for ISP & Pantry equipments circuits (Colour for cable - Black & White for source 1 & 2 respectively) | Mtrs | 235 | 135 | RO | 370 | 224 | 28 | 82880 | 10360 | 93240 |  | 93240
4.13 | 3 Core - 6 sq.mm flexible FRLS copper cables for Server room circuits | Mtrs | 40 | 15 | RO | 55 | 330 | 28 | 18150 | 1540 | 19690 |  | 19690
[6 empty] | 0 |  |  | 0 | 0 | 0 |  | 0
4.2 | LIGHTING CIRCUIT WITH PVC FRLS CONDUIT |  |  |  |  | 0 |  |  | 0 | 0 | 0 |  | 0
| Supply and laying of circuit mains using 2mm thick FRLS conduit, accessories like bends, junction boxes and saddles etc., 1100 V grade FRLS flexible copper wires and wiring accessories, terminating wires on either ends by providing copper lugs, 15A 4 way connectors. |  |  |  |  | 0 |  |  | 0 | 0 | 0 |  | 0
| Circuit mains shall be measured from to switch box / first light in the circuit with shortest possible route. |  |  |  |  | 0 |  |  | 0 | 0 | 0 |  | 0
4.21 | 2 Runs of 2.5 Sqmm and 1 Run of 1.5 Sqmm fire resistant FRLS wires in 20mm conduit. | Mtrs | R0 | RO | RO | 0 | 150 | 30 | 0 | 0 | 0 |  | 0
4.22 | 3 Runs of 1.5 Sqmm fire resistant FRLS wires in 20mm conduit. (For single Emergency lighting circuits) | Mtrs | R0 | RO | RO | 0 | 115 | 20 | 0 | 0 | 0 |  | 0
4.23 | 2 core 1Sqmm single strand copper flexible cable for dimming circuit control wiring in already laid conduit | Mtrs | 1150 | 1210 | 300 | 2660 | 65 | 10 | 172900 | 26600 | 199500 |  | 199500
4.24 | 3 Core - 2.5 sq.mm flexible FRLS copper conductor cables in already laid conduit / raceway. (For Lighting) | Mtrs | 2135 | 2325 | 620 | 5080 | 148 | 28 | 751840 | 142240 | 894080 |  | 894080
4.25 | 3 Core - 1.5 sq.mm flexible FRLS copper conductor cables in already laid conduit / raceway. (For Emergency Lighting ) | Mtrs | 525 | 570 | 120 | 1215 | 92 | 19 | 111780 | 23085 | 134865 |  | 134865
[6 empty] | 0 |  |  | 0 | 0 | 0 |  | 0
[6 empty] | 0 |  |  | 0 | 0 | 0 |  | 0
| Total for Circuit mains | [7 empty] | 2422930 | 447005 | 2869935 |  | 0
[6 empty] | 0 | [6 empty] | 0
5 | POINT WIRING |  |  |  |  | 0 | [6 empty] | 0
[6 empty] | 0 | [6 empty] | 0
5.1 | POINT WIRING with PVC FRLS conduits with 3R x 1.5 Sq.mm flexible Wires |  |  |  |  | 0 |  |  | 0 | 0 | 0 |  | 0
| Supplying and installation of wiring for light points with/without sensors by using 19mm dia,2mm thick FRLS PVC conduit of required dia as per IS732, conduit accessories, flexible conduit with couplers for drops with accessories. |  |  |  |  | 0 |  |  | 0 | 0 | 0 |  | 0
| All points shall be earthed with 1.5 Sqmm FRLS flexible copper wire. Wires shall be terminated at light fixtures with ferrules, 15A 4 way connector; wire ends shall not be loose / bare. Point wiring including all types of supports & accessories. |  |  |  |  | 0 |  |  | 0 | 0 | 0 |  | 0
[6 empty] | 0 |  |  | 0 | 0 | 0 |  | 0
5.11 | One light point controlled by one 6A modular switch. | Nos. | 12 | 15 | RO | 27 | 1334 | 267 | 36018 | 7209 | 43227 |  | 43227
5.12 | Two light point controlled by one 6A modular switch. | Nos. | 4 | 5 | RO | 9 | 1684 | 341 | 15156 | 3069 | 18225 |  | 18225
5.13 | Three light point controlled by one 6A modular switch. | Nos. | 2 | 4 | RO | 6 | 2024 | 405 | 12144 | 2430 | 14574 |  | 14574
5.14 | Four light point controlled by one 6A modular switch. | Nos. | 2 | 2 | RO | 4 | 2374 | 479 | 9496 | 1916 | 11412 |  | 11412
5.15 | Five light point controlled by one 6A modular switch. | Nos. | 1 | 1 | RO | 2 | 2724 | 552 | 5448 | 1104 | 6552 |  | 6552
5.16 | Six light point controlled by one 6A modular switch. | Nos. | 1 | 1 | RO | 2 | 3073 | 617 | 6146 | 1234 | 7380 |  | 7380
5.17 | Seven light point controlled by one 6A modular switch. | Nos. | 1 | 1 | RO | 2 | 3423 | 690 | 6846 | 1380 | 8226 |  | 8226
5.18 | Eight light point controlled by one 6A modular switch. | Nos. | 1 | 1 | RO | 2 | 3772 | 755 | 7544 | 1510 | 9054 |  | 9054
5.19 | Nine light point controlled by one 6A modular switch. | Nos. | RO | RO | RO | 0 | 4480 | 900 | 0 | 0 | 0 |  | 0
5.2 | Ten light point controlled by one 6A modular switch. | Nos. | RO | RO | RO | 0 | 4860 | 980 | 0 | 0 | 0 |  | 0
[6 empty] | 0 |  |  | 0 | 0 | 0 |  | 0
| Point Wiring With 3C x 1.5 Sq.mm flexible Cable |  |  |  |  | 0 |  |  | 0 | 0 | 0 |  | 0
5.21 | Primary light point - From LDB to first light point / Switch board 3 Core - 2.5 sq.mm flexible FRLS copper conductor cables in already laid conduit / Lighting tray. (For Lighting) | Nos | 60 | 60 | 5 | 125 | 2806 | 562 | 350750 | 70250 | 421000 | *Quoted for 3C*1.5 PVC cable | 421000
5.22 | Secondary light point - loop point - First point to other light points along with lighting sensors without Switch / MCB 3 Core - 1.5 sq.mm flexible FRLS copper conductor cables in already laid conduit / Lighting tray. Each looping - 4.0 to 6.0 mtr | Nos | 708 | 806 | 20 | 1534 | 442 | 92 | 678028 | 141128 | 819156 |  | 819156
[6 empty] | 0 | [6 empty] | 0
| Total for Point wiring | [7 empty] | 1127576 | 231230 | 1358806 |  | 0
[6 empty] | 0 | [6 empty] | 0
0
6 | POWER RECEPTACLES & ISOLATORS |  |  |  |  | 0 | [6 empty] | 0
[6 empty] | 0 | [6 empty] | 0
| Supply, Installation, Testing and Commissioning of the following Modular/Industrial Switch, sockets with modular front plate, and accessories as per the site conditions. |  |  |  |  | 0 | [6 empty] | 0
| The quoted rate for power socket outlets shall include a. Socket outlets - 5pin combi/intel sockets b. Switches c. 14 SWG metal boxes with knockout on all sides. 1mm thick backbox d. Front plate of required colours with accessories e. UPS power plate - White & Raw power plate - Grey unless otherwise mentioned |  |  |  |  | 0 |  |  | 0 | 0 | 0 |  | 0
| Note: Safety shutters to prevent accidental contact with live parts shall be provided. No indicator shall be provided for switches |  |  |  |  | 0 |  |  | 0 | 0 | 0 |  | 0
[6 empty] | 0 |  |  | 0 | 0 | 0 |  | 0
6.1 | Without GI / PVC back box for workstations |  |  |  |  | 0 |  |  | 0 | 0 | 0 |  | 0
[6 empty] | 0 |  |  | 0 | 0 | 0 |  | 0
6.11 | 1no. 6A 3 pin universal round pin socket controlled by 6A SP Switch | Nos. | 15 | 15 | RO | 30 | 203 | 46 | 6090 | 1380 | 7470 |  | 7470
6.12 | 1no. 6/16A 6 pin universal round pin socket controlled by 16A SP Switch -Raw Power | Nos. | 10 | 10 | RO | 20 | 295 | 65 | 5900 | 1300 | 7200 |  | 7200
6.13 | 1nos. 6A round pin socket controlled by 16A SP Switch with front plates- Raw power(for cluster of workstation) | Nos. | RO | RO | RO | 0 | 270 | 60 | 0 | 0 | 0 |  | 0
6.14 | 4nos. 6A round pin socket controlled by 16A SP Switch with front plates- UPS Power | Nos. | RO | RO | RO | 0 | 760 | 160 | 0 | 0 | 0 |  | 0
6.15 | 3nos. 6A/16A round pin socket controlled by 16A SP Switch with front plates.- Raw Power | Nos. | 270 | 260 | RO | 530 | 644 | 129 | 341320 | 68370 | 409690 |  | 409690
6.16 | 2nos. 6A, round pin socket controlled by 16A SP Switch and cover Plates.-UPS Power | Nos. | 2 | 2 | RO | 4 | 479 | 102 | 1916 | 408 | 2324 |  | 2324
6.17 | 1no. 6/16A, round pin socket controlled by 16A SP Switch and cover Plates. For UPS Power | Nos. | RO | RO | RO | 0 | 320 | 70 | 0 | 0 | 0 |  | 0
6.18 | Power Cube - 2x6A socket round pin controlled by 16A SP switch - Raw power for Workstation and UPS for Board room 50% of occupancy. Make CJ Infra . | Nos. | 285 | 265 | RO | 550 | 387 | 83 | 212850 | 45650 | 258500 |  | 258500
[6 empty] | 0 |  |  | 0 | 0 | 0 |  | 0
6.2 | With Metal back box for closed rooms & Other services. |  |  |  |  | 0 |  |  | 0 | 0 | 0 |  | 0
[6 empty] | 0 |  |  | 0 | 0 | 0 |  | 0
6.21 | 1no. 6A 3 pin universal round pin socket controlled by 6A SP Switch on UPS power. | Nos. | 62 | 62 | RO | 124 | 258 | 56 | 31992 | 6944 | 38936 |  | 38936
6.22 | 1no. 6A 3 pin universal round pin socket controlled by 6A SP Switch on Raw power for height adjustable table. | Nos. | 270 | 260 | RO | 530 | 258 | 56 | 136740 | 29680 | 166420 |  | 166420
6.23 | 1no. 6/16A 6 pin universal round pin socket controlled by 16A SP Switch with indicator - Raw Power. | Nos. | 70 | 70 | RO | 140 | 378 | 83 | 52920 | 11620 | 64540 |  | 64540
6.24 | 1nos. 6A round pin socket controlled by 16A SP Switch with front plates- UPS Power | Nos. | 8 | 8 | RO | 16 | 295 | 65 | 4720 | 1040 | 5760 |  | 5760
6.25 | 1no. 6/16A 6 pin universal round pin socket controlled by 16A SP Switch with indicator for - UPS power. | Nos. | 4 | 4 | RO | 8 | 378 | 83 | 3024 | 664 | 3688 |  | 3688
6.26 | 4nos. 6A round pin socket controlled by 16A SP Switch with front plates - UPS Power | Nos. | RO | RO | RO | 0 | 900 | 180 | 0 | 0 | 0 |  | 0
6.27 | 3nos. 6A round pin socket controlled by 16A SP Switch with front plates. - UPS Power | Nos. | 10 | 10 | RO | 20 | 608 | 129 | 12160 | 2580 | 14740 |  | 14740
6.28 | 2nos. 6/13A, round pin socket controlled by 16A SP Switch and cover Plates - UPS Power | Nos. | 32 | 32 | RO | 64 | 562 | 120 | 35968 | 7680 | 43648 |  | 43648
6.29 | Floor box similar to MK make access outlet of size 250 mm x 250 mm x 56mm 3comp MODEL Nos ESB 250/ML With 2 sets,2nos. 6A wround pin socket controlled by 16A SP Switch with front plates. with out back Box . | Nos. | 15 | 15 | RO | 30 | 8740 | 2300 | 262200 | 69000 | 331200 |  | 331200
6.3 | Pop up box with 2 nos 13A flat pin socket controlled by 1 16A switch | Nos. | RO | RO | RO | 0 | 6000 | 1500 | 0 | 0 | 0 |  | 0
6.31 | 1no. 6/16A 6 pin universal round pin socket controlled by 16A SP Switch with indicator - Raw Power. IP 44 | Nos. | RO | RO | 45 | 45 | 378 | 83 | 17010 | 3735 | 20745 |  | 20745
6.32 | 2 Module GI back box for data,TV, HDMI outlets in partitions | Nos. | 55 | 100 | 45 | 200 | 46 | 19 | 9200 | 3800 | 13000 |  | 13000
[6 empty] | 0 |  |  | 0 | 0 | 0 |  | 0
6.4 | Industrial sockets with IP 44 FOR SERVER / HUB/ NETWORK ROOMS- With required Box & all accessories to mount the same below the false floor . |  |  |  |  | 0 |  |  | 0 | 0 | 0 |  | 0
. | [5 empty] | 0 |  |  | 0 | 0 | 0 |  | 0
6.41 | 1No. 20A 3 pin 1 phase Industrial type socket with plug top in polycarbonate enclosure controlled by 32A DP MCB at DB level | Nos. | RO | 2 | RO | 2 | 1747 | 598 | 3494 | 1196 | 4690 |  | 4690
6.42 | 1No. 32A 3 pin 1 phase Industrial type socket with plug top in polycarbonate enclosure controlled by 32A DP MCB at DB level | Nos. | 8 | RO | RO | 8 | 1808 | 782 | 14464 | 6256 | 20720 |  | 20720
6.43 | 1No. 32A 3 pin 3 phase Commando socket with plug | Nos. | RO | RO | RO | 0 | 1200 | 350 | 0 | 0 | 0 |  | 0
[6 empty] | 0 |  |  | 0 | 0 | 0 |  | 0
6.5 | Industrial sockets with IP67 - for HVAC outdoor units / kitchen / café |  |  |  |  | 0 |  |  | 0 | 0 | 0 |  | 0
[6 empty] | 0 |  |  | 0 | 0 | 0 |  | 0
6.51 | 63A, 1ph 3 pin Industrial PC socket with plug top in PC enclosure controlled by DP MCB | Nos. | RO | RO | 2 | 2 | 7130 | 1380 | 14260 | 2760 | 17020 |  | 17020
6.52 | 32A/20A, 1ph 3 pin Industrial PC socket with plug top in PC enclosure controlled by DP MCB | Nos. | 4 | 4 | 12 | 20 | 5617 | 884 | 112340 | 17680 | 130020 |  | 130020
6.53 | 40A, 1ph 3 pin Industrial PC socket with plug top in PC enclosure controlled by DP MCB | Nos. | RO | RO | 2 | 2 | 5617 | 884 | 11234 | 1768 | 13002 |  | 13002
6.54 | 32A/40A, 3Ph 5 Pin Industrial PC socket with plug top in PC enclosure controlled by 4P MCB | Nos. | 4 | RO | 7 | 11 | 5226 | 902 | 57486 | 9922 | 67408 |  | 67408
6.55 | 63A, 3Ph 5 Pin Industrial PC socket with plug top in PC enclosure controlled by 4P MCB | Nos. | RO | RO | 7 | 7 | 8188 | 1380 | 57316 | 9660 | 66976 |  | 66976
| Isolators for HVAC |  |  |  | RO | 0 |  |  | 0 | 0 | 0 |  | 0
6.55 | Supplying, laying, testing and commissioning of suitable 16/40/63A DP MCB Isolator in Polycarbonate enclosure box (Outdoor type) | Nos. | RO | RO | RO | 0 | 1410 | 220 | 0 | 0 | 0 |  | 0
6.56 | 63A 4P 300mA RCBO in standard PC enclosure | Nos. | RO | RO | RO | 0 | 5710 | 860 | 0 | 0 | 0 |  | 0
6.57 | 25A 4P 300mA RCBO in standard PC enclosure | Nos. | RO | RO | RO | 0 | 4680 | 710 | 0 | 0 | 0 |  | 0
[6 empty] | 0 |  |  | 0 | 0 | 0 |  | 0
| Total for Power Receptacles & Isolators | [7 empty] | 1404604 | 303093 | 1707697 |  | 0
[6 empty] | 0 | [6 empty] | 0
7 | CABLE TRAYS, RACEWAYS & CONDUIT FOR POWER & NETWORKING |  |  |  |  | 0 | [6 empty] | 0
[6 empty] | 0 |  |  | 0 | 0 | 0 |  | 0
| Slotted angle GI ready made cable trays of 14 SWG. Pre galvanised, Quoted rates for installation shall include necessary anchor fasteners / 'Slotted channel' supports @ 1000mm interval etc., to suit site conditions. |  |  |  |  | 0 |  |  | 0 | 0 | 0 |  | 0
| Earthing strip of 25x3mm GI for entire length of the tray to be considered |  |  |  |  | 0 |  |  | 0 | 0 | 0 |  | 0
[6 empty] | 0 |  |  | 0 | 0 | 0 |  | 0
7.1 | Ladder Type |  |  |  |  | 0 |  |  | 0 | 0 | 0 |  | 0
[6 empty] | 0 |  |  | 0 | 0 | 0 |  | 0
7.11 | 600 x 50mm Size tray with support | Mts. | R0 | R0 | R0 | 0 | 550 | 285 | 0 | 0 | 0 |  | 0
7.12 | 450 x 50mm Size tray with support in shaft | Mts. | 15 | 45 | 15 | 75 | 460 | 235 | 34500 | 17625 | 52125 |  | 52125
7.13 | 300 x 50mm Size tray with support in shaft | Mts. | 20 | 20 | 8 | 48 | 424 | 152 | 20352 | 7296 | 27648 |  | 27648
7.14 | 150 x 50mm Size tray with support | Mts. | R0 | R0 | R0 | 0 | 410 | 105 | 0 | 0 | 0 |  | 0
7.15 | 100 x 50mm Size tray with support | Mts. | 5 | 5 | 5 | 15 | 359 | 83 | 5385 | 1245 | 6630 |  | 6630
[6 empty] | 0 |  |  | 0 | 0 | 0 |  | 0
7.2 | Perforated type tray |  |  |  |  | 0 |  |  | 0 | 0 | 0 |  | 0
[6 empty] | 0 |  |  | 0 | 0 | 0 |  | 0
7.21 | 600 x 50mm Size tray with support | Mts. |  |  |  | 0 |  |  | 0 | 0 | 0 |  | 0
7.22 | 450 x 50mm Size tray with support | Mts. | 23.75 | 23.75 | R0 | 47.5 | 690 | 235 | 32775 | 11162.5 | 43937.5 |  | 43937.5
7.23 | 300 x 50mm Size tray with support | Mts. | 42.75 | 42.75 | 42.75 | 128.25 | 543 | 152 | 69639.75 | 19494 | 89133.75 |  | 89133.75
7.24 | 150 x 50mm Size tray with support | Mts. | 33.25 | 33.25 | 5.7 | 72.2 | 396 | 97 | 28591.2 | 7003.4 | 35594.6 |  | 35594.6
7.25 | 100 x 50mm Size tray with support | Mts. | 42.75 | 42.75 | 7.6 | 93.1 | 341 | 83 | 31747.1 | 7727.3 | 39474.4 |  | 39474.4
7.26 | 150 x 50mm Size tray with support for lighting | Mts. | 52.25 | 52.25 | 14.25 | 118.75 | 396 | 97 | 47025 | 11518.75 | 58543.75 |  | 58543.75
7.27 | 100 x 50mm Size tray with support for lighting | Mts. | 128.25 | 137.75 | 23.75 | 289.75 | 341 | 83 | 98804.75 | 24049.25 | 122854 |  | 122854
7.28 | 50 x 50mm Size tray with support for lighting | Mts. | 114 | 128.25 | 42.75 | 285 | 295 | 69 | 84075 | 19665 | 103740 |  | 103740
[6 empty] | 0 |  |  | 0 | 0 | 0 |  | 0
7.3 | Ceiling & Floor Raceway |  |  |  |  | 0 |  |  | 0 | 0 | 0 |  | 0
| Supply & installation of raceways of following sizes made out of 1.6 mm thick Pre Galvanised sheet complete with Push type for ceiling & screwed type cover for floor & wall drops of below specified thickness with countersunk type screws. |  |  |  |  | 0 |  |  | 0 | 0 | 0 |  | 0
| Note : The rate quoted shall include providing earthing for the Wireway trunking with support hardware. (Usage of jumper wire at joining is acceptable) |  |  |  |  | 0 |  |  | 0 | 0 | 0 |  | 0
| Suitable size of Threaded rod to be used for respective raceways at distance of 1500mm each. |  |  |  |  | 0 |  |  | 0 | 0 | 0 |  | 0
| 100 x 40mm to 200 x 40mm raceway shall be with 6mm threaded rod. 250 x 40mm to 300 x 40mm raceway shall be with 8mm threaded rod. 450 x 40mm raceway shall be with 12mm threaded rod. |  |  |  |  | 0 |  |  | 0 | 0 | 0 |  | 0
| Ceiling raceway with 1.6 mm thick cover |  |  |  |  | 0 |  |  | 0 | 0 | 0 |  | 0
[6 empty] | 0 |  |  | 0 | 0 | 0 |  | 0
7.31 | (50x50)mm GI raceway with 1.6mm thick cover Backbone connectivity | Mts. | 57 | 57 | RO | 114 | 414 | 69 | 47196 | 7866 | 55062 |  | 55062
7.32 | (100x40)mm GI raceway | Mts. | 123.5 | 128.25 | 57 | 308.75 | 534 | 83 | 164872.5 | 25626.25 | 190498.75 |  | 190498.75
7.33 | (150x40)mm GI raceway | Mts. | 58.9 | 62.7 | 23.75 | 145.35 | 644 | 97 | 93605.4 | 14098.95 | 107704.35 |  | 107704.35
7.34 | (200x40)mm GI raceway | Mts. | 9.5 | 14.25 | RO | 23.75 | 764 | 111 | 18145 | 2636.25 | 20781.25 |  | 20781.25
7.35 | (250x40)mm GI raceway | Mts. | 7.6 | 9.5 | RO | 17.1 | 884 | 125 | 15116.4 | 2137.5 | 17253.9 |  | 17253.9
7.36 | (300x40)mm GI raceway | Mts. | 28.5 | 42.75 | RO | 71.25 | 1003 | 152 | 71463.75 | 10830 | 82293.75 |  | 82293.75
7.37 | (450x40)mm GI raceway | Mts. | 52.25 | 57 | RO | 109.25 | 1353 | 235 | 147815.25 | 25673.75 | 173489 |  | 173489
7.38 | (100x50mm ladder type cable tray with 1.6 mm thick cover-FOR NETWORK CABLE IN SHAFT | Mts. | 128.25 | 137.75 | RO | 266 | 525 | 83 | 139650 | 22078 | 161728 |  | 161728
[6 empty] | 0 |  |  | 0 | 0 | 0 |  | 0
| Floor raceway with 2.0 mm thick cover |  |  |  |  | 0 |  |  | 0 | 0 | 0 |  | 0
[6 empty] | 0 |  |  | 0 | 0 | 0 |  | 0
7.39 | (50x50)mm GI raceway | Mts. | R0 | R0 | RO | 0 | 320 | 75 | 0 | 0 | 0 |  | 0
7.4 | (100x40)mm GI raceway | Mts. | 261.25 | 275.5 | 38 | 574.75 | 433 | 83 | 248866.75 | 47704.25 | 296571 |  | 296571
7.41 | (150x40)mm GI raceway | Mts. | 42.75 | 42.75 | RO | 85.5 | 562 | 97 | 48051 | 8293.5 | 56344.5 |  | 56344.5
7.42 | (200x40)mm GI raceway | Mts. | 19 | 19 | RO | 38 | 690 | 111 | 26220 | 4218 | 30438 |  | 30438
7.43 | (250x40)mm GI raceway | Mts. | 42.75 | 42.75 | RO | 85.5 | 819 | 125 | 70024.5 | 10687.5 | 80712 |  | 80712
7.44 | (300x40)mm GI raceway | Mts. | 33.25 | 33.25 | RO | 66.5 | 948 | 152 | 63042 | 10108 | 73150 |  | 73150
[6 empty] | 0 |  |  | 0 | 0 | 0 |  | 0
7.45 | (100x40)mm Aluminium box section raceways | Mts. | R0 | R0 | RO | 0 |  |  | 0 | 0 | 0 |  | 0
[6 empty] | 0 |  |  | 0 | 0 | 0 |  | 0
7.4 | POWDER COATED TRUNKING FOR HUB ROOM/ SERVER ROOM |  |  |  |  | 0 |  |  | 0 | 0 | 0 |  | 0
| Supply & Installation of 2mm thick steel sheet factory fabricated post galvanized raceways to be laid in ceiling/floor for Data center area with necessary knockouts & cutouts for installation of Industrial socket outlets. The rate to include 2 mm thick Powder coated cover with fixing accessories, Earthing with 6Sqmm copper wire, complete with necessary supports, bends, access boxes and cross over junction boxes as per specification and site requirement. |  |  |  |  | 0 |  |  | 0 | 0 | 0 |  | 0
| 1) Power raceways should have different colour for each source. i.e source-1 should have Blue colour & source-2 should have Red colour. 2) Date raceway should have seimens grey colour. |  |  |  |  | 0 |  |  | 0 | 0 | 0 | *Quoted for Ceiling Raceway, Power Coated | 0
7.41 | (100x75)mm Raceways | Mts. | R0 | 45 | RO | 45 | 681 | 83 | 30645 | 3735 | 34380 |  | 34380
7.42 | (150x100)mm Raceways | Mts. | 30.4 | 30.4 | RO | 60.8 | 847 | 97 | 51497.6 | 5897.6 | 57395.2 |  | 57395.2
7.43 | (450x100)mm Raceways | Mts. | 14.25 | 14.25 | RO | 28.5 | 1831 | 235 | 52183.5 | 6697.5 | 58881 |  | 58881
7.44 | (450x75)mm ladder type cable tray | Mts. | 14.25 | 23.75 | RO | 38 | 1482 | 235 | 56316 | 8930 | 65246 |  | 65246
[6 empty] | 0 |  |  | 0 | 0 | 0 |  | 0
7.5 | JUNCTION BOXES - 2mm Thick cover |  |  |  |  | 0 |  |  | 0 | 0 | 0 |  | 0
| Supply & installation of Electro Galvanised junction boxes with 2mm cover with countersunk type screws for floor raceways of the following sizes.The dimension of the same shall be as follows. Open side of the junction box needs to be closed with GI cover |  |  |  |  | 0 |  |  | 0 | 0 | 0 |  | 0
7.51 | (60x60x55)mm GI floor junction box | Nos. | 15 | 15 | RO | 30 | 258 | 56 | 7740 | 1680 | 9420 |  | 9420
7.52 | (110x110x55)mm GI floor junction box | Nos. | 90 | 75 | 15 | 180 | 322 | 65 | 57960 | 11700 | 69660 |  | 69660
7.53 | (160x160x55)mm GI floor junction box | Nos. | 20 | 20 | 25 | 65 | 387 | 83 | 25155 | 5395 | 30550 |  | 30550
7.54 | (210x210x55)mm GI floor junction box | Nos. | 8 | 8 | RO | 16 | 479 | 102 | 7664 | 1632 | 9296 |  | 9296
7.55 | (260x260x55)mm GI floor junction box | Nos. | 15 | 15 | RO | 30 | 534 | 111 | 16020 | 3330 | 19350 |  | 19350
7.56 | (310x310x55)mm GI floor junction box | Nos. | 17 | 17 | RO | 34 | 819 | 166 | 27846 | 5644 | 33490 |  | 33490
7.57 | (460x460x55)mm GI floor junction box | Nos. | 5 | 5 | RO | 10 | 1344 | 313 | 13440 | 3130 | 16570 |  | 16570
[6 empty] | 0 |  |  | 0 | 0 | 0 |  | 0
7.6 | FLOOR/WALL CHIPPING FOR RACEWAYS/CONDUIT |  |  |  |  | 0 |  |  | 0 | 0 | 0 |  | 0
| Cutting of floor screeding for accommodating the floor raceways / conduits for the below mentioned size of raceways / conduits. The rate shall include closing of extra gap with cement mortar, cutting and making good to the original level. |  |  |  |  | 0 |  |  | 0 | 0 | 0 | *Quoted for 2mm thick,GI | 0
7.61 | (50x50)mm GI raceway | Mts. | R0 | R0 | RO | 0 | 420 | 180 | 0 | 0 | 0 |  | 0
7.62 | (100x40)mm GI raceway | Mts. | 237.5 | 275.5 | RO | 513 | 387 | 166 | 198531 | 85158 | 283689 |  | 283689
7.63 | (150x40)mm GI raceway | Mts. | 42.75 | 42.75 | RO | 85.5 | 387 | 166 | 33088.5 | 14193 | 47281.5 |  | 47281.5
7.64 | (200x40)mm GI raceway | Mts. | 19 | 19 | RO | 38 | 387 | 166 | 14706 | 6308 | 21014 |  | 21014
7.65 | (250x40)mm GI raceway | Mts. | 42.75 | 42.75 | RO | 85.5 | 387 | 166 | 33088.5 | 14193 | 47281.5 |  | 47281.5
7.66 | (300x40)mm GI raceway | Mts. | 33.25 | 33.25 | RO | 66.5 | 387 | 166 | 25735.5 | 11039 | 36774.5 |  | 36774.5
7.67 | 25mm dia, 2mm thick, PVC conduit | Mts. | 42.75 | 42.75 | RO | 85.5 | 387 | 166 | 33088.5 | 14193 | 47281.5 |  | 47281.5
[6 empty] | 0 |  |  | 0 | 0 | 0 |  | 0
7.7 | EMPTY CONDUITS |  |  |  |  | 0 |  |  | 0 | 0 | 0 |  | 0
| Supply & installation of 2 mm thick FRLS / MS type conduits of following sizes for open / enclosed wiring complete with all necessary accessories |  |  |  |  | 0 |  |  | 0 | 0 | 0 |  | 0
| Color coding for PVC conduits shall be as below |  |  |  |  | 0 |  |  | 0 | 0 | 0 |  | 0
| Raw power and lighting- Black UPS power - Blue Data and voice- Grey |  |  |  |  | 0 |  |  | 0 | 0 | 0 |  | 0
7.71 | 19 mm dia, 2mm thick, FRLS type PVC conduit | Mts. | 190 | 209 | 23.75 | 422.75 | 46 | 19 | 19446.5 | 8032.25 | 27478.75 |  | 27478.75
7.72 | 25 mm dia, 2mm thick, FRLS type PVC conduit | Mts. | 389.5 | 413.25 | 30.4 | 833.15 | 56 | 19 | 46656.4 | 15829.85 | 62486.25 |  | 62486.25
7.73 | 32 mm dia, 2mm thick, FRLS type PVC conduit | Mts. | 33.25 | 33.25 | 42.75 | 109.25 | 74 | 19 | 8084.5 | 2075.75 | 10160.25 |  | 10160.25
7.74 | 20 mm dia, 1.8 mm thick, PVC FRLS conduit | Mts. | 118.75 | 128.25 | RO | 247 | 46 | 19 | 11362 | 4693 | 16055 |  | 16055
7.75 | 25 mm dia, 1.8 mm thick, PVC FRLS conduit | Mts. | 475 | 498.75 | RO | 973.75 | 56 | 19 | 54530 | 18501.25 | 73031.25 |  | 73031.25
[6 empty] | 0 |  |  | 0 | 0 | 0 |  | 0
| Total for Cable trays, Raceways & Conduits - Power & Networking | [7 empty] | 2431747.85 | 570731.35 | 3002479.2 |  | 0
[6 empty] | 0 | [6 empty] | 0
8 | EARTHING |  |  |  |  | 0 | [6 empty] | 0
[6 empty] | 0 |  |  | 0 | 0 | 0 |  | 0
| Supplier shall provide installation methodology for the installation of earth electrodes |  |  |  |  | 0 |  |  | 0 | 0 | 0 |  | 0
| Supplier shall be present during the installation of earth electrode |  |  |  |  | 0 |  |  | 0 | 0 | 0 |  | 0
| All the testing at site shall be conducted in presence of consultants |  |  |  |  | 0 |  |  | 0 | 0 | 0 |  | 0
| Rate shall include all civil works including construction of chamber with PCC cover |  |  |  |  | 0 |  |  | 0 | 0 | 0 |  | 0
| Rate shall include driveway crossing pavers removal and relaying work |  |  |  |  | 0 |  |  | 0 | 0 | 0 |  | 0
[6 empty] | 0 |  |  | 0 | 0 | 0 |  | 0
8.01 | Pipe electrode earth station as per IS 3043 with 38mm dia Class B GI pipe, GI watering funnel with salt, charcoal, 450mm x 450mm x 300mm brick masonry chamber with CI frame and CI cover etc., complete. | Nos. |  |  |  | 0 |  |  | 0 | 0 | 0 |  | 0
8.02 | Maintenance Free Earth pits, earthing system shall be installed as per supplier guidelines /details. Rate shall include necessary civil works. The GI frame / chamber shall be of 300 x 300 mm. The rate shall also include necessary backfilling compounds for each earth pit as per manufacturer's guidelines. The unit shall be similar to T39 of Ashlok earth pit of height 3000mm and outer dia of 80mm . | Nos. | 2 | RO | RO | 2 | 13800 | 2300 | 27600 | 4600 | 32200 |  | 32200
[6 empty] | 0 |  |  | 0 | 0 | 0 |  | 0
| EARTH CONDUCTORS |  |  |  |  | 0 |  |  | 0 | 0 | 0 |  | 0
| GI/Cu earth conductors on cable tray or below ground as per site condition. All Cu. Strips shall be run in pvc heat shrinkable sleeve & mounted on insulation mounts. Cost of civil works shall be included for strips laid below ground. |  |  |  |  | 0 |  |  | 0 | 0 | 0 |  | 0
| GI conductors |  |  |  |  | 0 |  |  | 0 | 0 | 0 |  | 0
8.03 | 40 x 6 mm GI earth strip. | Mtrs | RO | RO | RO | 0 | 266 | 45 | 0 | 0 | 0 |  | 0
8.04 | 25 x 6 mm GI earth strip. | Mtrs | 76 | 76 | 19 | 171 | 115 | 33 | 19665 | 5643 | 25308 |  | 25308
8.05 | 25 x 3 mm GI earth strip. | Mtrs | 117.8 | 117.8 | 58.9 | 294.5 | 83 | 28 | 24443.5 | 8246 | 32689.5 |  | 32689.5
[6 empty] | 0 |  |  | 0 | 0 | 0 |  | 0
| CU conductors |  |  |  |  | 0 |  |  | 0 | 0 | 0 |  | 0
| COPPER CONDUCTOR - 25 x 6mm electrolytic grade copper strip in PVC sleeve & on insulated mounts, ground bus risers for earthing | Mtrs |  |  |  | 0 |  |  | 0 | 0 | 0 |  | 0
8.06 | 25 x 3 mm Cu earth strip with PVC sleeves. | Mtrs | RO | RO | RO | 0 | 1200 | 30 | 0 | 0 | 0 |  | 0
8.07 | 8 SWG tinned copper wire, with terminations on both the ends | Mtrs |  |  |  | 0 | 210 | 20 | 0 | 0 | 0 |  | 0
8.08 | 1C x 70 sq mm copper flexible cable with end terminations for third pin earthing from Earth pit to UPS room | Mtrs | R0 | R0 | RO | 0 | 1558 | 50 | 0 | 0 | 0 |  | 0
8.07 | 1C x 50 sq mm copper flexible cable with end terminations for third pin earthing from Earth pit to UPS room | Mtrs | R0 | R0 | RO | 0 | 1100 | 40 | 0 | 0 | 0 |  | 0
8.08 | 1C x 35 sq mm copper flexible cable with end terminations for third pin earthing from Earth pit to UPS room | Mtrs | 142.5 | RO | RO | 142.5 | 640 | 37 | 91200 | 5272.5 | 96472.5 |  | 96472.5
8.09 | 1C x 16 sqmm copper flexible cable with end terminations for third pin earthing & DB Body earthing | Mtrs | 152 | 42.75 | RO | 194.75 | 295 | 28 | 57451.25 | 5453 | 62904.25 |  | 62904.25
8.08 | 1C x 10 sqmm copper flexible cable with end terminations for rack and third pin earthing & DB Body earthing | Mtrs | 19 | 19 | RO | 38 | 192 | 28 | 7296 | 1064 | 8360 |  | 8360
8.09 | 1C x 6 sq mm for copper flexible cable with end terminations rack and third pin earthing & DB Body earthing | Mtrs | 152 | 152 | RO | 304 | 108 | 19 | 32832 | 5776 | 38608 |  | 38608
| PVC Insulated & Un Armoured Copper Conductor cables (YY Type) 1 Core x 150 Sq. mm | Mtrs | R0 | R0 | RO | 0 | 3379 | 60 | 0 | 0 | 0 |  | 0
| Earth Bus bars |  |  |  |  | 0 |  |  | 0 | 0 | 0 |  | 0
8.1 | 300mm long, 25 x 6 Copper Earth bus suitable for terminating suitable strip with holes at regular intervals connected to main bus. The same need to be mounted in MS powder coated box with transparent cover. | No's | 1 | 1 | RO | 2 | 4968 | 920 | 9936 | 1840 | 11776 |  | 11776
8.11 | 300mm long, 25 x 3 GI Earth bus suitable for terminating 8 SWG copper wire with holes at regular intervals connected to main bus. The same need to be mounted in MS powder coated box with transparent cover. | No's | 2 | 6 | 2 | 10 | 2852 | 460 | 28520 | 4600 | 33120 |  | 33120
8.12 | 300mm long, 25 x 3 Copper Earth bus suitable for terminating 6 sq mm copper wire with holes at regular intervals connected to main bus. The same need to be mounted in MS powder coated box with transparent cover. | No's | 1 | 1 | RO | 2 | 3864 | 782 | 7728 | 1564 | 9292 |  | 9292
[6 empty] | 0 | [6 empty] | 0
| Total for Earthing | [7 empty] | 306671.75 | 44058.5 | 350730.25 |  | 0
[6 empty] | 0 | [6 empty] | 0
9 | MISCELLANEOUS ITEMS |  |  |  |  | 0 | [6 empty] | 0
[6 empty] | 0 |  |  | 0 | 0 | 0 |  | 0
| All the items shall be of IS certified |  |  |  |  | 0 |  |  | 0 | 0 | 0 |  | 0
| All the items shall be in line with CEIG requirement |  |  |  |  | 0 |  |  | 0 | 0 | 0 |  | 0
9.01 | Rubber mat 3300V grade ISI approved - 2 m x 1m | Nos. | 2 | 2 | RO | 4 | 2944 | 460 | 11776 | 1840 | 13616 |  | 13616
9.02 | Shock treatment chart as approved by the Electrical Inspectorate mounted on teak wood frame and suitable for wall mounting in 3 languages (Local language, English & Hindi) | Nos. | 1 | 1 | RO | 2 | 1380 | 460 | 2760 | 920 | 3680 |  | 3680
9.03 | First aid kit | Nos. | 1 | 1 | RO | 2 | 1840 | 460 | 3680 | 920 | 4600 |  | 4600
9.04 | Danger boards | Nos. | 1 | 1 | RO | 2 | 1380 | 460 | 2760 | 920 | 3680 |  | 3680
9.05 | Supply & fixing of rubber gloves, gloves stand with wall mounting of Approved Make & as per supply voltage | Nos. | 1 | 1 | RO | 2 | 552 | 92 | 1104 | 184 | 1288 |  | 1288
9.06 | Laminated Schematic with glass frame | Nos. | 1 | 1 | RO | 2 | 1840 | 460 | 3680 | 920 | 4600 |  | 4600
9.07 | 100mm wide x 100mm depth DB cabinet M S Powder coated including supply & installation. | Sqft | 64 | 64 | RO | 128 | 189 | 28 | 24192 | 3584 | 27776 |  | 27776
[6 empty] | 0 |  |  | 0 | 0 | 0 |  | 0
9.08 | Professional Charges: |  |  |  |  | 0 |  |  | 0 | 0 | 0 |  | 0
| Professional charges towards filing application, preparation of drawings in necessary formats for approval, follow up and arranging approval of drawings, scheme by Local electricity authority / Electrical Inspectorate, obtaining clearance from electricity authority / Electrical Inspectorate. Area - 15000 Sq.ft. | LS | 1 |  | RO | 1 | 0 | 138000 | 0 | 138000 | 138000 |  | 138000
| Professional charges towards filing application, preparation of drawings in necessary formats for approval, follow up and arranging approval of drawings, scheme by Local electricity authority / Electrical Inspectorate, obtaining clearance from electricity authority / Electrical Inspectorate. Area - 12000 Sq.ft. | LS |  | 1 | RO | 1 | 0 | 138000 | 0 | 138000 | 138000 |  | 138000
[6 empty] | 0 |  |  | 0 | 0 | 0 |  | 0
9.09 | As built drawings: |  |  |  |  | 0 |  |  | 0 | 0 | 0 |  | 0
| Preparation and Submission of as built drawings of total work executed | LS | 1 | 1 | RO | 2 | 23000 | 4600 | 46000 | 9200 | 55200 |  | 55200
[6 empty] | 0 |  |  | 0 | 0 | 0 |  | 0
9.1 | Temporary lighting and Power |  |  |  |  | 0 |  |  | 0 | 0 | 0 |  | 0
| Providing all equipment necessary for proper illumination of construction work areas as specified. Area - 15000 Sq.ft. |  |  |  |  | 0 |  |  | 0 | 0 | 0 |  | 0
| Providing distribution boards with proper protection and industrial socket to tap power for cutting, grinding, drilling and welding related works. at each floor level. No loose wire connection to be allowed to plug in industrial socket provided in distribution board. Temporary lighting and power including all wiring and supports shall be removed when permanent lighting is installed. The contractor shall take regular lux level readings to ensure the temporary lighting system is installed and maintained as specified. |  |  |  |  | 0 |  |  | 0 | 0 | 0 |  | 0
| Execution |  |  |  |  | 0 |  |  | 0 | 0 | 0 |  | 0
| The contractor is responsible for the installation of temporary lighting systems. The system shall be installed at the earliest and coordinated with other construction activities. |  |  |  |  | 0 |  |  | 0 | 0 | 0 |  | 0
| Installation & Maintenance during construction |  |  |  |  | 0 |  |  | 0 | 0 | 0 |  | 0
| All fixtures and lamps shall be protected from physical damage. Fixtures shall be moved or modified as necessary during the construction process to limit the light being blocked by installed materials and systems. Broken or burned out fixtures shall be fixed or replaced immediately without any extra cost. 1no of fluorescent light to be considered for every 250 sq ft area with all wiring & safety accessories. During construction each closed cabins should have 1no of dedicated light. | LS | 1 | 1 | RO | 2 | 69000 | 13800 | 138000 | 27600 | 165600 |  | 165600
[6 empty] | 0 |  |  | 0 | 0 | 0 |  | 0
10 | EMERGENCY LIGHTING Inverter |  |  |  |  | 0 |  |  | 0 | 0 | 0 |  | 0
1 | 2kVA 1Ph / 1Ph , 230V, Emergency lighting Inverter with 90Min. in parallel mode operation |  |  |  |  | 0 |  |  | 0 | 0 | 0 |  | 0
1.1 | Supply, Unloading, Storing, shifting, installation, testing and commissioning of 1 Phase, 230 volts, 50Hz, 2 KVA Emergency lighting Inverter with all associated accessories. And battery backup - 90Min | Nos | RO | RO | RO | 0 | 40000 | 5000 | 0 | 0 | 0 |  | 0
1.2 | Supply, Unloading, Storing, shifting, installation, testing and commissioning of 3 Phase IN 1 Phase out , 415/230 volts, 50Hz, 10 KVA Emergency lighting Inverter with all associated accessories. And battery backup - 90Min | Nos | RO | RO | RO | 0 | 200000 | 25000 | 0 | 0 | 0 |  | 0
[6 empty] | 0 |  |  | 0 | 0 | 0 |  | 0
1.3 | Rack mounted 16A, 215 Volts, Single phase STS / ATS for HUb rack (Make - Socomec ) | Nos | 2 | RO | RO | 2 | 26496 | 3312 | 52992 | 6624 | 59616 | *24U rack considered | 59616
[6 empty] | 0 | [6 empty] | 0
| Total for Miscellaneous items | [7 empty] | 286944 | 328712 | 615656 |  | 0
[6 empty] | 0 | [6 empty] | 0
10 | Lighting Sensors (MK / Hager Make) |  |  |  |  | 0 |  |  | 0 | 0 | 0 |  | 0
| Supply, Installation, Testing & Commissioning of sensors |  |  |  |  | 0 |  |  | 0 | 0 | 0 |  | 0
10.01 | Daylight sensor with occupancy override | Nos. | R0 | R0 | RO | 0 | 13260 | 500 | 0 | 0 | 0 |  | 0
10.02 | Daylight sensor with occupancy override - Surface mount | Nos. | R0 | R0 | RO | 0 | 13260 | 500 | 0 | 0 | 0 |  | 0
10.03 | Occupancy sensors similar to LCM1061 | Nos. | R0 | R0 | RO | 0 | 3500 | 500 | 0 | 0 | 0 |  | 0
10.04 | Occupancy sensors similar to LRM 1071- Recessed Sensor | Nos. | R0 | R0 | RO | 0 | 3500 | 500 | 0 | 0 | 0 |  | 0
10.05 | Occupancy sensors | Nos. | R0 | R0 | RO | 0 | 3500 | 500 | 0 | 0 | 0 |  | 0
10.06 | Back box with threaded rod supports and conduit to house sensor | Nos. | R0 | R0 | RO | 0 | 350 | 80 | 0 | 0 | 0 |  | 0
| Total for Sensors | [7 empty] | 0 | 0 | 0
0
| Grand Total | [7 empty] | 10177016.6 | 2127530.85 | 12304547.45 |  | 12304547.45

## BOQ_LMS
SI NO | DESCRIPTION | UNIT | Voyager (Qty) | Victor (Qty) |  |  | Total Qty. | RATE |  | AMOUNT |  | TOTAL AMOUNT | REMARKS
|  |  | Ground | Level-02 Office | Level-02 Cafeteria | Level-02, Existing Office |  | SUPPLY | INSTALLATION | SUPPLY | INSTALLATION
1 | Supply of central processor assembled processor with two configurable links. Each processor link can be configured to be a dimmer link, shade link, or dimmer power panel link. Processor accepts 220-240V, 1 phase, 2 wire, 10A feed, (through power supply) Similar to Lutron Quantum/ Athena | Nos | 1 | 1 | RO | RO | 2 | 73125 | 1725 | 146250 | 3450 | 149700 |  | 149700
[7 empty] | 0 |  |  | 0 | 0 | 0 |  | 0
2 | Supply of Lighting control and monitor software, captures floor wise consumption, each event, Energy Reporting & monitoring per processor, | Nos | RO | RO | RO | RO | 0 | 106250 | 6250 | 0 | 0 | 0 |  | 0
[7 empty] | 0 |  |  | 0 | 0 | 0 |  | 0
4 | Supply of Lighting control BACnet softwares for BMS integration | Nos | 1 | 1 | RO | RO | 2 | 118125 | 5750 | 236250 | 11500 | 247750 |  | 247750
[7 empty] | 0 |  |  | 0 | 0 | 0 |  | 0
5 | SITC of Software for Energy Reporting & monitoring per processor, English. Similar to QSW-RPT-PP-A | Nos | 1 | 1 | RO | RO | 2 | 118125 | 5750 | 236250 | 11500 | 247750 |  | 247750
[7 empty] | 0 |  |  | 0 | 0 | 0 |  | 0
6 | Power Supply Unit for supply PDUs to Antenna devices Similar to Lutron QSPS-DH -1 -75 | Nos | 1 | 1 | RO | 1 | 3 | 9563 | 402 | 28689 | 1206 | 29895 |  | 29895
[7 empty] | 0 |  |  | 0 | 0 | 0 |  | 0
7 | SITC of Wireless Occupancy/Vacancy Sensor for rooms with a frequency of 865 MHz, Ceiling mount, infrared, 37.2 sq m (400 sq ft), battery-powered, 102 mm (4.0 in) diameter, white. Similar to LRF5-OCR2B-P-WH | Nos | 10 | 10 | 3 | 12 | 35 | 6188 | 402 | 216580 | 14070 | 230650 |  | 230650
[7 empty] | 0 |  |  | 0 | 0 | 0 |  | 0
8 | Same occupancy sensor as above but with different form factor for Corridors - wall mounted. Hallway sensor LRF5 OWLB/OKLB WH | Nos | RO | RO | RO | RO | 0 | 6875 | 500 | 0 | 0 | 0 |  | 0
[7 empty] | 0 |  |  | 0 | 0 | 0 |  | 0
9 | SITC of Wireless Daylight Sensor for office , closed rooms which works on 865 MHz, ceiling mount, battery-powered, 44 mm (1.6 in) diameter. Similar to LRF5-DCRB-WH | Nos | 48 | 52 | RO | 32 | 132 | 6188 | 402 | 816816 | 53064 | 869880 |  | 869880
[7 empty] | 0 |  |  | 0 | 0 | 0 |  | 0
10 | SITC of Sensor Module, to connect 10 number of sensors either of the Occupancy / Daylight / Personal sensors/PIco. No wired connections, ceiling mount Similar to QSM5-XW-C | Nos | 5.8 | 6.2 | 0.3 | 4.4 | 16.7 | 9563 | 575 | 159702.1 | 9602.5 | 169304.6 |  | 169304.6
[7 empty] | 0 |  |  | 0 | 0 | 0 |  | 0
11 | Supply, Installation, Testing and Commissioning of ceiling mount partition sensor using an infrared transmitter/receiver pair to detect partition movement. The keypads in partitioned room should behave independently when there is a partition and should work the same when there is no partition. Similar to GRX-IRPS-WH + PP-DV | Nos | 0 | 0 | 0 | 0 | 0 | 15625 | 625 | 0 | 0 | 0 |  | 0
[7 empty] | 0 |  |  | 0 | 0 | 0 |  | 0
12 | SITC of Eco system/DALI Dimming controller; Controls 2 independent DALI links with up to 64 DALI ballasts per link. 4 groups of sensors inputs: Occ sensor, daylight sensor and IR sensor. Requires mains/line voltage feed Similar to Lutron QSNE-2DAL-D | Nos | 7.25 | 7.75 | 2 | 5.5 | 22.5 | 62438 | 1150 | 1404855 | 25875 | 1430730 |  | 1430730
[7 empty] | 0 |  |  | 0 | 0 | 0 |  | 0
13 | SITC of Switching module with 4 channels, each channel with minimum 5 amp rating with provisions of sensors inputs: Occ sensor, daylight sensor and IR sensor. Requires mains/line voltage feed Similar to Lutron QSNE-4S 5230D module | Nos | 3 | 3 | RO | 4 | 10 | 24188 | 1150 | 241880 | 11500 | 253380 |  | 253380
[7 empty] | 0 |  |  | 0 | 0 | 0 |  | 0
14 | SITC of Wireless personalised control Keypad with a WPC approved frequency of 865 Mhz, 3 Button with raise and lower for smaller rooms, with faceplate,mounts on glass surfaces also, with guaranteed 10 year battery life along with necessary fixing arrangements and programming at site etc, complete as required similar to Lutron PN2 2B/3B/3BRL TAW +LPFP S1 TAW | Nos | 2 | 2 | RO | 4 | 8 | 9563 | 402 | 76504 | 3216 | 79720 |  | 79720
[7 empty] | 0 |  |  | 0 | 0 | 0 |  | 0
15 | SITC of Wireless personalised control Keypad with a WPC approved frequency of 865 Mhz, 6 Button with raise and lower for bigger rooms, with faceplate,mounts on glass surfaces also, with guaranteed 10 year battery life along with necessary fixing arrangements and programming at site etc, complete as required similar to Lutron PN2 3BRL TAW +PN2 3B TAW +LPFP S2 TAW | Nos | 4 | 4 | RO | 4 | 12 | 10688 | 402 | 128256 | 4824 | 133080 |  | 133080
[7 empty] | 0 |  |  | 0 | 0 | 0 |  | 0
16 | Touch Screen IPAD - mini for control of lighting through software | Nos | RO | RO | RO | RO | 0 |  |  | 0 | 0 | 0 |  | 0
[7 empty] | 0 |  |  | 0 | 0 | 0 |  | 0
17 | SITC of wired network interface for AV integration | Nos | 1 | 1 | RO | 1 | 3 | 95625 | 4025 | 286875 | 12075 | 298950 |  | 298950
[7 empty] | 0 |  |  | 0 | 0 | 0 |  | 0
18 | Supply of desktop server with Microsoft Windows 2010 Server Operating System Installed. The hardware Includes the computer with a high performance hard drive for maximum data integrity, a monitor, a keyboard and a mouse. | Nos | RO | RO | RO | RO | 0 | 218750 | 6250 | 0 | 0 | 0 |  | 0
[7 empty] | 0 |  |  | 0 | 0 | 0 |  | 0
19 | Supply of wire landing board. QS-WLB | Nos | 2 | 2 | RO | 2 | 6 | 9563 | 575 | 57378 | 3450 | 60828 |  | 60828
[7 empty] | 0 |  |  | 0 | 0 | 0 |  | 0
20 | CAT 6 Cable | Rmt | RO | RO | RO | RO | 0 | 35 | 8 | 0 | 0 | 0 |  | 0 | *Dlink
[7 empty] | 0 |  |  | 0 | 0 | 0 |  | 0
21 | 8 port Network switch | Nos | RO | RO | RO | RO | 0 | 81250 | 3500 | 0 | 0 | 0 |  | 0
[7 empty] | 0 |  |  | 0 | 0 | 0 |  | 0
22 | QS cable for power and data similar to Lutron GRX-CBL-46L Cable Common – 12 AWG (4.0 mm2); Power – 12 AWG (4.0 mm2); MUX Data – 22 AWG (0.25 mm2); Data – 22 AWG (0.25 mm2); Sense Line – 18 AWG (0.75 mm2); Drain Wire – 24 AWG (0.2 mm2) | Rmt | 180 | 185 | 45 | 250 | 660 | 96 | 54 | 63360 | 35640 | 99000 |  | 99000
[7 empty] | 0 |  |  | 0 | 0 | 0 |  | 0
23 | Complete commissioning of the system | LS | 1 | 1 | RO | 1 | 3 | 95625 |  | 286875 | 0 | 286875 |  | 286875
[7 empty] | 0 |  |  | 0 | 0 | 0 |  | 0
24 | Distribution Board for placing LMS devices (4 tier 56 DB) Schneider Make | Nos | 1 | 1 | RO | 1 | 3 | 20813 | 2875 | 62439 | 8625 | 71064 |  | 71064
| Sub Total | [8 empty] | 4448959.1 | 209597.5 | 4658556.6 |  | 4658556.6

## BOQ_LEED
Project |  | M/s Societe Generale
Sl. No | Code | Description | Location | Unit | Quantity | Rate | AMOUNT | Remarks
LEED and WELL points
Terms and conditions for LEED v4 PLATINUM as below: 1. Clients to have renewable energy use and has to be reflected and accounted as wheeled energy in electricity bills. 2. REC purchases to be analyzed if any. Note:- LEED Certification is only for the New fit out area not for refurb areas
1 |  | LEED REGISTRATION |  | Ls | 1 |  | 0 |  | 0
|  | Carrying out LEED (Leadership in Energy and Environmental Design) registration for the project under the appropriate LEED rating system (e.g., LEED ID+C, LEED NC, or LEED O+M), including all coordination, documentation, and administrative formalities required for official registration with the U.S. Green Building Council (USGBC) or Green Business Certification Inc. (GBCI). | [6 empty] | 0
|  | Preparing and submitting the required documentation for LEED project registration with USGBC/GBCI. Payment of applicable registration fees to USGBC/GBCI on behalf of the client (to be reimbursed as per actuals if applicable). Coordination with the design, construction, and sustainability teams to gather necessary information for registration. Uploading project information on the LEED Online platform and creating the project account. Providing support in selecting the appropriate LEED rating system based on project type and scope. Maintaining communication with USGBC/GBCI for acknowledgment, updates, and verification of registration status. Submitting registration confirmation and official receipt for client records. Inclusions: Administrative, consultancy, and coordination charges for LEED registration. All documentation support for initial LEED project setup on LEED Online. Liaison with project stakeholders for registration completion. | [6 empty] | 0
0
2 |  | WELL (HSR) |  | Ls | 1 |  | 0 |  | 0
|  | WELL ( HSR ) related to Indoor air quality for new fitout (GF- Voayger ,2F (Full Floor)- Right top quadrant) | [6 empty] | 0
0
2.01 |  | LEED & WELL CONSULTANT |  | Ls | 1 |  | 0 |  | 0
|  | Engaging a qualified and USGBC-accredited LEED Consultant to provide complete consultancy services for achieving LEED Certification for the project under the applicable rating system (LEED ID+C, LEED NC, or LEED O+M). The consultant shall guide the project team from registration to certification, ensuring compliance with all required LEED prerequisites and credits. | [6 empty] | 0
|  | Total Amount Of LEED & WELL |  |  |  |  | 0 |  | 0

## Make List
ANNEXURE -4
PROPOSED MAKE OF MATERIALS
S.No. | Item | Make | SG Preferred Make
PROPOSED MAKES FOR CIVIL & INTERIOR WORKS
PROPOSED MAKES FOR MEP
1 | Electrical Panels | VV Systems
2 | LT Cables | Polycab
3 | Copper Wires | Polycab
4 | Switches & Sockets | Honeywell MK-Eva
5 | Power Cube | CJ Infra
6 | MCB / ELCB / MCCB | Schneider
7 | Distribution System | Schneider
8 | Industrial Socket | Neptune- BALS
9 | PVC Conduits | VIP/Precision/Universal | VIP
10 | Batteries | Exide / Quanta
11 | Inverter | Socomec
12 | Light Fixtures | Revix
13 | Decorative Light Fixtures | Revix
14 | LMS | Lutron / Zencontrol / Helver
15 | GI Ducts | Ductofab / GP Spira / Dev duct | GP Spira
16 | GI Sheets | Jindal / Tata
17 | Diffusers | Airmaster / Systemair / Synchro | Airmaster
18 | Grills | Airmaster / Systemair / Synchro | Airmaster
19 | Thermal Insulation (Nitrile rubber) | K-Flex / Armaflex / A-Flex
20 | Acoustic Insulation (Nitrile rubber) | K-Flex / Armaflex / A-Flex
21 | Acoustic Insulation (Fiberglass) | UP Twiga
22 | VCD and Fire Dampers | Airmaster / Systemair / Synchro | Airmaster
23 | Mixing Box | Airmaster / Systemair / Synchro | Airmaster
24 | Butterfly Damper | Airmaster / Systemair / Synchro | Airmaster
25 | Flexible Ducts | UP Twiga / Seven Star
26 | Collar Damper | Airmaster / Systemair | Airmaster
27 | Dx. units & VRF units | Bluestar / Daikin | Bluestar
28 | Refrigerant Pipes | Total line / Rajco / Nippon
29 | Inline Fans | Caryaire / Kruger / Systemair | Caryaire
30 | Plumbing Fixtures & Accessories | Hindware / Jaquar / Euronics
31 | Sink and Tap | Nirali / Futura
32 | PVC Pipes | Astral pipes / Supreme / Finolex
33 | PHE Valves | Zoloto / Leader | Zoloto
34 | GI - Pipe | Jindal ( Hissar ) / TATA
35 | Sprinkler | Tyco / New age / HD | Tyco
36 | Flexible Drops | Tyco / New age / HD | Tyco-Braided
37 | Fire Extinguishers | Safex / Excellent/ Eversafe | Safex
38 | Fire Signages | Prolite / Agnis / Agni
39 | Fire Alarm Panel | Honeywell Notifier
40 | Smoke Detectors / heat Detectors | Honeywell Notifier
41 | Cables/Wires | Polycab / Ravicab / Varsha /Calliplast | Polycab
42 | MS Conduits | Bharat / BEC | Bharat
43 | PA Speakers | Honeywell
44 | Amplifier | Honeywell
45 | Microphone | Honeywell
46 | Cables/Wires | Polycab / KEI / Bonton | Polycab
47 | Rodent Repellent System | Maser / C-System / Varna
48 | WLD System | Maser / C-System / Varna
49 | CCTV | Honeywell
50 | NVR | Honeywell
51 | Access Control | Tyco (iStar Ultra)
52 | Turnstile | P-Gate, Turnstile-KABA | P-Gate--Boon Edam(Local Supply)
53 | Cables & Conduits | Cables - Amp / D-link / Finolex Conduit - Precision / VIP national / BEC
52 | VAV | Honeywell
54 | BMS | Honeywell Trend
55 | Chilled Water FCU | Edgetech / Carrier / Zeco
56 | Chilled Water pipes | Jindal / Tata
57 | Auto Sequential Panel | Aircon Controls / Thittanix
Note: Final Make Selection shall be Adrianse prerogative