## SUMMARY
Cuberoot Engineering Service Consultants LLP ISRO Layout, Bengaluru info@cuberootconsultants.com |  | Date: | 2026-01-27
|  | Project Name: | CLAY WORKS SENETE
|  | Client: | CLAY WORKS
|  | Architect: | STAPATHI
|  | Subject: | SUMMARY OF FIRE WORKS
PART | DESCRIPTION | SUPPLY AMOUNT | INSTALLATION AMOUNT
A | FIRE ALARM SYSTEM
B | PUBLIC ADDRESS SYSTEM
C | FIRE PROTECTION SYSTEM
D | SIGNAGE
E | EXTINGUSHERS
| TOTAL | 0 | 0
| TOTAL AMOUNT | 0

## FA
SL.NO | DESCRIPTION | UNIT | 6th Floor | TOTAL | Drawing Qty Estimation | Jamal WO | INSTALLATION RATE | SUPPLY AMOUNT | DT REPLY | INSTALLATION AMOUNT
C | FIRE ALARM SYSTEM
1 | Supply, Installation, testing & commissioning of microprocessor based Analogue Addressable peer to peer networkable, Fire Alarm Control panel with with power supply & battery backup complete as per following feature. The number of Fire alarm panels and loop cards shall be designed as per OEM configuration.
| 4 loop panel (Considering 5&6 floor looping) | Nos | 1 | 1 | 1
1a | Each loop shall be loaded with 80% devices of manufacturer specified capacity. The control panel shall be capable of expansion up to 10 SLC modules. The system shall be capable of annunciation . Looping shall be continuos with other floors. Each loop shall be with 20% spare capacity.
1b | Battery back up for 48 Hrs during normal operation and 30 minutes alarm operation, with minimum 640 or higher Character LCD display/ 8" resistive touch screen display. Necessary interface card to connect a repeater panel and all hardware & software as per specification. Battery bank should be with enclosure.
1c | The panel shall be EN standrard. The panel shall preferably be programmable without any authorisation dongle and laptop as well as software. In case the dongle/software is required, the same shall be handed over to client and shall also be available with minimum two independent service providers. The panel shall have a supervised in-built memory storage to store site-related back-up files.
1d | Supply and installation of software for programming( mapping) the Fire detection and voice alarm system thorugh FACP / Lap top. The software shall consisting with facility like Upload / down load of informations to FACP, Graphics compatible to autocad, Detectors information with change in address / sensitivity etc as required.
2 | Supply, Installation, testing & comissioning of Bacnet IP card for BMS integration. The number of BACnet IP cards shall be as per the number of Fire alarm panels | Nos | 1 | 1
0
3 | Supply, Installation, testing & comissioning of PC based Graphics User Interface for Monitoring & Control of complete Fire system. The GUI based main network software shall network with FA panels on True Peer-to-Peer network. It shall be capable of graphically representing each facility being monitored with floor plans and icons depicting the actual locations of the various systems.. It shall have the facility to change the sensitivity of any detector. The software shall be capable of monitoring 200 Nodes with 100 MB baud Transmission rate on Fibre Optics Network and 12 MB baud Transmission on cable and 2,50,000 network , GUI shall be capable of monitoring & controlling and mapping the unlimited fire points. The Graphic User Interface Station shall provide Annunciation, Status display, Monitoring & Control of each and every element connected to Fire Alarm System and Networks. Graphic User Interface (Client) shall be connected to the server PC via TCP/IP or, if necessary, Wireless connectivity. The workstation shall provide full functionality of the server in terms of monitoring and control. However it shall have a provision of customized configuration where filtering of events shall be possible. It shall have provision for the configuration multiple password-protected operators with varying customized authority levels. The Graphic workstation shall act as an independent node communicating on the peer to peer network and shall not be dependant on the Fire Panel CPU for operation. Failure of Fire Panel CPU shall not result in failure of GUI. | Lot | 1 | 1
0
4 | PC for GUI software with compatible Ink Jet Printer for recording of the events. Intel i8 3 Ghz processor, 16 GB RAM, NVIDIA Graphics card with 2GB, 1TB HDD, 32" Color flat panel LED Monitor 1080P HD Resolution, 100/1000Mbps network card with original Microsoft Windows 8 Operating System, antivirus softwares,MS softwares. or Vendor can quote as per the OEM recommendation | Nos | 1 | 1
0
5 | Supply, Installation, testing & comissioning of Active Repeater Panel with display for monitoring & controlling the FACP on the network loop with Power supply. Peer To Peer Networked with main panel, such that the status of the entire system shall be available on individual repeater panels. | Nos | 1 | 1 | 0
0
6 | Supply, Installation, testing & comissioning of Passive Repeater Panel with display for monitoring the FACP on the network loop with Power supply. Peer To Peer Networked with main panel, such that the status of the entire system shall be available on individual repeater panels. | Nos | RO | 0
0
7 | Analogue Addressable Photo electric smoke detector with programmable for timed automatic sensitivity selection with base, Junction box and other accessories as required and detectors shall be EN standards, |  |  | 0
a | Above False ceiling | Nos | 121 | 121 | 125
b | Below False ceiling | Nos | 198 | 198 | 194
0
8 | Supply Installation Testing & Commissioning of multi sensor detector (photo+heat) having multiple selectable sensitivity levels with base,powder coated back box RED and other accessories as required and Detectors shall be EN standard | Nos | 4 | 4 | 6
0
9 | Supply Installation Testing & Commissioning of Analogue Addressable Duct sensor detector with multiple sensitivity levels, programmable for timed automatic sensitivity selection and with base, Detectors shall be EN standard. (One Duct sensor for each AHU) | Nos | 2 | 2 | 2
0
10 | Supply Installation Testing & Commissioning of Response indicator | Nos | 121 | 121 | 125
0
11 | Supply Installation Testing & Commissioning of Analogue Addressable Fault isolator module capable of monitoring shorted loop circuit and automatically restore communications when shorted conditions are corrected. (FIM's are used for every 20 detectors/devices). MS powder coated backbox and other accessories as required | Nos | 18 | 18 | 12
0
12 | Supply Installation Testing & Commissioning of Analogue Addressable Monitor module operating at 24V DC, 2A, rated at 230V, provided with DPDT contact. MS powder coated backbox and other accessories as required BASE BUILDER FA INTEGRATION PA INTEGRATION | Nos | 2 | 2 | 5
0
13 | Supply Installation Testing & Commissioning of Analogue Addressable Control module operating at 24V DC, 2A, rated at 230V, provided with DPDT contact.MS powder coated backbox and other accessories as required BASE BUILDER INTEGRATION PA INTEGRATION | Nos | 2 | 2 | 4
0
14 | Analogue Addressable Control relay module operating at 24V DC, 2A, rated at 230V, provided with DPDT contact. MS powder coated backbox and other accessories as required ACS TRIP AHU | Nos | 2 | 2 | 0
0
15 | Supply Installation Testing & Commissioning of Addressable Electronic Hooter cum Strobe ceiling mounted. The hooters shall be made of ABS plastic, and have a DB level of 65dbA and a multi tone facility. Addressable Control Module shall be fitted in a junction box . Rate shall inclusive of MS powder coated backbox and other accessories as required | Nos | 10 | 10 | 10
0
16 | Supply Installation Testing & Commissioning of Addressable Manual call point having an integrally mounted addressable module that monitors and reports contact status. (PULL TYPE). MCP shall be covered with acrylic box Rate shall inclusive of metal backbox including necessary civil works | Nos | 4 | 4 | 4
0
17 | 2C x 1.5 mm2, Stranded Copper conductor,Type A ST1 PVC insulated, RED COLOR, Armoured FRLS Cu Cable 1100 V as per IS 1554, with GI saddle spacers every 0.3 mtr with Single compression Cable Glands (metal), ABS Junction Boxes (wherever required), terminals,Ferruling, Cable dressing with cable tie, complete. The colour of the cable shall be red. | Rmt | 3924 | 3924 | 3241 | 2746.8
0
18 | Supply and laying of approved make FRLS PVC conduits (2mm thick) on ceiling / wall / floor etc. complete with accessories like, Junction boxes, Collars, Bends, clamps, saddles etc. (for MCP) | Rmt | 250 | 250
0
19 | Removing of exisiting Detectors from the existing location and refixing the same on the proposed/same location including Modification & alignment in existing cable based on site condition (this item can be used if existing detectors placed exactly on the partition/wall/above the HVAC ducts).Necessary costing for removing,, refixing to be included in quote. (vendor is responsible for safe handling of detectors, if any damage occurs during removing , same shall be procured by vendor and install without extra cost) | Lot | 1 | 1
TOTAL FOR PART - C

## PA
SL.NO | DESCRIPTION | UNIT | 6th Floor | TOTAL | Drawing estimation qty | SUPPLY RATE | INSTALLATION RATE | SUPPLY AMOUNT | INSTALLATION AMOUNT
D | PUBLIC ADDRESS SYSTEM
1 | Supply, Installation, testing & comissioning of 6W RMS True Ceiling Mount Speakers with inbuilt 100V Line Matching Transformer, wide opening angle, optimized for music & speech applications with 2mm thick powder coated back box, supports as per specifications. Colour of back box is as per architect approval. - Max Power: 8W,Rated Power: 6Watts, Power Tapping: 6/3/1.5W - Effective frequency range : 125 Hz to 16KHz - SPL at rated power (1Khz at 1 m) minimum 95 dB | Nos | RO | 0 | 43
2 | Supply, Installation, testing & comissioning of 6W RMS False Ceiling Mount Speakers with inbuilt 100V Line Matching Transformer, wide opening angle, optimized for music & speech applications with mounting clamps as per specifications - Max Power: 8W,Rated Power: 6Watts, Power Tapping: 6/3/1.5W - Effective frequency range : 125 Hz to 16KHz - SPL at rated power (1Khz at 1 m) minimum 95 dB | Nos | 151 | 151 | 107 |  |  |  |  | Make : Bosch considered
3 | Supply, Installation, testing & comissioning of 6W Wall Mounted Speakers with inbuilt 100V line matching transformers as specified as per specifications. The speakers shall be provided with powder coated back box, supports as per specifications. Colour of back box is as per architect approval. - Max Power: 8W,Rated Power: 6Watts, Power Tapping: 6/3/1.5 W - Effective frequency range : 125 Hz to 16KHz - SPL at rated power (1Khz at 1 m) minimum 95 dB | Nos | 4 | 4 | 4
0
4 | Supply of 6 Zone Digital Voice Evacuation Master controller with built in Amplifier. The System shall meet the standards of BS EN54 - 32 & EN 60849. The System Shall have Built in 500W Class-D Amplifier and it should be capable for the EVAC, Paging, PA and BGM functions. The Controller shall have SD card option to store the EVAC and Alert Voice Message. The Controller shall have Speaker line supervision record out and amplifier auto changeover. The Controller shall have following features: Separate Zone volume control at the front side of panel, Status indications on the Panel for EVAC,Fault ,AC,DC ,Fault, ALERT & Fireman mic, Zone capacity of 120 zones by cascaded 19 unit’s routers. With 6 programmable control inputs and 6 programmable control outputs for voice evacuation system, 8 programmable Control Input and output, Fireman Microphone with High Priority, THD<1%, Frequency response 80Hz - 20kHz, Up to 1000 Record files, 100V Class-AB Speaker Output. | No | 1 | 1
0
5 | Supply of Digital Voice Evacuation remote paging microphone with support 12 zones and 12 groups programable control. Support the redundant cable wiring, system capacity of 32 units and communication distance up to 600 meters, the paging microphone will be real time monitored by the system The Microphone shall have Reset/Cancel, All Call & Call Buttons. CAT6 Cable Communication up to 600 meter and DIP Switches to set up ID and Priorities. | Nos | 1 | 1
0
6 | Supply of Professional grade 480W mixer power Amplifier with following features:- 70V/100V 4–16-ohm speaker outputs, Isolated transformer for human safety, Plug & play U disk, FM radio, wireless remote control with three microphone inputs. Two auxiliary inputs, and one auxiliary outputs for link, Protection of overheat, overload, clip & short circuit, Frequency Response 50Hz ~ 16KHz ( + 1dB, - 3dB), S/N ratio>80dB, THD<0.1%, Power Supply 230V AC. | Nos | 3 | 3 | 3 |  |  |  |  | Quoted for Normal Amplifier
0
7 | Supply of Professional grade 240W mixer power Amplifier with following features:- 70V/100V 4–16-ohm speaker outputs, Isolated transformer for human safety, Plug & play U disk, FM radio, wireless remote control with three microphone inputs. Two auxiliary inputs, and one auxiliary outputs for link, Protection of overheat, overload, clip & short circuit, Frequency Response 50Hz ~ 16KHz ( + 1dB, - 3dB), S/N ratio>80dB, THD<0.1%, Power Supply 230V AC. | Nos | 1 | 1 | [5 empty] | Quoted for Normal Amplifier
0
8 | 2C x 1.5 mm2 (TWISTED PAIR) , Stranded Copper twisted pair conductor,Type A ST1 PVC insulated, Armoured FRLS Cable 1100 V as per IS 1554, with GI saddle spacers every 0.3 mtr with Single compression Cable Glands (for true ceiling mount speakers) ,ABS Junction Boxes (wherever required), terminals,Ferruling, cable dressing with cable tie, complete. The colour of the cable shall be Blue | Nos | 1510 | 1510 | 1660.75 | 1057
0
9 | Supply, Installation, testing & comissioning of Volume controller (Where ever required) | Nos | 1 | 1
0
10 | Supply, installation, testing & commissioning of Suitable size rack as per following specification, Conforms to DIN 41494 Or Equivalent EIA/ISO/EN/CEA Standard Finish - Powder coated finish with Seven tank pretreatment process meeting ASTM standard. shall be of mild steel with suitable anticorrosion protective coating Color - Black/off white/grey Fan module on top of the rack Welded frame with vented top cover with fan , perforated Metal Door with lock & Key and Back vented / Perforated metal door with lock & key and partially vented side panels, free standing on floor with 4 No. casters wheels with 2 no with brakes & 2 No. without brakes, cable oraginesers, Levelers with required 16A/5A power strips including accessories.The racks shall have lockable steel doors having proper ventilation slots for heat dissipation. Cable entry parts should be provided at the bottom. Number of racks shall be as per the design requirement. vendor to consider required number of racks as per their requirement 80% Loading of the rack to be considered. | Nos | 1 | 1 | 1
TOTAL FOR PART - D

## FPS
SL.NO | DESCRIPTION | UNIT | 6th Floor | TOTAL | Hemanth WO Qty | INSTALLATION RATE | SUPPLY AMOUNT | INSTALLATION AMOUNT
E | FIRE PROTECTION SYSTEM
1 | Supply, Installation, Testing & Commissioning of MS Pipes (BLACK), C class, ERW, Heavy grade conforming to IS: 1239 for pipes from 25 mm to 150mm dia. complete with fittings, supports, miscellaneous and consumables and Painting, with threaded fittings up to 50mm dia and grooved fittings from 65mm dia & above. All the branching should be done with proper T fitting. No gas cutting allowed. Pipe to be painted with Zinc chromate primer over that 2 coats red enamel paint as per Fire authorities requirement over all pipes (PO RED) and also inclusive of making hole in the wall, chasing, chipping, making good with plastering after completion of work, pipe sleeve of suitable higher size, sealing the sleeves with glass wool in between & fire sealant, etc. Cost of Steel supports for piping (like angles, channels, clamps, tie rods, brackets, nuts and bolts as per the standard shall also be included in the quoted rate. All pipes should be supported by factory galvanised MS angle(black) (Size 50x50x6mm) sections only, Welding of galvanised clamps and supports shall not be permitted VOC level shall be less than 250 g/ltrs and for rubber lining 850g/ltrs. Rate shall inclusive of Testing of Sprinkler line with 1.5 times pressure for 24 hrs and providing necessary hydraulic calculations
a | 25mm nominal dia | Rmt | 395 | 395 | 296.25
b | 32mm nominal dia | Rmt | 25 | 25 | 18.75
c | 40mm nominal dia | Rmt | 122 | 122 | 91.5
a | 50mm nominal dia | Rmt | 73 | 73 | 54.75
a | 65mm nominal dia | Rmt | 81 | 81 | 60.75
a | 80mm nominal dia | Rmt | 37 | 37 | 27.75
a | 100mm nominal dia | Rmt | 89 | 89 | 66.75
d | 150mm nominal dia | Rmt | 34 | 34 | 25.5
2 | Supply testing and commissioning of 15 mm chrome finish quartzoid bulb, Standard response sprinkler heads suitable for 68 deg. C, K 80
a | Pendent - 68deg C | Nos | 251 | 251 | 188.25
b | Upright - 68deg C | Nos | 251 | 251 | 188.25
c | Sidewall - 68deg C | Nos | RO
3 | Supply & fixing of approved type rosette plates ( Recessed type, in two piece) for Sprinklers below false ceiling area. The Rosette shall be fabricated by M.S. plate of 2mm thick and the finish shall be powder coated and color shall be as approved by architects / clients. | Nos | 251 | 251 | 188.25
4 | Stainless steel corrugated flexible pipe(hose) for dropping sprinklers below false ceiling, pipe shall be UL Listed, 12 bar pressure rating and 1800 mm long 25 mm dia with union / reducer collar, clamps etc. as required. (BRAIDED) - To be connected to existing sprinkler network with required fittings/accessories | No | 251 | 251 | 188.25
5 | Cutting , removing, rerouting of existing fire fighting pipes, sizes from 25 to 150mm dia from various places or reroute the existing pipes as per the site requirement. (in the areas such as UPS & server room, Electrical room). Quoted rate shall include painting of exisitng pipes wherever modification done, sizes from 25 to 150mm dia from various places. Vendor to check the drawing, Visit the site, analyse the quantum of works involved & quote accordingly.
a | 25mm nominal dia | Rmt | 60 | 60 | 45
b | 32mm nominal dia | Rmt | 10 | 10 | 7.5
c | 40mm nominal dia | Rmt | 25 | 25 | 18.75
a | 50mm nominal dia | Rmt | 10 | 10 | 7.5
a | 65mm nominal dia | Rmt | 10 | 10 | 7.5
6 | Providing dummy in the builder sprinkler | Nos | 5 | 5
7 | Removing of exiting sprinkler | Nos | 20 | 20
8 | Painting of exisitng pipes fire fighting pipes wherever modification done, sizes from 25 to 150mm dia from various places. | Lot | 1 | 1
TOTAL FOR PART - E

## Extingusher
SL.NO | DESCRIPTION | UNIT | 6th Floor | TOTAL | SUPPLY RATE | INSTALLATION RATE | SUPPLY AMOUNT | INSTALLATION AMOUNT
G | EXTINGUSHERS
1 | CO2 type Fire Extinguisher ISI marked confirming to IS:15683 latest. Capacity 4.5 Kg. Complete with delivery hose horn, squeeze grip release valve, locking arrangement,operating temperature -30°C to +55°C, supplied with body bearing IS 7285 mark and approved by CCoE tested at 250 kgf/cm2., fitted with ISI marked & CCoE approved valve as per IS 3224. CO2 Gas as per IS: 15222. externally painted with PO Red Shade No. 538 of IS 5, operation manual and floor stand or Wall Mount Bracket including accessories as required as per site condition. The stand shall be of M.S, with tripod stand to accommodate the extinguisher. (Server rooms & Electrical rooms, UPS room) | Nos | 3 | 3
2 | Powder Fire Extinguisher (Stored Pressure type) (Powder pressurized with dry nitrogen gas at 15 bar.) capacity: 6kg duly ISI marked conforming to IS: 15683:2006/latest, with IS 14609 ISI marked ABC powder complete with squeeze grip release valve, discharge pipe, locking arrangement, pressure gauge, operation manual,Body Hydrotested at 35 bar, Operating temperature -30°C to +55°C, external epoxy powder coating with PO Red Shade No. 538 of IS 5, and floor stand. or Wall Mount Bracket including accessories as required as per site condition. The stand shall be of M.S, with tripod stand to accommodate the extinguisher. (corridor areas, AHU room) | Nos | 20 | 20
3 | Clean Agent (Stored Pressure) Type Fire Extinguisher Complete with squeeze grip release valve, locking arrangement, pressure gauge, operation manual, bracket with two screw and sleeve filled with HFC- 236 FA . Complete in all respect, Capacity 4 Kg. with Floor mounting stand or Wall Mount Bracket as per site conditions. The stand shall be of M.S, with tripod stand to accommodate the extinguisher. | Nos | 3 | 3
4 | Wet chemical stored pressure 6Ltr capacity including accessories, pressure guage and floor mounting stand. The stand shall be of M.S, with tripod stand to accommodate the extinguisher. (kitchen - preparation area) | Nos | RO | 0
TOTAL FOR PART - G

## Signage
SL.NO | DESCRIPTION | UNIT | 6th Floor | TOTAL | SUPPLY RATE | INSTALLATION RATE | SUPPLY AMOUNT | INSTALLATION AMOUNT
F | SIGNAGE
1 | Supply Installation Testing & Commissioning of FIRE SIGNAGES and LED Configured Emergency Exit SIGNAGE system 1. Recessed/Surface/Suspendend Mounting Type (based on mockup approval) 2. LED light with Rechargeable battery backup of 180 minutes 3. Continously provides illumination through mains power supply 4. Suitable for different types of exit Facia 5. As per IS 9583-1981 6.Photoluminescent & maintained type 7.Suitable for 230v, 50Hz 8. Sample to be submitted before procurement
a | "FIRE EXIT " (BATTERY BACKED SIGNAGE) - SINGLE SIDE - 150*400mm - FOR FIRE EXIT STAIRCASE | Nos | 2 | 2
b | "DIRECTIONAL EMERGENCY EXIT " (AUTOGLOW - "Opaque" PVC foam board of computerised cut, PVC non-reflective self adhesive vinyl painted foam board ) - with suspension chains . DOUBLE SIDE - 150*300mm The signages shall be fixed to the ceiling with the help of chain and dropped below false ceiling. | Nos | 2 | 2
c | "DIRECTIONAL EMERGENCY EXIT " (AUTOGLOW - "Opaque" PVC foam board of computerised cut, PVC non-reflective self adhesive vinyl painted foam board ) - with suspension chains . SINGLE SIDE - 150*300mm The signages shall be fixed to the ceiling with the help of chain and dropped below false ceiling. | Nos | 2 | 2
d | " EXTINGUISHER Signages - (AUTOGLOW - "Opaque" PVC foam board of computerised cut, PVC non-reflective self adhesive vinyl painted foam board) with suspension chains (Autoglo signages, size 150 x 300) - double side | Nos | 23 | 23
d | " MCP Signages - (AUTOGLOW - "Opaque" PVC foam board of computerised cut, PVC non-reflective self adhesive vinyl painted foam board) with suspension chains (Autoglo signages, size 150 x 300) - double side | Nos | 2 | 2
d | Fire Evacuation Route Map as per following specification Evacuation plan shall be glow in dark. A2 size with 5mm thick rear & 3mm thick front acrylic cover including wall mount supports. samples to be shown before execution | Nos | RO | 0
TOTAL FOR PART - F