## ELEC Make List
LIST OF MAKES for ELECTRICAL & LV SYSTEM
(All materials shall be ISI mark)
S.No. | Details of Materials | Make/Manufacturers Name
1 | M.S. Conduits and accessories | BEC
2 | Conduit accessories | BEC
3 | FRLS P.V.C. conduits and accessories | BEC/ESC Plast/Anchor
4 | FRLS P.V.C. insulated copper conductor wires 1100 volts grade | Bonton/Finolex/Havells/Anchor
5 | MCCB,s and Accessories | Schneider/Indoasian-Optium/Anchor/Eaton
6 | Miniature circuit breakers/ DB | Schneider/Indoasian-Optipro/Wipro/Anchor
7 | Auto Transfer Switch | Socomec/Schneider
8 | Switches, sockets | Honeywell Citric/ Wipro-Northwest/Indoasian-Shynora/Anchor (Roma Plus)
9 | Gang Box | Make same as make of switch & sockets
10 | G.I. Pipe | Tata/Jindal
11 | PVC insulated Aluminium/copper conduc-Tor armoured cables of 1100 V / Volt grade | Bonton/Finolex/Havells
12 | PVC insulated flexible copper conduc- tor cables of 1100 V grade | Bonton/Finolex/Havells
13 | Cable Glands | OBO
14 | Cable Lugs | HEX
15 | LED Light fixtures | Philips/Divinity/RIPPL/Legero/Havells/Panasonic
16 | GLS Lamps/CFL Lamps/ Tube Lights | Philips (LED Light Fixture)/Legero/Havells
17 | Decorative light fixtures | Divinity/RIPPL/TISVA/Legero/Havells
18 | Day light/Occupancy Sensor | Philip/Zen Control
19 | Indicating Lamps | Schneider/Siemens
20 | Terminal Blocks | Elmex
21 | Energy meter | Schneider / Socomec/Siemens
22 | Industrial socket outlet,socket and top/Junction Box | Indoasian/PotenzaGrip
23 | Earth Leakage Circuit Breaker | Schneider/Indoasian-Optipro
24 | Maintenance Free Earthing | OBO/ABB/ERICO
25 | Cable Tray | AAA/BEC/ Global Electrical & Controls/OBO
26 | Raceway – with sheet steel | AAA/BEC/ Global Electrical & Controls/OBO
27 | Floor Access Box | Fraser Techno/Burland/Schulte-Evoline
28 | SDB’s and Panels | AAA/Nextgen/Global Electrical & Controls/ Advance
29 | Wire Mesh Tray | Schneider/Siemens/OBO
31 | Panel Suppression System | Fyrex/Ceasfire/Minimax
32 | Lighting Management System | Zen Control/Lutron
33 | UPS System | Eaton/Vertiv/Schneider/Socomec/Fuji Electric
34 | Exit Signages | Eaton/Ekavis/Ayzo
35 | Disable System | Eaton/Ekavis/Ayzo
36 | Any other Item Sample to be approved by PMC/MEP Consultant

## MEP SUMMARY
|  | AMOUNT | [6 empty] | MEP MARKUP- | 0%
SR.NO | SUMMARY | B1 | B2 | B3 | B6 | CONTROL | LAB | TOTAL
1 | TOTAL ELECTRICAL WORK | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | LIGHT FIXTURES WORK | 0 | 0 | 0 |  | 0 | 0 | 0
4 | HVAC WORK | 0 | 0 | 0 | 0 | 0 | 0 | 0
0
| TOTAL | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exclusion
IT System
AV System
Low Voltage is not in scope

## Elect B1
Sl.No. | Description | Unit |  | Supply & Installation
|  |  | Qty | Rate In Rs. | Amount in Rs.
A. | POINT WIRING
All wires shall be FRLS PVC insulated copper conductor. Point wiring rates are inclusive of 3 x 1.5 sq mm insulated copper conductor wires for circuit.(from DB to switch board).
All sockets to be checked with a Check Plug socket tester for live-neutral reverse, no earth,neutral fault, live earth reverse, neutral earth reverse.
The Circuit No. and DB no. label shall be provided on all UPS ,RAW sockets and switchboards with label printer.
Colour coding for conduits to be done for different systems. The whole length of conduits to be painted.
All circuit & point wiring shall be colour coded & shall have ferruling on both end for circuit identification complete as required etc.Labelling on all the switches and sockets to be done with respect to DB reference, phase and circuit no.
Earth loop Impedance Test to be performed. RCD test to be done. Cable Insulation Tests to be done.
Wherever the occupancy sensor is provided in the cabin/ meeting rooms/workstations , the circuit wires from Distribution Board to occupancy sensor and sensor to switch are inclusive in the point wiring rate.
Labeling of all sockets and emergency lights to be provided and Ferruling for all the circuits to be considered
1 | Wiring for the following light points with 3x1.5 Sq.mm FRLS PVC insulated stranded copper conductor wires in concealed M.S. conduits in F.ceiling/walls/ceiling as directed including providing and fixing of 6 amps flush type switches, 5 sided G.I Boxes for housing switc­hes and earth­ing complete as required. Rates are inclusive of 3 x 1.5 sq mm FRLS PVC insulated stranded copper conductor wires for circuit
a. | First point controlled by one no. 6 amp switch. | Nos. | 15 |  | 0
0
2 | Same as item No. 1a above but LOOP POINT i.e. wiring of point looped from first point with 3 x 1.5 sq. mm FRLS PVC insulated copper conductor wire in concealed/exposed MS conduit and earthing | Nos. | 23 |  | 0
0
3 | Wiring for the following light points with 1.5 Sq.mm FRLS PVC insulated stranded copper conductor wires in concealed M.S. conduits in F.ceiling/walls/ceiling as direc­ted including providing and fixing of 6 amps flush type switches, 5 sided G.I Boxes for housing switc­hes and earth­ing comple­te as required. Rates are inclusive of 3 x 1.5 sq mm FRLS PVC insulated stranded copper conductor wires for circuit |  |  |  | 0
0
a. | First point controlled by one no. 16 amp switch. | Nos. | 0 |  | 0
0
4 | Wiring for the following light points controlled by MCB in DB (Cost of MCB has been taken elsewhere in the tender) with 3 x 1.5 sq. mm FRLS PVC insulated copper conductor wires in concealed/exposed M.S. conduits as called for and earthing. |  |  |  | 0
0
a. | First point controlled by existing MCB in D.B. To first light Em Light | Nos. | 1 |  | 0
0
5 | Same as item No. 4.a above but LOOP POINT i.e. wiring of point looped from first point with 3x1.5 sq. mm FRLS PVC. insulated copper conductor wire in concealed/exposed M.S. conduit and earthing | Nos. | 6 |  | 0
0
6 | SITC of 2C x 1.5 sq mm non shielded Cable for DALI Ballast wiring in 25 mm dia MS conduit with all fixing accessories complete as required | Rmt. | 0 |  | 0
0
7 | SITC of 4C x 1.5 sq mm shielded Cable for QSM wiring in suitable size of MS conduit with all fixing accessories complete as required. Cable Common – 12 AWG (4.0 mm2); Power – 12 AWG (4.0 mm2); MUX Data – 22 AWG (0.25 mm2); Data – 22 AWG (0.25 mm2); Sense Line – 18 AWG (0.75 mm2); Drain Wire – 24 AWG (0.2 mm2) | Rmt. | 0 |  | 0
0
8 | Wiring for 6/16 amps outlets with 3 X 2.5 sq.mm FRLS PVC insulated copper conductor wires in M.S. Conduits in ceiling/walls/floor as direc­ted incl­u­ding providing & fixing of 6/16 amps flush type 5 pin socket and 16 amps switch with cover plate, 5 sided G.I boxes for housing switches, sockets and earthi­ng complete as required. (for general areas 4 nos loop in one circuits) | Nos. | 6 |  | 0
0
9 | Wiring for inline fan points with 2 x 2.5 sq.mm FRLS PVC insulated stranded copper con­ductor wires in concealed M.S. conduits in F.ceiling/ walls/ Ceiling as directed including providing and fixing of 16 amps flush type switches 16 amps 3 pin socket near inline fan, 5 sided G.I. boxes for housing switches and 16 amps 3 pin socket outlet and earthing and complete as required.(including body earth for GI boxes) | Nos. | 2 |  | 0
0
10 | Wiring for Geyser/Projector/Hand Dryer points with 2 x 4 + 1 x 4 sq mm FRLS PVC insulated copper conductor wires in concealed M.S. conduits in F.ceiling/ walls/ Ceiling as directed including providing & fixing 16 amps flush type switch near the white board and 6/16 amps 6 pin socket near the projector in ceiling , 5 sided G.I. boxes for housing switches and 6/16 A 6 pin socket outlet , earthing and complete as required.(including body earth for GI boxes) ( 1 point per circuit) | Nos. | 2 |  | 0
0
11 | Wiring for VRV Indoor units with 3 x 2.5 sq.mm FRLS PVC insulated stranded copper conductor wires in concealed M.S. conduits in F.ceiling/ walls/ Ceiling as directed including providing providing and fixing of 6 amps flush type switches 16 amps 3 pin socket near VRV points, 5 sided G.I. boxes for housing switches and 16 amps 3 pin socket outlet and earthing and complete as required.(including body earth for GI boxes) (1 point per circuit) | Nos. | 5 |  | 0
0
12 | Wiring for VAV /fire damper points with 3 x 2.5 sq.mm FRLS PVC insulated copper conductor wires in concealed M.S. conduits in F.ceiling/ walls/ Ceiling as directed including providing & fixing 6 amps flush type switches, 6 amps 3 pin socket near VAV points, 5 sided G.I. boxes for housing switches and 6 A sockets earthing and complete as required. The sockets to be fused spur type (MK make). (including body earth for GI boxes) (8 to 10 points per circuits) | Nos. | 0 |  | 0
0
13 | Wiring for 16 amps power outlet poi­nts with 4 sq.mm FRLS PVC insulated stranded copper conductor wires in concealed/recessed M.S. conduit as directed including providing providing and fixing of 16 amps flush type switch and 6 pin socket with cover plate 5 sided G.I. outlet boxes for switches and socket and earthing the third pin with 2.5 sq mm FRLS PVC stranded copper wire complete as required (Only one outlet shall be connected on each circuit) (including body earth for GI boxes) | Nos. | 5 |  | 0
0
14 | Wiring for 16 amps power outlet points with 4 sq.mm FRLS PVC insulated stranded copper conductor wires for the first power outlet and 4 sq.mm FRLS PVC insu­lated stranded copper conductor wires for the second outlet, in concealed M.S. cond­uits in F.ceiling/ walls/Ceiling/floor ducts as directed including providing providing and fixing of 16 amps flush type switch and 6 pin socket with cover plate, 5 sided G.I. outlet boxes for housing switches and socket, and earthing the third pin with 2.5 sq.mm FRLS PVC insulated copper conductor wires complete as required (Two power out­lets shall be connected on each circuit)(including body earth for GI boxes) | Set of Two | 1 |  | 0
0
15 | Wiring for A/C outlet points with 4.0 sq mm FRLS PVC insulated stranded copper conductor wires in M.S. conduitl/wall/floor ducts as directed including providing 25 A socket with 25 amps SP MCB ( Tiny Trip) 5 sided GI Outlet Box for housing and socket and MCB and earthing with 2.5 sq. mm FRLS PVC insulated stranded Copper Conductor wires complete as required. | Nos. | 0 |  | 0
0
| Different colours to be used for 3 core cables for raw power and UPS power. |  |  |  | 0
16 | Wiring for UPS/Raw plug outlets points with three core, 2.5 sqmm FRLS PVC Insulated and PVC sheathed flexible cable with bright annealed electrolytic copper conductor, 1100 volt grade confirming to IS : 694-1990 with latest amendments, in existing Channels/ conduit in ceiling/walls/floor including all cable termination accessories) (including body earth for GI boxes). Colour Coding to be followed | RM | 140 |  | 0
0
17 | Wiring for UPS/Raw plug outlets points with three core, 4.0 sqmm FRLS PVC Insulated and PVC sheathed flexible cable with bright annealed electrolytic copper conductor , 1100 volt grade confirming to IS : 694-1990 with latest amendments, in existing Channels/ conduit in ceiling/walls/floor inclu­ding all cable termination accessories) Earthing of GI Box to be included. Colour Coding to be followed. | RM | 45 |  | 0
0
18 | Wiring for Power plug outlets points with three core, 6.0 sqmm FRLS PVC Insulated and PVC sheathed flexible cable with bright annealed electrolytic copper conductor , 1100 volt grade confirming to IS : 694-1990 with latest amendments, in existing Channels/ conduit in ceiling/walls/floor inclu­ding all cable termination accessories). Colour Coding to be followed. | RM | 0 |  | 0
0
19 | Wiring for Power plug outlets points with three core, 10.0 sqmm FRLS PVC Insulated and PVC sheathed flexible cable with bright annealed electrolytic copper conductor , 1100 volt grade confirming to IS : 694-1990 with latest amendments, in existing Channels/ conduit in ceiling/walls/floor inclu­ding all cable termination accessories). Colour Coding to be followed. | RM | 25 |  | 0
0
| The word UPS shall be printed on all UPS sockets. |  |  |  | 0
| The word RAW shall be printed on all RAW sockets. |  |  |  | 0
| The Circuit No. and DB no. label shall be provided on all UPS ,RAW sockets and switchboards with label printer. |  |  |  | 0
| Contractor is required to submit samples of all types of switches and sockets to Consultant and Architects representative for approval before ordering the material. |  |  |  | 0
0
20 | Providing and fixing of 1 Nos. 6 amp round pin type socket and 1 No. 6 amps switch cover plate, 5 sided G.I. Boxes for housing switches and sockets and earthing complete as required (for UPS/Raw). GI Box to have earth pin for body earthing | Nos. | 15 |  | 0
0
21 | Providing and fixing of 2 Nos. 6 amp round pin type socket and 1 No. 6 amps switch cover plate, 5 sided G.I. Boxes for housing switches and sockets and earthing complete as required (for UPS/Raw). GI Box to have earth pin for body earthing | Nos. | 14 |  | 0
0
22 | Providing and fixing of 3 Nos. 6 amp round pin type socket and 1 No. 6 amps switch cover plate, 5 sided G.I. Boxes for housing switches and sockets and earthing complete as required (for UPS/Raw). GI Box to have earth pin for body earthing | Nos. | 1 |  | 0
0
23 | Providing and fixing of 2 Nos. 6/16 amp round pin type socket and 1 No. 16 amps switch cover plate, 5 sided G.I. Boxes for housing switches and sockets and earthing complete as required (for UPS/Raw). GI Box to have earth pin for body earthing | Nos. | 0 |  | 0
0
24 | Providing and fixing of 1 No.16 amps flush type 6 pin socket and 1 No. 16 amps switch with indicator, cover plate, 5 sided G.I. Boxes for housing switches and sockets and earthing complete as required (for UPS / RAW) GI Boxes to have earth pin for body earthing | Nos. | 2 |  | 0
0
25 | Providing and fixing Underfloor Access Outlets (250 x 250 x 55 - mm 70 compartments 1Trap including providing 2 Nos 6 Amps Round Pin sockets and 1 no. 16 Amp Switch & 2 data outlet complete as required. | Nos. | 1 |  | 0
0
26 | Supply and fixing of the following sizes of thermoplastic moulded plug and socket IEC 309 type in PVC Box of suitable size flush / surface and making connections complete as required. The box shall be IP 44. |  |  |  | 0
a | 3 pin 16/20 A 1 phase industrial socket with mcb & plug top | Nos. | 0 |  | 0
b | 3 pin 32 A 1 phase industrial socket plug top | Nos. | 0 |  | 0
0
27 | Providing and fixing in position the following M.S. conduits including all accessories concealed in F. ceiling/wall/floor as required including 1.6 mm thick M.S. junction or pull boxes with 3mm thick perspex sheet cover plate compl­te with 1.6 mm dia. G.I. pull wires in the length of conduit. |  |  |  | 0
0
a. | 20 mm dia conduit ( 1.6 mm thick) | RM | 40 |  | 0
b. | 25 mm dia conduit (1.6 mm thick) | RM | 75 |  | 0
c. | 32 mm dia conduit (2.0 mm thick) | RM | 50 |  | 0
28 | The Electrical Contractor shall provide sufficient temporary lighting for working in the Building total area 1130 sq. ft. divided in single floor and maintain the same till completion of the project.It shall include replacement of all fused/faulty lamps.It shall include providing 15 A plug sockets (industrial type with ON/OFF switch/MCB) on 4 sides walls one plug at every 5-8 meter distance. The Contractors will tap off supply from these plugs for his use. Tubelights to maintain a lighting level of 150 lux on the floor,.Each 15 A socket and each Light circuit shall be protected by suitable MCBs.Use three core PVC Insulated PVC sheathed copper conductor cables for wiring.The contractor shall salvage the complete wiring and take it back at the end of the project. | L.S. | 1 |  | 0
0
| TOTAL CARRIED OVER TO SUMMARY |  |  |  | 0
0
B. | CONDUITING FOR TELEPHONE , COMPUTER & CONDUITING AND WIRING FOR T.V. SYSTEM. |  |  |  | 0
0
1 | Providing and fixing in position the following M.S. conduits including all accessories concealed in F. ceiling/wall/floor as required including 1.6 mm thick M.S. junction or pull boxes with 3mm thick perspex sheet cover plate compl­te with 1.6 mm dia. G.I. pull wires in the length of conduit. |  |  |  | 0
0
a. | 20 mm dia conduit( 1.6 mm wall thickness) | RM | 35 |  | 0
b. | 25 mm dia conduit ( 1.6 mm wall thickness) | RM | 70 |  | 0
c. | 32 mm dia conduit ( 1.6 mm wall thickness) | RM | 55 |  | 0
0
2 | Providing and fixing in position suitable 1.2 mm thick G.I./ PVC outlet box for RJ- 45 computer outlet with all fixing accessories as required. | Nos. | 5 |  | 0
0
3 | Supply and fixing of 1.2 mm thick G.I Box along with RG 11 TV Co axial socket with Cover Plate | Nos. | 1 |  | 0
0
4 | Supply drawing connecting testing and commissioning of TV Coaxial cable RG 6 in existing conduit | RM | 60 |  | 0
0
| TOTAL CARRIED OVER TO SUMMARY |  |  |  | 0
0
C. | EARTHING |  |  |  | 0
0
1 | Providing and fixing in position the following copper strips and wires including providing all fixing accessories and effecting proper connections |  |  |  | 0
| Note:- MS Cable markers at the earth bus, panel and DB entries to be provided |  |  |  | 0
a. | G.I. tape 25 mm x 6 mm | RM | 100 |  | 0
b. | Copper tape 25mm x 3 mm | RM | 0 |  | 0
c. | GI wire 8 SWG | RM | 60 |  | 0
d. | GI wire 12 SWG | RM | 0 |  | 0
e. | Supply installation , and making of Exothermic weld suitable to bond GI strip of 25x5 mm with Copper Strip of 25x5 mm with 75mm extensions on either side | Nos. | 0 |  | 0
f. | Copper Earth Link connectors - 200 mm long, 25mm wide and 5 mm thick | Nos. | 0 |  | 0
0
2 | Supply and laying, effecting proper connec­tions, testing & commissioning of the following sizes of 1.1 KV armoured XLPE/ unarmoured FRLS sheathed XLPE insulation, conforming to IS: 7098 (Part-1)- 1988 ( 90 deg C) aluminium /copper conductor cables conforming to IS : 1554 and FRLS Insulated flexible copper cables as per IS 694 laid over MS supports in existing RCC ducts/ laid in ground /laid on Cable Trays including clamping the cables to sup­ports in an approved manner as required complete with all accessories. |  |  |  | 0
0
a | 1c x 50 sq.mm FRLS insulated flexible copper conductor cables | RM | 0 |  | 0
0
b | 1c x 35 sq.mm FRLS insulated flexible copper conductor cables | RM | 0 |  | 0
0
c | 1c x 25 sq.mm FRLS insulated flexible copper conductor cables | RM | 0 |  | 0
0
d | 1c x 16 sq.mm FRLS insulated flexible copper conductor cables | RM | 0 |  | 0
0
e | 1c x 10 sq.mm FRLS insulated flexible copper conductor cables | RM | 60 |  | 0
0
f | 1c x 6 sq.mm FRLS insulated flexible copper conductor cables | RM | 35 |  | 0
0
g | 2 Nos 1 x 10 Sq. mm FRLS insulated flexible copper conductor cables (Green Colour for UPS DB Sub-main Earthing) | RM | 0 |  | 0
0
3 | Supplying and making of end termination for the following size of compression lugs and PG Threaded Nylon Flexible cable glands complete with all fixing accessories as required |  |  |  | 0
0
a | 1c x 50 sq.mm FRLS insulated flexible copper conductor cables | Sets | 0 |  | 0
0
b | 1c x 35 sq.mm FRLS insulated flexible copper conductor cables | Sets | 0 |  | 0
0
c | 1c x 25 sq.mm FRLS insulated flexible copper conductor cables | Sets | 0 |  | 0
0
d | 1c x 16 sq.mm FRLS insulated flexible copper conductor cables | Sets | 0 |  | 0
0
d | 1c x 10 sq.mm FRLS insulated flexible copper conductor cables | Sets | 4 |  | 0
0
4 | Providing earthing station at loca­tion as called for including provid­ing 600 mm x 600 mm x 3 mm thick tinned copper electrode 2 Nos 25 x 3 mm copper strip (for body earthing GI strip can be considerd) up to ground level 20mm dia medium class GI pipe (India Tube Company make or approved equal) CI funnel with 20 gauge GI wire mesh, masonry chamber with concrete base, CI man­hole cover (cover to be heavy duty) with frame (300mm x 300mm) and bitumastic paint and packing the fixture of charcoal and common salt around plate electrode complete as per I.S. ( Minimum depth shall be 4.2 M ) for UPS & Server | Nos. | 0 |  | 0
0
5 | Supply, Installation, testing and commissioning of Maintenance Free Earthing of make Electrolytic Earthing comprising of type 'K' copper 2.4 mm wall thickness, hollow tube 10 feet long, 2.125 inches outer diameter completely filled with non hazardous metallic salts (Terrafill) to achieve an earth resistance of less than 1 ohms. Provide masonry chamber with concrete base, CI man­hole cover (cover to be heavy duty) with frame (300mm x 300mm) and make earth pit sign/ identifcation no in each earth station for UPS & Server | Nos. | 1 |  | 0
0
6 | Supply, installation, testing and commissioning of sheet metal enclosed 450 x 200 x 150 (D) mm insulated earth distribution board with 1 nos. 50 x 6 mm copper tinned earth bars on SMC insulator suitable for 6/8 nos connections complete with all fixing accessories as required. | Nos. | 0 |  | 0
0
7 | Supply, installation, testing and commissioning of sheet metal enclosed 300 x 200 x 150 ( D) mm insulated earth distribution board with 1 nos. 32 x 6 mm copper tinned earth bars on SMC insulator suitable for 6/8 nos connections complete with all fixing accessories as required. | Nos. | 1 |  | 0
0
8 | Supplying and laying of the following sizes of Heavy duty PVC Pipes below paved area including chase cutting and back filling. |  |  |  | 0
a. | 100 mm outer dia | RM | 0 |  | 0
b. | 80 mm outer dia | RM | 10 |  | 0
0
| TOTAL CARRIED OVER TO SUMMARY |  |  |  | 0
0
D | CABLES, MAINS & SUBMAINS |  |  |  | 0
0
1 | Supply and laying, effecting proper connec­tions, testing & commissioning of the following sizes of 1.1 KV armoured XLPE/ unarmoured FRLS sheathed XLPE insulation, conforming to IS: 7098 (Part-1)- 1988 ( 90 deg C) aluminium /copper conductor cables conforming to IS : 1554 and FRLS Insulated flexible copper cables as per IS 694 laid over MS supports in existing RCC ducts/ laid in ground /laid on Cable Trays including clamping the cables to sup­ports in an approved manner as required complete with all accessories. |  |  |  | 0
0
| Note : All cables to be glanded and crimped with suitable sized lugs. All Cable trays to be double earthed. All raceways and cable glands to be earthed with brass round earth clips and wires. |  |  |  | 0
| Earthing ring to be included in all the cable glands. |  |  |  | 0
| Sub main cables should be labelled at both ends |  |  |  | 0
| Joints shall be allowed only at the 2 ends of the cables and not in between. |  |  |  | 0
0
a | 3.5 c x 300 sq.mm1.1 KV grade XLPE Insulated FRLS sheathed armoured aluminium conductor cable | RM | 0 |  | 0
0
b | 3.5 c x 240 sq.mm1.1 KV grade XLPE Insulated FRLS sheathed armoured aluminium conductor cable (Assumed) | RM | 0 |  | 0
0
c | 3.5 c x 185 sq.mm1.1 KV grade XLPE Insulated FRLS sheathed armoured aluminium conductor cable | RM | 0 |  | 0
0
d | 3.5 c x 150 sq.mm1.1 KV grade XLPE Insulated FRLS sheathed armoured aluminium conductor cable | RM | 0 |  | 0
0
e | 3.5 c x 120 sq.mm1.1 KV grade XLPE Insulated FRLS sheathed armoured aluminium conductor cable | RM | 0 |  | 0
0
f | 3.5 c x 95 sq.mm1.1 KV grade XLPE Insulated FRLS sheathed armoured aluminium conductor cable | RM | 0 |  | 0
0
g | 3.5 c x 70 sq.mm1.1 KV grade XLPE Insulated FRLS sheathed armoured aluminium conductor cable | RM | 0 |  | 0
0
h | 3.5 c x 50 sq.mm1.1 KV grade XLPE Insulated FRLS sheathed armoured aluminium conductor cable For SDB L&P (Assumed) | RM | 60 |  | 0 | 2
0
i | 4 c x 35 sq.mm1.1 KV grade XLPE Insulated FRLS sheathed armoured aluminium conductor cable | RM | 0 |  | 0
0
j | 4 c x 25 sq.mm1.1 KV grade XLPE Insulated FRLS sheathed armoured aluminium conductor cable For DB and VRV ODU | RM | 45 |  | 0 | 2
0
k | 4 c x 25 sq.mm1.1 KV grade XLPE Insulated FRLS sheathed armoured copper conductor cable | RM | 0 |  | 0
0
l | 4 c x 16 sq.mm1.1 KV grade XLPE Insulated FRLS sheathed armoured aluminium conductor cable | RM | 0 |  | 0
0
m | 4 c x 16 sq.mm 1.1 KV grade XLPE Insulated FRLS sheathed armoured copper conductor cable | RM | 0 |  | 0
0
n | 4 c x 10 sq.mm 1.1 KV grade XLPE Insulated FRLS sheathed armoured copper conductor cable For UPS DB | RM | 0 |  | 0
0
p | 4 c x 6 sq.mm 1.1 KV grade XLPE Insulated FRLS sheathed armoured copper conductor cable | RM | 0 |  | 0
0
q | 4 c x 4 sq.mm 1.1 KV grade XLPE Insulated FRLS sheathed armoured copper conductor cable | RM | 0 |  | 0
0
s | 4 c x 2.5 sq.mm 1.1 KV grade XLPE Insulated FRLS sheathed armoured copper conductor cable For CS AHU & Hydrogen Exhaust | RM | 0 |  | 0
0
t | 3 c x 10 sq.mm 1.1 KV grade PVC Insulated FRLS Armoured copper conductor cable | RM | 0 |  | 0
0
u | 3 c x 6 sq.mm 1.1 KV grade XLPE Insulated FRLS sheathed armoured copper conductor cable For VRV DB | RM | 15 |  | 0
0
x | 2 c x 10 sq.mm 1.1 KV grade XLPE Insulated FRLS sheathed armoured copper conductor cable For UPS | RM | 25 |  | 0 | 2
0
z | 1c x 6 sq.mm FRLS XLPE insulated flexible copper conductor cables | RM | 0 |  | 0
0
aa | 1c x 10 sq.mm FRLS XLPE insulated flexible copper conductor cables | RM | 0 |  | 0
0
ab | 1c x 16 sq.mm FRLS XLPE insulated flexible copper conductor cables | RM | 0 |  | 0
0
ac | 1c x 25 sq.mm FRLS XLPE insulated flexible copper conductor cables | RM | 0 |  | 0
0
ad | 1c x 35 sq.mm FRLS XLPE insulated flexible copper conductor cables | RM | 0 |  | 0
0
2 | Supplying and making terminal joints for the following size of 1.1 KV PVC insulated copper conductor armoured cables including providing heavy duty tinned copper terminal crimping lugs, solder, insulation tape, approved sealing epoxy compound, double compression brass cable glands, effecting gland connec­tions and effecting terminal connections to the equipment complete as required. Use compression lugs and PG Threaded Nylon Flexible cable glands for single core flexible cables |  |  |  | 0
0
a | 3.5 c x 300 sq.mm1.1 KV grade XLPE Insulated FRLS sheathed armoured aluminium conductor cable | Sets | 0 |  | 0
0
b | 3.5 c x 240 sq.mm1.1 KV grade XLPE Insulated FRLS sheathed armoured aluminium conductor cable | Sets | 0 |  | 0
0
c | 3.5 c x 185 sq.mm1.1 KV grade XLPE Insulated FRLS sheathed armoured aluminium conductor cable | Sets | 0 |  | 0
0
d | 3.5 c x 150 sq.mm1.1 KV grade XLPE Insulated FRLS sheathed armoured aluminium conductor cable | Sets | 0 |  | 0
0
e | 3.5 c x 120 sq.mm1.1 KV grade XLPE Insulated FRLS sheathed armoured aluminium conductor cable | Sets | 0 |  | 0
0
f | 3.5 c x 95 sq.mm1.1 KV grade XLPE Insulated FRLS sheathed armoured aluminium conductor cable | Sets | 0 |  | 0
0
g | 3.5 c x 70 sq.mm1.1 KV grade XLPE Insulated FRLS sheathed armoured aluminium conductor cable | Sets | 0 |  | 0
0
h | 3.5 c x 50 sq.mm1.1 KV grade XLPE Insulated FRLS sheathed armoured aluminium conductor cable | Sets | 2 |  | 0
0
i | 4 c x 35 sq.mm1.1 KV grade XLPE Insulated FRLS sheathed armoured aluminium conductor cable | Sets | 0 |  | 0
0
j | 4 c x 25 sq.mm1.1 KV grade XLPE Insulated FRLS sheathed armoured copper conductor cable | Sets | 6 |  | 0
0
k | 4 c x 25 sq.mm1.1 KV grade XLPE Insulated FRLS sheathed armoured AL conductor cable | Sets | 0 |  | 0
0
l | 4 c x 16 sq.mm1.1 KV grade XLPE Insulated FRLS sheathed armoured aluminium conductor cable | Sets | 0 |  | 0
0
m | 4 c x 16 sq.mm 1.1 KV grade XLPE Insulated FRLS sheathed armoured copper conductor cable | Sets | 0 |  | 0
0
n | 4 c x 10 sq.mm 1.1 KV grade XLPE Insulated FRLS sheathed armoured copper conductor cable For UPS DB | Sets | 0 |  | 0
0
p | 4 c x 6 sq.mm 1.1 KV grade XLPE Insulated FRLS sheathed armoured copper conductor cable for VRV ODUs | Sets | 0 |  | 0
0
q | 4 c x 4 sq.mm 1.1 KV grade XLPE Insulated FRLS sheathed armoured copper conductor cable | Sets | 0 |  | 0
0
s | 4 c x 2.5 sq.mm 1.1 KV grade PVC Insulated FRLS sheathed armoured copper conductor cable | Sets | 0 |  | 0
0
u | 3 c x 6 sq.mm 1.1 KV grade XLPE Insulated FRLS sheathed armoured copper conductor cable | Sets | 2 |  | 0
0
w | 2 c x 16 sq.mm 1.1 KV grade XLPE Insulated FRLS sheathed armoured copper conductor cable | Sets | 0 |  | 0
0
x | 2 c x 10 sq.mm 1.1 KV grade XLPE Insulated FRLS sheathed armoured copper conductor cable | Sets | 2 |  | 0
0
aa | 1c x 10 sq.mm FRLS XLPE insulated flexible copper conductor cables | Sets | 0 |  | 0
0
ab | 1c x 16 sq.mm FRLS XLPE insulated flexible copper conductor cables | Sets | 0 |  | 0
0
ac | 1c x 25 sq.mm FRLS XLPE insulated flexible copper conductor cables | Sets | 0 |  | 0
0
ac | 1c x 35 sq.mm FRLS XLPE insulated flexible copper conductor cables | Sets | 0 |  | 0
0
| TOTAL CARRIED OVER TO SUMMARY |  |  |  | 0
0
E | RACEWAYS AND CABLE TRAYS |  |  |  | 0
| Note :- |  |  |  | 0
0
1 | Fabricating supplying to site of installation, installation on ceiling/ surface 1.6 mm thick M.S. powder coated raceways of height 50 mm and 2.0 mm thick openable cover, totally enclosed, the joints between two lengths of channels or between channel and junction box shall be joined together with 3 mm thick M.S. Powder coated coupler plates to make it dust and water proof. The cost shall including all supporting and fixing accessories including dash fasteners. (Orange colour for data and Blue colour for power) |  |  |  | 0
a | 250 mm (wide) x 50 mm (height) | RM | 0 |  | 0
b | 150 mm (wide) x 50 mm (height) | RM | 10 |  | 0
c | 100 mm (wide) x 50 mm (height) | RM | 20 |  | 0
d | 150 mm (wide) x 150 mm (height) | RM | 0 |  | 0
0
2 | Fabricating supplying to site of installation, in floor including chase cutting of floor,leveling, refilling and making good the same from 1.6 mm thick and 2 mm thick cover pregalvanised MS CRCA sheet, totally enclosed, height 40 mm . The two lengths of raceways shall be fitted with Collars , 50 mm wide, 3 mm thick , press fit type. The raceways shall be clamped to the floor slab with GI clamps , 3mm thick and shall be screwed to the floor slab. The joint between raceway and junction box will be made with GI flexible strip( 3 nos), 3 mm thick, 4 inches long ,15 mm wide which will be nut bolted to the Junction box complete as required etc. |  |  |  | 0
0
a | 300 mm x 300 x 60 mm (height) | Nos. | 0 |  | 0
b | 250 mm x 250 x 60 mm (height) | Nos. | 0 |  | 0
c | 200 mm x 200 x 60 mm (height) | Nos. | 3 |  | 0
d | 150 mm x 150 x 60 mm (height) | Nos. | 6 |  | 0
e | 100 mm x 100 x 60 mm (height) | Nos. | 2 |  | 0
0
3 | Fabricating supplying to site of installation, in floor including chase cutting of floor,leveling, refilling and making good the same from 1.6 mm thick and 2 mm thick cover pregalvanised MS CRCA sheet, totally enclosed, height 40 mm . The two lengths of raceways shall be fitted with Collars , 50 mm wide, 3 mm thick , press fit type. The raceways shall be clamped to the floor slab with GI clamps , 3mm thick and shall be screwed to the floor slab. The joint between raceway and junction box will be made with GI flexible strip( 3 nos), 3 mm thick, 4 inches long ,15 mm wide which will be nut bolted to the Junction box complete as required etc. |  |  |  | 0
0
a | 250 mm (wide) x 40 mm (height) | RM | 0 |  | 0
b | 150 mm (wide) x40 mm (height) | RM | 5 |  | 0
c | 100 mm (wide) x 40 mm (height) | RM | 10 |  | 0
0
5 | Fabricating supplying to site of installation, Junction boxes for floor raceways made from 2 mm thick , with 2.5 mm thick G.I. cover including providing neoprene gaskets between the cover and the junction box, cadmium plated flat/round head screws, height as per site condition,totally enclosed. Proper cutouts shall be made in the side walls for raceway entry wherever required. The junction box shall be all side walls should be welded expect top cover and all side walls shall have suitable size of rectangular knock out holes for taking raceways / conduits as required and not a complete cut out. The top cover should be sealed with M Seal to make it dust and water proof complete as required etc. |  |  |  | 0
0
a | 300 mm x 300 x 50 mm (height) | Nos. | 0 |  | 0
b | 200 mm x 200 x 50 mm (height) | Nos. | 2 |  | 0
c | 150 mm x 150 x 50 mm (height) | Nos. | 4 |  | 0
d | 100 mm x 100 x 50 mm (height) | Nos. | 2 |  | 0
0
6 | Design manufacture , supply and fixing in position the cable trays of the following sizes for supporting 1.1 KV grade armoured/unarmoured aluminium /copper conductor cables. Fabricate the cable trays from perforated 1.6/2mm thick M.S. CRCA sheet duly galvanised with expansion coupler plates duly galvanised, with bolts, washer and nuts. Knock out holes for cable connections as per approved design. The tray should comply with the specification of NEC (National Electric Codes) and NEMA (National Electric Manufacturers Association). The steel should be as per IS:226 and galvanising as per IS :2629/BS 729/ASTM 123. The rate shall also include for supporting steel , fish plates , fixing accessories , nuts bolts, supporting down rods , dash fastener, cutting the RCC etc. complete as required. (the horizontal and vertical bends, T's should be factory fabricated and the rate should include for the same) |  |  |  | 0
0
a | 100 mm wide x 40 mm x 2.0 mm thk | RM | 0 |  | 0
b | 150 mm wide x 40 mm x 2.0 mm thk | RM | 60 |  | 0
c | 300 mm wide x 40 mm x 2.0 mm thk | RM | 0 |  | 0
d | 450 mm wide x 40 mm x 2.0 mm thk | RM | 0 |  | 0
e | 600 mm wide x 40 mm x 2.0 mm thk | RM | 0 |  | 0
0
7 | Design manufacture , supply and fixing in position the Ladder Type cable trays of the following sizes for supporting 1.1 KV grade armoured/unarmoured aluminium /copper conductor cables. Fabricate the cable trays to from Ladder Type 2.0 mm thick M.S. Flat/ Angle iron with bolts, washer and nuts. as per approved design. The tray should comply with the specification of NEC (National Electric Codes) and NEMA (National Electric Manufacturers Association). The steel should be as per IS:226 and galvanising as per IS :2629/BS 729/ASTM 123. The rate shall also include for supporting steel ,jointing fish plates , fixing accessories , nuts bolts, supporting down rods, dash fastener, cutting the RCC etc. complete as required. |  |  |  | 0
0
a | 300 mm wide x 50 mm x 2.0 mm thk | RM | 0 |  | 0
8 | Fabricating ,supplying to site of installation, installation of 500 mm size of 105 mm height mesh type EZ -Electroplated Zinc ( Legrand - Cablofil make ) cable tray including threaded G.I. down rods, dash fasteners , cablofil fixing accesories etc. complete as required. Cablofil make | RM | 0 |  | 0
0
| TOTAL CARRIED OVER TO SUMMARY |  |  |  | 0
0
F | DISTRIBUTION BOARDS |  |  |  | 0
0
1 | Supply,inginstalling ,connecting testing and commissioning of the following double door 1/4 rows vertical type 1.6 mm thick and 1. 4 thick door sheet steel enclosed fully recessed type, TPN Miniature Circuit Breakers Distribution Boards dust proof, verm­in proof, with hinged and lockable doors complete with DP MCB's and inter-connection with copper wire , insulated copper bus bar , cable glands­/conduit entry bushes, bonding to earth and paint­ing. Also provide separate neutral busbar for each phase. Provide separate Earth Links for each phase. Use brass thimbles for connections of all wires. 1 row for single phase and 4 rows for 3 phase. Provide separate 4 way 63 A main neutral link also. The phase busbar links shall be factory pre insulated. |  |  |  | 0
| Note :- The IP rating of the DB should be IP 43 . |  |  |  | 0
| Provide DB charts in laminated sheets in all Distribution Boards |  |  |  | 0
| A4 size SLD to be fixed on all DBs. |  |  |  | 0
0
1 | Light & Power Distribution Board |  |  |  | 0
0
a | 10 Way TPN DB, each phase consisting of 8 Nos. 10/20 AMP SP MCB’s and controlled by one number 100 mA sensitivity 63 AMPS DP RCCB backed up with 1 no 63 Amps 4 pole MCB. For VRV DB | Nos | 0 |  | 0
0
b | 12 Way TPN DB, each phase consisting of 10 Nos. 10/20 AMP SP MCB’s and controlled by one number 100 mA sensitivity 63 AMPS DP RCCB backed up with 1 no 63 Amps 4 pole MCB. For Light DB | Nos | 1 |  | 0
0
c | 14 Way TPN DB, each phase consisting of 12 Nos. 10/20 AMP SP MCB’s and controlled by one number 100 mA sensitivity 63 AMPS DP RCCB backed up with 1 no 63 Amps 4 pole MCB. For Power DB | Nos | 0 |  | 0
0
d | 12 Way SPN DB, consisting of 8 Nos. 10/20 AMP SP MCB’s and controlled by one number 100 mAsensitivity 63 AMPS DP RCCB backed up with 63 Amps DP MCB as incomer. For VRV DB | Nos | 1 |  | 0
0
2 | UPS Distribution Boards (All MCB's in workstation DB's should be D Curve) |  |  |  | 0
0
a | 12 Way TPN DB, each phase consisting of 10 Nos. 10/20 AMP SP MCB’s and controlled by one number 63 AMPS DP RCCB (100 mA) for each phase and 1 no. 63 amps 4 pole MCB incomer. | Nos.. | 0 |  | 0
0
b | 14 Way SPN DB, consisting of 10 Nos. 10/20 AMP SP MCB’s and controlled by one number 100 mA sensitivity 63 AMPS DP RCCB backed up with 63 Amps DP MCB. | Nos.. | 0 |  | 0
0
c | 12 Way SPN DB, consisting of 18 Nos. 10/20 AMP SP MCB’s and controlled by one number 100 mA sensitivity 63 AMPS DP RCCB backed up with 63 Amps DP MCB. For UPS DB | Nos.. | 1 |  | 0
0
d | 12 Way SPN DB, consisting of 4 Nos. 25/32 AMP DP MCB’s and controlled by one number 100 mA sensitivity 63 AMPS DP RCCB ( 100 mA) for backed up with 63 Amps 4D MCB. The bus bar shall be Twin bus bar. | Nos.. | 0 |  | 0
0
3 | Supply, installation, testing and commissioning of sheet metal with 40 A DP MCB. This shall include cable entry boxes both for incoming and outgoing cable). | Nos. | 1 |  | 0
0
4 | Supply, installation, testing and commissioning of sheet metal weather proof enclosure with 63 A FP RCBO(300mA) This shall include cable entry boxes both for incoming and outgoing cable) For VRV units. The enclosure shall be IP 42. For VRV Out Door units | Nos. | 1 |  | 0
0
5 | Supply, installation, testing and commissioning of sheet metal weatherproof Enclosure with 25/32 A DP MCB. This shall include cable entry boxes both for incoming and outgoing cable). | Nos. | 0 |  | 0
0
6 | Supply, installation, testing and commissioning of sheet metal with 16 A FP MCB. This shall include cable entry boxes both for incoming and outgoing cable). For CS AHU | Nos. | 0 |  | 0
0
| TOTAL CARRIED OVER TO SUMMARY |  |  |  | 0
0
G | SUB DISTRIBUTION PANELS |  |  |  | 0
0
1 | Sub Distribution Panels |  |  |  | 0
| Design, manufacture, supplying & installing at site in positioning, connecting, testing and commissioning of the following cubical type, dead front, 2mm thick sheet steel enclosed, free standing indoor type extendible Sub Distribution Panel with vermin proof hinged lockable doors for each compartment provide bus bar interconnections for incoming and outgoing including feeders earthing and painting and as per specifications. |  |  |  | 0
Note | Provide insulated dedicated earth link in all UPS Panels |  |  |  | 0
| All MCCB's 200 Amps and above shall be Microprocessor based |  |  |  | 0
| All Light & Power panel ,UPS and A.C. Panel incomer MCCB shall have Over current, Earth fault and short circuit protection. |  |  |  | 0
| All Incomer MCCB's in UPS Panels shall be Microprocessor based |  |  |  | 0
| The microprocessor based MCCBs shall have |  |  |  | 0
| Over Load (Phase) |  |  |  | 0
| Current setting Ir(Ir=XIn) OFF 0.4 to 1.0 in steps of 0.1 |  |  |  | 0
| Time delay , tr( Inverse) 10 sec at 6/r |  |  |  | 0
| Over Load (Neutral) |  |  |  | 0
| Current setting In (Intrl =XIr) 0.5, 0.75&1.00 Intrl |  |  |  | 0
| Inverse 10 sec at 6 Intrl/Fixed 200ms |  |  |  | 0
| Short Circuit setting -2- 10 |  |  |  | 0
| Instantaneous - 1.5-1 |  |  |  | 0
| All MCB's in UPS Panels shall be D Curve |  |  |  | 0
| In all Electrical panels protective acrylic sheet to be provided in cable alley and feeders. |  |  |  | 0
| The meters shall be able to monitor all major power quality parameters Voltage , current , frequency , KVAH,KWH,Power factor and individual,harmonics, ethernet ready - IEC-625-22. |  |  |  | 0
| The ATS shall be 4 pole with inbuilt manual operating switch. In case the controller of the ATS fails it should be capable of transferring the load while the ATS is in maintenance. The ATS and controller should be same make |  |  |  | 0
| Provide On / Off and trip indicating lamp on main incomer only. |  |  |  | 0
| Panel construction shall be Form 3b for all Panels with MCCB outgoings and Form 2b for all Panels with MCB's outgoings. |  |  |  | 0
| The Earth fault release/relay and CBCTs shall be same make as OEM Switchgear been used in the Panels. It shall not trip on imbalance of load. |  |  |  | 0
| All meters shall have Modbus card for BMS connectivity |  |  |  | 0
| All the Electrical Panels shall be in accordance with IS 8623 standards |  |  |  | 0
0
a | The SDB L&P shall consists of : |  |  |  | 0
0
| MAIN INCOMER |  |  |  | 0
| 1 Nos. 100 A TPN MCCB (25KA/1 sec)( O/C, S/C,E/F) and neutral isolation link 100% of rated current. Terminals suitable to receive 3.5c x 50 sq. mm . Al Ar cable connection on one side and Busbar connection on the other side. |  |  |  | 0
0
| BUSBAR |  |  |  | 0
| 150 amps 4P busbar chamber of suitable length with Aluminium busbars. All busbars and interconnections shall be of suitable size aluminium strips current density of aluminium shall not be more than 0.8 Amps/ sq.mm.provide 100% capacity for neutral bus bar. |  |  |  | 0
0
| INDICATING PANELS |  |  |  | 0
| 3 nos phase indicating lamps (LED type) each backed up with MCB and switch shall be provided for each incomer. |  |  |  | 0
| Provide Intelligent Panel Meter - multifunctional meter with RS485 for all incoming feeder |  |  |  | 0
| Provide Transient Voltage Surge Suppressor Rating 40kA class II along with 63 A MCCB. Including all necessary accessories. For Switching Operation on each incomer. |  |  |  | 0
| Provide earth fault protection (EF) in the incomer MCCB |  |  |  | 0
0
| OUTGOINGS |  |  |  | 0
| 4 Nos. 63 A 4P MCB (10 kA/ 1 sec) terminal to receive suitable Cable on one side and Busbar connection on the other side. |  |  |  | 0
| 2 Nos. 40 A DP MCB (10 kA/ 1 sec) terminal to receive suitable Cable on one side and Busbar connection on the other side. |  |  |  | 0
0
| The SDB L&P as described above and specifications complete | Set | 1 |  | 0
0
b | The UPS SDB in UPS Room shall consists of : |  |  |  | 0
0
| MAIN INCOMER |  |  |  | 0
| 2 No. 100 A TP+2N MCCB (25KA/1 sec)( O/C, S/C,E/F). Terminals suitable to receive 5R x 1c x 35 sq. mm Cu. Flexible cable connection on one side and Busbar connection on the other side. |  |  |  | 0
0
| BUSBAR |  |  |  | 0
| 150 amps TP+2N busbar chamber of suitable length with Copper busbars. All busbars and interconnections shall be of suitable size copper strips current density of copper shall not be more than 1.6 Amps/ sq.mm. |  |  |  | 0
0
| INDICATING PANELS |  |  |  | 0
| 3 nos phase indicating lamps (LED type) each backed up with MCB and switch shall be provided for each incomer. |  |  |  | 0
| Provide on/off indication lamp on each incomer and buscoupler. |  |  |  | 0
| Provide Intelligent Panel Meter - multifunctional meter with RS485 for all incoming feeder |  |  |  | 0
| Provide Transient Voltage Surge Suppressor Rating 40kA class I&II along with 63 A MCB. Including all necessary accessories. For Switching Operation on each incomer. |  |  |  | 0
| Provide earth fault protection (EF) in the incomer MCCB |  |  |  | 0
0
| OUTGOINGS |  |  |  | 0
| 4 Nos. 63 A 4P MCB (10 kA/ 1 sec) terminal to receive suitable Cable on one side and Busbar connection on the other side. |  |  |  | 0
| 4 Nos. 63A DP MCB (10 kA/ 1 sec) terminals to receive suitable Copper Ar. Cable on one side and Busbar connection on the other side. |  |  |  | 0
| The above Panel as described above and specifications complete | Set | 0 |  | 0
0
2 | The contractor to submit reports of torque tightness tests for all the nut bolt cable joints in all the panels with red marking after the torque tightening has been done as per manufactures recommendation. | Set | 0 |  | 0
0
3 | Providing & fixing in position 1000 mm wide , Electrical Insulating Mats as per IS 15652:2006, 2mm thick, suitable up to 3.3 KV , fire retardant,no effect of acids, alkalies and transformer oils, moisture proof, high tensile strength and texture finish / cloth impression (Anti slip , marking on top) . | RM | 3 |  | 0
0
4 | Replacement of existing 250 A tap off box with 400 A tap off box at site with all the necessary accessories complete as required. | Nos. | 0 |  | 0
0
5 | Supply & fixing in position approved shock treatment chart written in English, Hindi and Local language. These charts shall be framed in wooden frame & covered with clear glass. | Nos. | 1 |  | 0
0
6 | Supply & fixing in position the best quality danger notice boards of approved shape & size as reqd. by the local Electrical Inspecting Authority written in English, Hindi & local language. | Nos. | 1 |  | 0
0
7 | Supply & fixing in position the Electrical A 1 Size SLD chart in the UPS/electrical room . These charts shall be framed in wooden frame & covered with clear glass. | Nos. | 1 |  | 0
0
8 | Supplying the first aid box as approved by John Ambulance society. | Nos. | 1 |  | 0
0
9 | Supply & Fixing of NO/NC Relay Module complete as required. | Nos. | 0 |  | 0
0
10 | 2 core -1.5 sq.mm PVC FRLS wires in already laid suitable size of M.S conduit complete as required. | Rmt | 0 |  | 0
0
11 | Supply, Installations, Testing and Commissioning of 2 Kg Fire Suppression System (CQRS) in all Floor Panels of Electrical and UPS Room to be included. - Automatic Direct Low Pressure Fire Suppression System, UL Listed FK-5-1-12 Extinguishing Fluid shall be filled in UL Listed Cylinder, UL Listed Pressure Switch should be integrated in DLP Valve for Indication on Fire Suppression Panel and Main Fire Alarm System, 15 Meter UL Listed Detection Tube shall be UV Protected made of Modified Polyamide associated with End of Line Adapter with Pressure Gauge, master Control Panel with A/V Alarm and Battery Backup along with Potential Free Contact to integrate with existing Fire Alarm System for Central Monitoring. Mounting Bracket with all necessary accessories. complete in all respect. System Component Approval: Cylinder-UL Listed, Gas-UL Listed, Detection Tube-UL Listed, Pressure Switch-UL Listed Make: FireMech / Ceasefire / Honeywell | Nos. | 0 |  | 0
0
| TOTAL CARRIED OVER TO SUMMARY |  |  |  | 0

## Light FixturesB1
Sl.No. | Description | Unit |  | Supply & Installation
|  |  | Qty | Rate In Rs. | Amount in Rs.
H | SUPPLY & INSTALLATION OF LIGHTING FIXTURES |  |  |  |  | *Quoted Installation
1 | Supply & Fixing in position testing and commissioning of the following Lighting fixtures at site including all type of fixing accessories complete as required etc. Use all light fixture shall be LED Type. (Samples of all light fixtures to be submitted to the client/architect/consultant for approval prior to procurement of fixtures) |  |  |  | 0
0
a | 32 Watts LED 600x600mm panel LED light as per approved make. | Nos | 0 |  | 0
0
b | 32 Watts LED 600x600mm panel LED Fire Proof light as per approved make.(Fire proof for Bonded store) | Nos | 0 |  | 0
0
c | 15 watts Suspended Cylindrical LED light as per approved make. | Nos | 0 |  | 0
0
d | Suspended Channel LED light (90x1500) at Cabins as per approved make | Nos | 0 |  | 0
0
e | Suspended Channel LED light (90x750) at Reception as per approved make | Nos | 0 |  | 0
0
f | 13 wattts Surface Mounted LED Down light as per approved make | Nos | 16 |  | 0
0
g | 13 wattts Recessed LED Down light as per approved make | Nos | 26 |  | 0
0
2 | Supply, Installation, Testing & Commissioning of 3 Watts LED Ni Cd Battery backup up to 1.5 hr emergency Exit light Prolite or equivalent make. The sample shall be submitted before ordering. or Equivalent make. | Nos | 2 |  | 0
0
3 | Supply, installation, testing commissioning of recessed ceiling mounted photo cell switching units to provide ON/OFF switching of lighting in response to ambient light levels. | Nos | 0 |  | 0
0
4 | Supply & installation of Passive infra-red presence detector for lighting control to set the parameters of all meeting rooms and cabin (ON/OFF selection of lights)( Lights switch OFF in steps of 1 minute) | Nos | 0 |  | 0
a | Switches lighting OFF when sufficient daylight is present. |  |  |  | 0
b | Used as on ON/OFF daylight dependant switch or in series with a wall switch |  |  |  | 0
c | Lighting level adjustable up to 1500 lux approx. |  |  |  | 0
0
| TOTAL CARRIED OVER TO SUMMARY |  |  |  | 0

## ElectB2
Sl.No. | Description | Unit |  | Supply & Installation
|  |  | Qty | Rate In Rs. | Amount in Rs.
A. | POINT WIRING
| All wires shall be FRLS PVC insulated copper conductor. Point wiring rates are inclusive of 3 x 1.5 sq mm insulated copper conductor wires for circuit.(from DB to switch board). |  |  |  | 0
| All sockets to be checked with a Check Plug socket tester for live-neutral reverse, no earth,neutral fault, live earth reverse, neutral earth reverse. |  |  |  | 0
| The Circuit No. and DB no. label shall be provided on all UPS ,RAW sockets and switchboards with label printer. |  |  |  | 0
| Colour coding for conduits to be done for different systems. The whole length of conduits to be painted. |  |  |  | 0
| All circuit & point wiring shall be colour coded & shall have ferruling on both end for circuit identification complete as required etc.Labelling on all the switches and sockets to be done with respect to DB reference, phase and circuit no. |  |  |  | 0
| Earth loop Impedance Test to be performed. RCD test to be done. Cable Insulation Tests to be done. |  |  |  | 0
| Wherever the occupancy sensor is provided in the cabin/ meeting rooms/workstations , the circuit wires from Distribution Board to occupancy sensor and sensor to switch are inclusive in the point wiring rate. |  |  |  | 0
| Labeling of all sockets and emergency lights to be provided and Ferruling for all the circuits to be considered |  |  |  | 0
1 | Wiring for the following light points with 3x1.5 Sq.mm FRLS PVC insulated stranded copper conductor wires in concealed M.S. conduits in F.ceiling/walls/ceiling as directed including providing and fixing of 6 amps flush type switches, 5 sided G.I Boxes for housing switc­hes and earth­ing complete as required. Rates are inclusive of 3 x 1.5 sq mm FRLS PVC insulated stranded copper conductor wires for circuit |  |  |  | 0
0
a. | First point controlled by one no. 6 amp switch. | Nos. | 8 |  | 0
0
2 | Same as item No. 1a above but LOOP POINT i.e. wiring of point looped from first point with 3 x 1.5 sq. mm FRLS PVC insulated copper conductor wire in concealed/exposed MS conduit and earthing | Nos. | 12 |  | 0
0
3 | Wiring for the following light points with 1.5 Sq.mm FRLS PVC insulated stranded copper conductor wires in concealed M.S. conduits in F.ceiling/walls/ceiling as direc­ted including providing and fixing of 6 amps flush type switches, 5 sided G.I Boxes for housing switc­hes and earth­ing comple­te as required. Rates are inclusive of 3 x 1.5 sq mm FRLS PVC insulated stranded copper conductor wires for circuit |  |  |  | 0
0
a. | First point controlled by one no. 16 amp switch. | Nos. | 0 |  | 0
0
4 | Wiring for the following light points controlled by MCB in DB (Cost of MCB has been taken elsewhere in the tender) with 3 x 1.5 sq. mm FRLS PVC insulated copper conductor wires in concealed/exposed M.S. conduits as called for and earthing. |  |  |  | 0
0
a. | First point controlled by existing MCB in D.B. To first light Em Light | Nos. | 1 |  | 0
0
5 | Same as item No. 4.a above but LOOP POINT i.e. wiring of point looped from first point with 3x1.5 sq. mm FRLS PVC. insulated copper conductor wire in concealed/exposed M.S. conduit and earthing | Nos. | 8 |  | 0
0
6 | SITC of 2C x 1.5 sq mm non shielded Cable for DALI Ballast wiring in 25 mm dia MS conduit with all fixing accessories complete as required | Rmt. | 0 |  | 0
0
7 | SITC of 4C x 1.5 sq mm shielded Cable for QSM wiring in suitable size of MS conduit with all fixing accessories complete as required. Cable Common – 12 AWG (4.0 mm2); Power – 12 AWG (4.0 mm2); MUX Data – 22 AWG (0.25 mm2); Data – 22 AWG (0.25 mm2); Sense Line – 18 AWG (0.75 mm2); Drain Wire – 24 AWG (0.2 mm2) | Rmt. | 0 |  | 0
0
8 | Wiring for 6/16 amps outlets with 3 X 2.5 sq.mm FRLS PVC insulated copper conductor wires in M.S. Conduits in ceiling/walls/floor as direc­ted incl­u­ding providing & fixing of 6/16 amps flush type 5 pin socket and 16 amps switch with cover plate, 5 sided G.I boxes for housing switches, sockets and earthi­ng complete as required. (for general areas 4 nos loop in one circuits) | Nos. | 7 |  | 0
0
9 | Wiring for inline fan points with 2 x 2.5 sq.mm FRLS PVC insulated stranded copper con­ductor wires in concealed M.S. conduits in F.ceiling/ walls/ Ceiling as directed including providing and fixing of 16 amps flush type switches 16 amps 3 pin socket near inline fan, 5 sided G.I. boxes for housing switches and 16 amps 3 pin socket outlet and earthing and complete as required.(including body earth for GI boxes) | Nos. | 2 |  | 0
0
10 | Wiring for Geyser/Projector/Hand Dryer points with 2 x 4 + 1 x 4 sq mm FRLS PVC insulated copper conductor wires in concealed M.S. conduits in F.ceiling/ walls/ Ceiling as directed including providing & fixing 16 amps flush type switch near the white board and 6/16 amps 6 pin socket near the projector in ceiling , 5 sided G.I. boxes for housing switches and 6/16 A 6 pin socket outlet , earthing and complete as required.(including body earth for GI boxes) ( 1 point per circuit) | Nos. | 4 |  | 0
0
11 | Wiring for VRV Indoor units with 3 x 2.5 sq.mm FRLS PVC insulated stranded copper conductor wires in concealed M.S. conduits in F.ceiling/ walls/ Ceiling as directed including providing providing and fixing of 6 amps flush type switches 16 amps 3 pin socket near VRV points, 5 sided G.I. boxes for housing switches and 16 amps 3 pin socket outlet and earthing and complete as required.(including body earth for GI boxes) (1 point per circuit) | Nos. | 6 |  | 0
0
12 | Wiring for VAV /fire damper points with 3 x 2.5 sq.mm FRLS PVC insulated copper conductor wires in concealed M.S. conduits in F.ceiling/ walls/ Ceiling as directed including providing & fixing 6 amps flush type switches, 6 amps 3 pin socket near VAV points, 5 sided G.I. boxes for housing switches and 6 A sockets earthing and complete as required. The sockets to be fused spur type (MK make). (including body earth for GI boxes) (8 to 10 points per circuits) | Nos. | 0 |  | 0
0
13 | Wiring for 16 amps power outlet poi­nts with 4 sq.mm FRLS PVC insulated stranded copper conductor wires in concealed/recessed M.S. conduit as directed including providing providing and fixing of 16 amps flush type switch and 6 pin socket with cover plate 5 sided G.I. outlet boxes for switches and socket and earthing the third pin with 2.5 sq mm FRLS PVC stranded copper wire complete as required (Only one outlet shall be connected on each circuit) (including body earth for GI boxes) | Nos. | 3 |  | 0
0
14 | Wiring for 16 amps power outlet points with 4 sq.mm FRLS PVC insulated stranded copper conductor wires for the first power outlet and 4 sq.mm FRLS PVC insu­lated stranded copper conductor wires for the second outlet, in concealed M.S. cond­uits in F.ceiling/ walls/Ceiling/floor ducts as directed including providing providing and fixing of 16 amps flush type switch and 6 pin socket with cover plate, 5 sided G.I. outlet boxes for housing switches and socket, and earthing the third pin with 2.5 sq.mm FRLS PVC insulated copper conductor wires complete as required (Two power out­lets shall be connected on each circuit)(including body earth for GI boxes) | Set of Two | 1 |  | 0
0
15 | Wiring for A/C outlet points with 4.0 sq mm FRLS PVC insulated stranded copper conductor wires in M.S. conduitl/wall/floor ducts as directed including providing 25 A socket with 25 amps SP MCB ( Tiny Trip) 5 sided GI Outlet Box for housing and socket and MCB and earthing with 2.5 sq. mm FRLS PVC insulated stranded Copper Conductor wires complete as required. | Nos. | 0 |  | 0
0
| Different colours to be used for 3 core cables for raw power and UPS power. |  |  |  | 0
16 | Wiring for UPS/Raw plug outlets points with three core, 2.5 sqmm FRLS PVC Insulated and PVC sheathed flexible cable with bright annealed electrolytic copper conductor, 1100 volt grade confirming to IS : 694-1990 with latest amendments, in existing Channels/ conduit in ceiling/walls/floor including all cable termination accessories) (including body earth for GI boxes). Colour Coding to be followed | RM | 145 |  | 0
0
17 | Wiring for UPS/Raw plug outlets points with three core, 4.0 sqmm FRLS PVC Insulated and PVC sheathed flexible cable with bright annealed electrolytic copper conductor , 1100 volt grade confirming to IS : 694-1990 with latest amendments, in existing Channels/ conduit in ceiling/walls/floor inclu­ding all cable termination accessories) Earthing of GI Box to be included. Colour Coding to be followed. | RM | 40 |  | 0
0
18 | Wiring for Power plug outlets points with three core, 6.0 sqmm FRLS PVC Insulated and PVC sheathed flexible cable with bright annealed electrolytic copper conductor , 1100 volt grade confirming to IS : 694-1990 with latest amendments, in existing Channels/ conduit in ceiling/walls/floor inclu­ding all cable termination accessories). Colour Coding to be followed. | RM | 0 |  | 0
0
19 | Wiring for Power plug outlets points with three core, 10.0 sqmm FRLS PVC Insulated and PVC sheathed flexible cable with bright annealed electrolytic copper conductor , 1100 volt grade confirming to IS : 694-1990 with latest amendments, in existing Channels/ conduit in ceiling/walls/floor inclu­ding all cable termination accessories). Colour Coding to be followed. | RM | 25 |  | 0
0
| The word UPS shall be printed on all UPS sockets. |  |  |  | 0
| The word RAW shall be printed on all RAW sockets. |  |  |  | 0
| The Circuit No. and DB no. label shall be provided on all UPS ,RAW sockets and switchboards with label printer. |  |  |  | 0
| Contractor is required to submit samples of all types of switches and sockets to Consultant and Architects representative for approval before ordering the material. |  |  |  | 0
0
20 | Providing and fixing of 1 Nos. 6 amp round pin type socket and 1 No. 6 amps switch cover plate, 5 sided G.I. Boxes for housing switches and sockets and earthing complete as required (for UPS/Raw). GI Box to have earth pin for body earthing | Nos. | 16 |  | 0
0
21 | Providing and fixing of 2 Nos. 6 amp round pin type socket and 1 No. 6 amps switch cover plate, 5 sided G.I. Boxes for housing switches and sockets and earthing complete as required (for UPS/Raw). GI Box to have earth pin for body earthing | Nos. | 13 |  | 0
0
22 | Providing and fixing of 3 Nos. 6 amp round pin type socket and 1 No. 6 amps switch cover plate, 5 sided G.I. Boxes for housing switches and sockets and earthing complete as required (for UPS/Raw). GI Box to have earth pin for body earthing | Nos. | 1 |  | 0
0
23 | Providing and fixing of 2 Nos. 6/16 amp round pin type socket and 1 No. 16 amps switch cover plate, 5 sided G.I. Boxes for housing switches and sockets and earthing complete as required (for UPS/Raw). GI Box to have earth pin for body earthing | Nos. | 0 |  | 0
0
24 | Providing and fixing of 1 No.16 amps flush type 6 pin socket and 1 No. 16 amps switch with indicator, cover plate, 5 sided G.I. Boxes for housing switches and sockets and earthing complete as required (for UPS / RAW) GI Boxes to have earth pin for body earthing | Nos. | 2 |  | 0
0
25 | Providing and fixing Underfloor Access Outlets (250 x 250 x 55 - mm 70 compartments 1Trap including providing 2 Nos 6 Amps Round Pin sockets and 1 no. 16 Amp Switch & 2 data outlet complete as required. | Nos. | 1 |  | 0
0
26 | Supply and fixing of the following sizes of thermoplastic moulded plug and socket IEC 309 type in PVC Box of suitable size flush / surface and making connections complete as required. The box shall be IP 44. |  |  |  | 0
a | 3 pin 16/20 A 1 phase industrial socket with mcb & plug top | Nos. | 0 |  | 0
b | 3 pin 32 A 1 phase industrial socket plug top | Nos. | 0 |  | 0
0
27 | Providing and fixing in position the following M.S. conduits including all accessories concealed in F. ceiling/wall/floor as required including 1.6 mm thick M.S. junction or pull boxes with 3mm thick perspex sheet cover plate compl­te with 1.6 mm dia. G.I. pull wires in the length of conduit. |  |  |  | 0
0
a. | 20 mm dia conduit ( 1.6 mm thick) | RM | 40 |  | 0
b. | 25 mm dia conduit (1.6 mm thick) | RM | 70 |  | 0
c. | 32 mm dia conduit (2.0 mm thick) | RM | 50 |  | 0
28 | The Electrical Contractor shall provide sufficient temporary lighting for working in the Building total area 1066 sq. ft. divided in single floor and maintain the same till completion of the project.It shall include replacement of all fused/faulty lamps.It shall include providing 15 A plug sockets (industrial type with ON/OFF switch/MCB) on 4 sides walls one plug at every 5-8 meter distance. The Contractors will tap off supply from these plugs for his use. Tubelights to maintain a lighting level of 150 lux on the floor,.Each 15 A socket and each Light circuit shall be protected by suitable MCBs.Use three core PVC Insulated PVC sheathed copper conductor cables for wiring.The contractor shall salvage the complete wiring and take it back at the end of the project. | L.S. | 1 |  | 0
0
| TOTAL CARRIED OVER TO SUMMARY |  |  |  | 0
0
B. | CONDUITING FOR TELEPHONE , COMPUTER & CONDUITING AND WIRING FOR T.V. SYSTEM. |  |  |  | 0
0
1 | Providing and fixing in position the following M.S. conduits including all accessories concealed in F. ceiling/wall/floor as required including 1.6 mm thick M.S. junction or pull boxes with 3mm thick perspex sheet cover plate compl­te with 1.6 mm dia. G.I. pull wires in the length of conduit. |  |  |  | 0
0
a. | 20 mm dia conduit( 1.6 mm wall thickness) | RM | 35 |  | 0
b. | 25 mm dia conduit ( 1.6 mm wall thickness) | RM | 65 |  | 0
c. | 32 mm dia conduit ( 1.6 mm wall thickness) | RM | 50 |  | 0
0
2 | Providing and fixing in position suitable 1.2 mm thick G.I./ PVC outlet box for RJ- 45 computer outlet with all fixing accessories as required. | Nos. | 5 |  | 0
0
3 | Supply and fixing of 1.2 mm thick G.I Box along with RG 11 TV Co axial socket with Cover Plate | Nos. | 1 |  | 0
0
4 | Supply drawing connecting testing and commissioning of TV Coaxial cable RG 6 in existing conduit | RM | 60 |  | 0
0
| TOTAL CARRIED OVER TO SUMMARY |  |  |  | 0
0
C. | EARTHING |  |  |  | 0
0
1 | Providing and fixing in position the following copper strips and wires including providing all fixing accessories and effecting proper connections |  |  |  | 0
| Note:- MS Cable markers at the earth bus, panel and DB entries to be provided |  |  |  | 0
a. | G.I. tape 25 mm x 6 mm | RM | 95 |  | 0
b. | Copper tape 25mm x 3 mm | RM | 0 |  | 0
c. | GI wire 8 SWG | RM | 55 |  | 0
d. | GI wire 12 SWG | RM | 0 |  | 0
e. | Supply installation , and making of Exothermic weld suitable to bond GI strip of 25x5 mm with Copper Strip of 25x5 mm with 75mm extensions on either side | Nos. | 0 |  | 0
f. | Copper Earth Link connectors - 200 mm long, 25mm wide and 5 mm thick | Nos. | 0 |  | 0
0
2 | Supply and laying, effecting proper connec­tions, testing & commissioning of the following sizes of 1.1 KV armoured XLPE/ unarmoured FRLS sheathed XLPE insulation, conforming to IS: 7098 (Part-1)- 1988 ( 90 deg C) aluminium /copper conductor cables conforming to IS : 1554 and FRLS Insulated flexible copper cables as per IS 694 laid over MS supports in existing RCC ducts/ laid in ground /laid on Cable Trays including clamping the cables to sup­ports in an approved manner as required complete with all accessories. |  |  |  | 0
0
a | 1c x 50 sq.mm FRLS insulated flexible copper conductor cables | RM | 0 |  | 0
0
b | 1c x 35 sq.mm FRLS insulated flexible copper conductor cables | RM | 0 |  | 0
0
c | 1c x 25 sq.mm FRLS insulated flexible copper conductor cables | RM | 0 |  | 0
0
d | 1c x 16 sq.mm FRLS insulated flexible copper conductor cables | RM | 0 |  | 0
0
e | 1c x 10 sq.mm FRLS insulated flexible copper conductor cables | RM | 65 |  | 0
0
f | 1c x 6 sq.mm FRLS insulated flexible copper conductor cables | RM | 30 |  | 0
0
g | 2 Nos 1 x 10 Sq. mm FRLS insulated flexible copper conductor cables (Green Colour for UPS DB Sub-main Earthing) | RM | 0 |  | 0
0
3 | Supplying and making of end termination for the following size of compression lugs and PG Threaded Nylon Flexible cable glands complete with all fixing accessories as required |  |  |  | 0
0
a | 1c x 50 sq.mm FRLS insulated flexible copper conductor cables | Sets | 0 |  | 0
0
b | 1c x 35 sq.mm FRLS insulated flexible copper conductor cables | Sets | 0 |  | 0
0
c | 1c x 25 sq.mm FRLS insulated flexible copper conductor cables | Sets | 0 |  | 0
0
d | 1c x 16 sq.mm FRLS insulated flexible copper conductor cables | Sets | 0 |  | 0
0
d | 1c x 10 sq.mm FRLS insulated flexible copper conductor cables | Sets | 4 |  | 0
0
4 | Providing earthing station at loca­tion as called for including provid­ing 600 mm x 600 mm x 3 mm thick tinned copper electrode 2 Nos 25 x 3 mm copper strip (for body earthing GI strip can be considerd) up to ground level 20mm dia medium class GI pipe (India Tube Company make or approved equal) CI funnel with 20 gauge GI wire mesh, masonry chamber with concrete base, CI man­hole cover (cover to be heavy duty) with frame (300mm x 300mm) and bitumastic paint and packing the fixture of charcoal and common salt around plate electrode complete as per I.S. ( Minimum depth shall be 4.2 M ) for UPS & Server | Nos. | 0 |  | 0
0
5 | Supply, Installation, testing and commissioning of Maintenance Free Earthing of make Electrolytic Earthing comprising of type 'K' copper 2.4 mm wall thickness, hollow tube 10 feet long, 2.125 inches outer diameter completely filled with non hazardous metallic salts (Terrafill) to achieve an earth resistance of less than 1 ohms. Provide masonry chamber with concrete base, CI man­hole cover (cover to be heavy duty) with frame (300mm x 300mm) and make earth pit sign/ identifcation no in each earth station for UPS & Server | Nos. | 1 |  | 0
0
6 | Supply, installation, testing and commissioning of sheet metal enclosed 450 x 200 x 150 (D) mm insulated earth distribution board with 1 nos. 50 x 6 mm copper tinned earth bars on SMC insulator suitable for 6/8 nos connections complete with all fixing accessories as required. | Nos. | 0 |  | 0
0
7 | Supply, installation, testing and commissioning of sheet metal enclosed 300 x 200 x 150 ( D) mm insulated earth distribution board with 1 nos. 32 x 6 mm copper tinned earth bars on SMC insulator suitable for 6/8 nos connections complete with all fixing accessories as required. | Nos. | 1 |  | 0
0
8 | Supplying and laying of the following sizes of Heavy duty PVC Pipes below paved area including chase cutting and back filling. |  |  |  | 0
a. | 100 mm outer dia | RM | 0 |  | 0
b. | 80 mm outer dia | RM | 10 |  | 0
0
| TOTAL CARRIED OVER TO SUMMARY |  |  |  | 0
0
D | CABLES, MAINS & SUBMAINS |  |  |  | 0
0
1 | Supply and laying, effecting proper connec­tions, testing & commissioning of the following sizes of 1.1 KV armoured XLPE/ unarmoured FRLS sheathed XLPE insulation, conforming to IS: 7098 (Part-1)- 1988 ( 90 deg C) aluminium /copper conductor cables conforming to IS : 1554 and FRLS Insulated flexible copper cables as per IS 694 laid over MS supports in existing RCC ducts/ laid in ground /laid on Cable Trays including clamping the cables to sup­ports in an approved manner as required complete with all accessories. |  |  |  | 0
0
| Note : All cables to be glanded and crimped with suitable sized lugs. All Cable trays to be double earthed. All raceways and cable glands to be earthed with brass round earth clips and wires. |  |  |  | 0
| Earthing ring to be included in all the cable glands. |  |  |  | 0
| Sub main cables should be labelled at both ends |  |  |  | 0
| Joints shall be allowed only at the 2 ends of the cables and not in between. |  |  |  | 0
0
a | 3.5 c x 300 sq.mm1.1 KV grade XLPE Insulated FRLS sheathed armoured aluminium conductor cable | RM | 0 |  | 0
0
b | 3.5 c x 240 sq.mm1.1 KV grade XLPE Insulated FRLS sheathed armoured aluminium conductor cable (Assumed) | RM | 0 |  | 0
0
c | 3.5 c x 185 sq.mm1.1 KV grade XLPE Insulated FRLS sheathed armoured aluminium conductor cable | RM | 0 |  | 0
0
d | 3.5 c x 150 sq.mm1.1 KV grade XLPE Insulated FRLS sheathed armoured aluminium conductor cable | RM | 0 |  | 0
0
e | 3.5 c x 120 sq.mm1.1 KV grade XLPE Insulated FRLS sheathed armoured aluminium conductor cable | RM | 0 |  | 0
0
f | 3.5 c x 95 sq.mm1.1 KV grade XLPE Insulated FRLS sheathed armoured aluminium conductor cable | RM | 0 |  | 0
0
g | 3.5 c x 70 sq.mm1.1 KV grade XLPE Insulated FRLS sheathed armoured aluminium conductor cable | RM | 0 |  | 0
0
h | 3.5 c x 50 sq.mm1.1 KV grade XLPE Insulated FRLS sheathed armoured aluminium conductor cable For SDB L&P (Assumed) | RM | 60 |  | 0 | 2
0
i | 4 c x 35 sq.mm1.1 KV grade XLPE Insulated FRLS sheathed armoured aluminium conductor cable | RM | 0 |  | 0
0
j | 4 c x 25 sq.mm1.1 KV grade XLPE Insulated FRLS sheathed armoured aluminium conductor cable For DB and VRV ODU | RM | 50 |  | 0 | 6
0
k | 4 c x 25 sq.mm1.1 KV grade XLPE Insulated FRLS sheathed armoured copper conductor cable | RM | 0 |  | 0
0
l | 4 c x 16 sq.mm1.1 KV grade XLPE Insulated FRLS sheathed armoured aluminium conductor cable | RM | 0 |  | 0
0
m | 4 c x 16 sq.mm 1.1 KV grade XLPE Insulated FRLS sheathed armoured copper conductor cable | RM | 0 |  | 0
0
n | 4 c x 10 sq.mm 1.1 KV grade XLPE Insulated FRLS sheathed armoured copper conductor cable For UPS DB | RM | 0 |  | 0
0
p | 4 c x 6 sq.mm 1.1 KV grade XLPE Insulated FRLS sheathed armoured copper conductor cable | RM | 0 |  | 0
0
q | 4 c x 4 sq.mm 1.1 KV grade XLPE Insulated FRLS sheathed armoured copper conductor cable | RM | 0 |  | 0
0
s | 4 c x 2.5 sq.mm 1.1 KV grade XLPE Insulated FRLS sheathed armoured copper conductor cable For CS AHU & Hydrogen Exhaust | RM | 0 |  | 0
0
t | 3 c x 10 sq.mm 1.1 KV grade PVC Insulated FRLS Armoured copper conductor cable | RM | 0 |  | 0
0
u | 3 c x 6 sq.mm 1.1 KV grade XLPE Insulated FRLS sheathed armoured copper conductor cable For VRV DB | RM | 20 |  | 0
0
x | 2 c x 10 sq.mm 1.1 KV grade XLPE Insulated FRLS sheathed armoured copper conductor cable For UPS | RM | 25 |  | 0 | 2
0
z | 1c x 6 sq.mm FRLS XLPE insulated flexible copper conductor cables | RM | 0 |  | 0
0
aa | 1c x 10 sq.mm FRLS XLPE insulated flexible copper conductor cables | RM | 0 |  | 0
0
ab | 1c x 16 sq.mm FRLS XLPE insulated flexible copper conductor cables | RM | 0 |  | 0
0
ac | 1c x 25 sq.mm FRLS XLPE insulated flexible copper conductor cables | RM | 0 |  | 0
0
ad | 1c x 35 sq.mm FRLS XLPE insulated flexible copper conductor cables | RM | 0 |  | 0
0
2 | Supplying and making terminal joints for the following size of 1.1 KV PVC insulated copper conductor armoured cables including providing heavy duty tinned copper terminal crimping lugs, solder, insulation tape, approved sealing epoxy compound, double compression brass cable glands, effecting gland connec­tions and effecting terminal connections to the equipment complete as required. Use compression lugs and PG Threaded Nylon Flexible cable glands for single core flexible cables |  |  |  | 0
0
a | 3.5 c x 300 sq.mm1.1 KV grade XLPE Insulated FRLS sheathed armoured aluminium conductor cable | Sets | 0 |  | 0
0
b | 3.5 c x 240 sq.mm1.1 KV grade XLPE Insulated FRLS sheathed armoured aluminium conductor cable | Sets | 0 |  | 0
0
c | 3.5 c x 185 sq.mm1.1 KV grade XLPE Insulated FRLS sheathed armoured aluminium conductor cable | Sets | 0 |  | 0
0
d | 3.5 c x 150 sq.mm1.1 KV grade XLPE Insulated FRLS sheathed armoured aluminium conductor cable | Sets | 0 |  | 0
0
e | 3.5 c x 120 sq.mm1.1 KV grade XLPE Insulated FRLS sheathed armoured aluminium conductor cable | Sets | 0 |  | 0
0
f | 3.5 c x 95 sq.mm1.1 KV grade XLPE Insulated FRLS sheathed armoured aluminium conductor cable | Sets | 0 |  | 0
0
g | 3.5 c x 70 sq.mm1.1 KV grade XLPE Insulated FRLS sheathed armoured aluminium conductor cable | Sets | 0 |  | 0
0
h | 3.5 c x 50 sq.mm1.1 KV grade XLPE Insulated FRLS sheathed armoured aluminium conductor cable | Sets | 2 |  | 0
0
i | 4 c x 35 sq.mm1.1 KV grade XLPE Insulated FRLS sheathed armoured aluminium conductor cable | Sets | 0 |  | 0
0
j | 4 c x 25 sq.mm1.1 KV grade XLPE Insulated FRLS sheathed armoured copper conductor cable | Sets | 6 |  | 0
0
k | 4 c x 25 sq.mm1.1 KV grade XLPE Insulated FRLS sheathed armoured AL conductor cable | Sets | 0 |  | 0
0
l | 4 c x 16 sq.mm1.1 KV grade XLPE Insulated FRLS sheathed armoured aluminium conductor cable | Sets | 0 |  | 0
0
m | 4 c x 16 sq.mm 1.1 KV grade XLPE Insulated FRLS sheathed armoured copper conductor cable | Sets | 0 |  | 0
0
n | 4 c x 10 sq.mm 1.1 KV grade XLPE Insulated FRLS sheathed armoured copper conductor cable For UPS DB | Sets | 0 |  | 0
0
p | 4 c x 6 sq.mm 1.1 KV grade XLPE Insulated FRLS sheathed armoured copper conductor cable for VRV ODUs | Sets | 0 |  | 0
0
q | 4 c x 4 sq.mm 1.1 KV grade XLPE Insulated FRLS sheathed armoured copper conductor cable | Sets | 0 |  | 0
0
s | 4 c x 2.5 sq.mm 1.1 KV grade PVC Insulated FRLS sheathed armoured copper conductor cable | Sets | 0 |  | 0
0
u | 3 c x 6 sq.mm 1.1 KV grade XLPE Insulated FRLS sheathed armoured copper conductor cable | Sets | 2 |  | 0
0
w | 2 c x 16 sq.mm 1.1 KV grade XLPE Insulated FRLS sheathed armoured copper conductor cable | Sets | 0 |  | 0
0
x | 2 c x 10 sq.mm 1.1 KV grade XLPE Insulated FRLS sheathed armoured copper conductor cable | Sets | 2 |  | 0
0
aa | 1c x 10 sq.mm FRLS XLPE insulated flexible copper conductor cables | Sets | 0 |  | 0
0
ab | 1c x 16 sq.mm FRLS XLPE insulated flexible copper conductor cables | Sets | 0 |  | 0
0
ac | 1c x 25 sq.mm FRLS XLPE insulated flexible copper conductor cables | Sets | 0 |  | 0
0
ac | 1c x 35 sq.mm FRLS XLPE insulated flexible copper conductor cables | Sets | 0 |  | 0
0
| TOTAL CARRIED OVER TO SUMMARY |  |  |  | 0
0
E | RACEWAYS AND CABLE TRAYS |  |  |  | 0
| Note :- |  |  |  | 0
0
1 | Fabricating supplying to site of installation, installation on ceiling/ surface 1.6 mm thick M.S. powder coated raceways of height 50 mm and 2.0 mm thick openable cover, totally enclosed, the joints between two lengths of channels or between channel and junction box shall be joined together with 3 mm thick M.S. Powder coated coupler plates to make it dust and water proof. The cost shall including all supporting and fixing accessories including dash fasteners. (Orange colour for data and Blue colour for power) |  |  |  | 0
a | 250 mm (wide) x 50 mm (height) | RM | 0 |  | 0
b | 150 mm (wide) x 50 mm (height) | RM | 10 |  | 0
c | 100 mm (wide) x 50 mm (height) | RM | 25 |  | 0
d | 150 mm (wide) x 150 mm (height) | RM | 0 |  | 0
0
2 | Fabricating supplying to site of installation, in floor including chase cutting of floor,leveling, refilling and making good the same from 1.6 mm thick and 2 mm thick cover pregalvanised MS CRCA sheet, totally enclosed, height 40 mm . The two lengths of raceways shall be fitted with Collars , 50 mm wide, 3 mm thick , press fit type. The raceways shall be clamped to the floor slab with GI clamps , 3mm thick and shall be screwed to the floor slab. The joint between raceway and junction box will be made with GI flexible strip( 3 nos), 3 mm thick, 4 inches long ,15 mm wide which will be nut bolted to the Junction box complete as required etc. |  |  |  | 0
0
a | 300 mm x 300 x 60 mm (height) | Nos. | 0 |  | 0
b | 250 mm x 250 x 60 mm (height) | Nos. | 0 |  | 0
c | 200 mm x 200 x 60 mm (height) | Nos. | 3 |  | 0
d | 150 mm x 150 x 60 mm (height) | Nos. | 7 |  | 0
e | 100 mm x 100 x 60 mm (height) | Nos. | 2 |  | 0
0
3 | Fabricating supplying to site of installation, in floor including chase cutting of floor,leveling, refilling and making good the same from 1.6 mm thick and 2 mm thick cover pregalvanised MS CRCA sheet, totally enclosed, height 40 mm . The two lengths of raceways shall be fitted with Collars , 50 mm wide, 3 mm thick , press fit type. The raceways shall be clamped to the floor slab with GI clamps , 3mm thick and shall be screwed to the floor slab. The joint between raceway and junction box will be made with GI flexible strip( 3 nos), 3 mm thick, 4 inches long ,15 mm wide which will be nut bolted to the Junction box complete as required etc. |  |  |  | 0
0
a | 250 mm (wide) x 40 mm (height) | RM | 0 |  | 0
b | 150 mm (wide) x40 mm (height) | RM | 5 |  | 0
c | 100 mm (wide) x 40 mm (height) | RM | 15 |  | 0
0
5 | Fabricating supplying to site of installation, Junction boxes for floor raceways made from 2 mm thick , with 2.5 mm thick G.I. cover including providing neoprene gaskets between the cover and the junction box, cadmium plated flat/round head screws, height as per site condition,totally enclosed. Proper cutouts shall be made in the side walls for raceway entry wherever required. The junction box shall be all side walls should be welded expect top cover and all side walls shall have suitable size of rectangular knock out holes for taking raceways / conduits as required and not a complete cut out. The top cover should be sealed with M Seal to make it dust and water proof complete as required etc. |  |  |  | 0
0
a | 300 mm x 300 x 50 mm (height) | Nos. | 0 |  | 0
b | 200 mm x 200 x 50 mm (height) | Nos. | 2 |  | 0
c | 150 mm x 150 x 50 mm (height) | Nos. | 6 |  | 0
d | 100 mm x 100 x 50 mm (height) | Nos. | 2 |  | 0
0
6 | Design manufacture , supply and fixing in position the cable trays of the following sizes for supporting 1.1 KV grade armoured/unarmoured aluminium /copper conductor cables. Fabricate the cable trays from perforated 1.6/2mm thick M.S. CRCA sheet duly galvanised with expansion coupler plates duly galvanised, with bolts, washer and nuts. Knock out holes for cable connections as per approved design. The tray should comply with the specification of NEC (National Electric Codes) and NEMA (National Electric Manufacturers Association). The steel should be as per IS:226 and galvanising as per IS :2629/BS 729/ASTM 123. The rate shall also include for supporting steel , fish plates , fixing accessories , nuts bolts, supporting down rods , dash fastener, cutting the RCC etc. complete as required. (the horizontal and vertical bends, T's should be factory fabricated and the rate should include for the same) |  |  |  | 0
0
a | 100 mm wide x 40 mm x 2.0 mm thk | RM | 0 |  | 0
b | 150 mm wide x 40 mm x 2.0 mm thk | RM | 55 |  | 0
c | 300 mm wide x 40 mm x 2.0 mm thk | RM | 0 |  | 0
d | 450 mm wide x 40 mm x 2.0 mm thk | RM | 0 |  | 0
e | 600 mm wide x 40 mm x 2.0 mm thk | RM | 0 |  | 0
0
7 | Design manufacture , supply and fixing in position the Ladder Type cable trays of the following sizes for supporting 1.1 KV grade armoured/unarmoured aluminium /copper conductor cables. Fabricate the cable trays to from Ladder Type 2.0 mm thick M.S. Flat/ Angle iron with bolts, washer and nuts. as per approved design. The tray should comply with the specification of NEC (National Electric Codes) and NEMA (National Electric Manufacturers Association). The steel should be as per IS:226 and galvanising as per IS :2629/BS 729/ASTM 123. The rate shall also include for supporting steel ,jointing fish plates , fixing accessories , nuts bolts, supporting down rods, dash fastener, cutting the RCC etc. complete as required. |  |  |  | 0
0
a | 300 mm wide x 50 mm x 2.0 mm thk | RM | 0 |  | 0
8 | Fabricating ,supplying to site of installation, installation of 500 mm size of 105 mm height mesh type EZ -Electroplated Zinc ( Legrand - Cablofil make ) cable tray including threaded G.I. down rods, dash fasteners , cablofil fixing accesories etc. complete as required. Cablofil make | RM | 0 |  | 0
0
| TOTAL CARRIED OVER TO SUMMARY |  |  |  | 0
0
F | DISTRIBUTION BOARDS |  |  |  | 0
0
1 | Supply,inginstalling ,connecting testing and commissioning of the following double door 1/4 rows vertical type 1.6 mm thick and 1. 4 thick door sheet steel enclosed fully recessed type, TPN Miniature Circuit Breakers Distribution Boards dust proof, verm­in proof, with hinged and lockable doors complete with DP MCB's and inter-connection with copper wire , insulated copper bus bar , cable glands­/conduit entry bushes, bonding to earth and paint­ing. Also provide separate neutral busbar for each phase. Provide separate Earth Links for each phase. Use brass thimbles for connections of all wires. 1 row for single phase and 4 rows for 3 phase. Provide separate 4 way 63 A main neutral link also. The phase busbar links shall be factory pre insulated. |  |  |  | 0
| Note :- The IP rating of the DB should be IP 43 . |  |  |  | 0
| Provide DB charts in laminated sheets in all Distribution Boards |  |  |  | 0
| A4 size SLD to be fixed on all DBs. |  |  |  | 0
0
1 | Light & Power Distribution Board |  |  |  | 0
0
a | 10 Way TPN DB, each phase consisting of 8 Nos. 10/20 AMP SP MCB’s and controlled by one number 100 mA sensitivity 63 AMPS DP RCCB backed up with 1 no 63 Amps 4 pole MCB. For VRV DB | Nos | 0 |  | 0
0
b | 12 Way TPN DB, each phase consisting of 10 Nos. 10/20 AMP SP MCB’s and controlled by one number 100 mA sensitivity 63 AMPS DP RCCB backed up with 1 no 63 Amps 4 pole MCB. | Nos | 0 |  | 0
0
c | 14 Way TPN DB, each phase consisting of 12 Nos. 10/20 AMP SP MCB’s and controlled by one number 100 mA sensitivity 63 AMPS DP RCCB backed up with 1 no 63 Amps 4 pole MCB. For Light & Power DB | Nos | 1 |  | 0
0
d | 12 Way SPN DB, consisting of 8 Nos. 10/20 AMP SP MCB’s and controlled by one number 100 mAsensitivity 63 AMPS DP RCCB backed up with 63 Amps DP MCB as incomer. For VRV DB | Nos | 1 |  | 0
0
2 | UPS Distribution Boards (All MCB's in workstation DB's should be D Curve) |  |  |  | 0
0
a | 12 Way TPN DB, each phase consisting of 10 Nos. 10/20 AMP SP MCB’s and controlled by one number 63 AMPS DP RCCB (100 mA) for each phase and 1 no. 63 amps 4 pole MCB incomer. | Nos.. | 0 |  | 0
0
b | 14 Way SPN DB, consisting of 10 Nos. 10/20 AMP SP MCB’s and controlled by one number 100 mA sensitivity 63 AMPS DP RCCB backed up with 63 Amps DP MCB. | Nos.. | 0 |  | 0
0
c | 12 Way SPN DB, consisting of 10 Nos. 10/20 AMP SP MCB’s and controlled by one number 100 mA sensitivity 63 AMPS DP RCCB backed up with 63 Amps DP MCB. For UPS DB | Nos.. | 1 |  | 0
0
d | 12 Way SPN DB, consisting of 4 Nos. 25/32 AMP DP MCB’s and controlled by one number 100 mA sensitivity 63 AMPS DP RCCB ( 100 mA) for backed up with 63 Amps 4D MCB. The bus bar shall be Twin bus bar. | Nos.. | 0 |  | 0
0
3 | Supply, installation, testing and commissioning of sheet metal with 40 A DP MCB. This shall include cable entry boxes both for incoming and outgoing cable). | Nos. | 1 |  | 0
0
4 | Supply, installation, testing and commissioning of sheet metal weather proof enclosure with 63 A FP RCBO(300mA) This shall include cable entry boxes both for incoming and outgoing cable) For VRV units. The enclosure shall be IP 42. For VRV Out Door units | Nos. | 1 |  | 0
0
5 | Supply, installation, testing and commissioning of sheet metal weatherproof Enclosure with 25/32 A DP MCB. This shall include cable entry boxes both for incoming and outgoing cable). | Nos. | 0 |  | 0
0
6 | Supply, installation, testing and commissioning of sheet metal with 16 A FP MCB. This shall include cable entry boxes both for incoming and outgoing cable). For CS AHU | Nos. | 0 |  | 0
0
| TOTAL CARRIED OVER TO SUMMARY |  |  |  | 0
0
G | SUB DISTRIBUTION PANELS |  |  |  | 0
0
1 | Sub Distribution Panels |  |  |  | 0
| Design, manufacture, supplying & installing at site in positioning, connecting, testing and commissioning of the following cubical type, dead front, 2mm thick sheet steel enclosed, free standing indoor type extendible Sub Distribution Panel with vermin proof hinged lockable doors for each compartment provide bus bar interconnections for incoming and outgoing including feeders earthing and painting and as per specifications. |  |  |  | 0
Note | Provide insulated dedicated earth link in all UPS Panels |  |  |  | 0
| All MCCB's 200 Amps and above shall be Microprocessor based |  |  |  | 0
| All Light & Power panel ,UPS and A.C. Panel incomer MCCB shall have Over current, Earth fault and short circuit protection. |  |  |  | 0
| All Incomer MCCB's in UPS Panels shall be Microprocessor based |  |  |  | 0
| The microprocessor based MCCBs shall have |  |  |  | 0
| Over Load (Phase) |  |  |  | 0
| Current setting Ir(Ir=XIn) OFF 0.4 to 1.0 in steps of 0.1 |  |  |  | 0
| Time delay , tr( Inverse) 10 sec at 6/r |  |  |  | 0
| Over Load (Neutral) |  |  |  | 0
| Current setting In (Intrl =XIr) 0.5, 0.75&1.00 Intrl |  |  |  | 0
| Inverse 10 sec at 6 Intrl/Fixed 200ms |  |  |  | 0
| Short Circuit setting -2- 10 |  |  |  | 0
| Instantaneous - 1.5-1 |  |  |  | 0
| All MCB's in UPS Panels shall be D Curve |  |  |  | 0
| In all Electrical panels protective acrylic sheet to be provided in cable alley and feeders. |  |  |  | 0
| The meters shall be able to monitor all major power quality parameters Voltage , current , frequency , KVAH,KWH,Power factor and individual,harmonics, ethernet ready - IEC-625-22. |  |  |  | 0
| The ATS shall be 4 pole with inbuilt manual operating switch. In case the controller of the ATS fails it should be capable of transferring the load while the ATS is in maintenance. The ATS and controller should be same make |  |  |  | 0
| Provide On / Off and trip indicating lamp on main incomer only. |  |  |  | 0
| Panel construction shall be Form 3b for all Panels with MCCB outgoings and Form 2b for all Panels with MCB's outgoings. |  |  |  | 0
| The Earth fault release/relay and CBCTs shall be same make as OEM Switchgear been used in the Panels. It shall not trip on imbalance of load. |  |  |  | 0
| All meters shall have Modbus card for BMS connectivity |  |  |  | 0
| All the Electrical Panels shall be in accordance with IS 8623 standards |  |  |  | 0
0
a | The SDB L&P shall consists of : |  |  |  | 0
0
| MAIN INCOMER |  |  |  | 0
| 1 Nos. 100 A TPN MCCB (25KA/1 sec)( O/C, S/C,E/F) and neutral isolation link 100% of rated current. Terminals suitable to receive 3.5c x 50 sq. mm . Al Ar cable connection on one side and Busbar connection on the other side. |  |  |  | 0
0
| BUSBAR |  |  |  | 0
| 150 amps 4P busbar chamber of suitable length with Aluminium busbars. All busbars and interconnections shall be of suitable size aluminium strips current density of aluminium shall not be more than 0.8 Amps/ sq.mm.provide 100% capacity for neutral bus bar. |  |  |  | 0
0
| INDICATING PANELS |  |  |  | 0
| 3 nos phase indicating lamps (LED type) each backed up with MCB and switch shall be provided for each incomer. |  |  |  | 0
| Provide Intelligent Panel Meter - multifunctional meter with RS485 for all incoming feeder |  |  |  | 0
| Provide Transient Voltage Surge Suppressor Rating 40kA class II along with 63 A MCCB. Including all necessary accessories. For Switching Operation on each incomer. |  |  |  | 0
| Provide earth fault protection (EF) in the incomer MCCB |  |  |  | 0
0
| OUTGOINGS |  |  |  | 0
| 4 Nos. 63 A 4P MCB (10 kA/ 1 sec) terminal to receive suitable Cable on one side and Busbar connection on the other side. |  |  |  | 0
| 2 Nos. 40/32 A DP MCB (10 kA/ 1 sec) terminal to receive suitable Cable on one side and Busbar connection on the other side. |  |  |  | 0
0
| The SDB L&P as described above and specifications complete | Set | 1 |  | 0
0
2 | The contractor to submit reports of torque tightness tests for all the nut bolt cable joints in all the panels with red marking after the torque tightening has been done as per manufactures recommendation. | Set | 0 |  | 0
0
3 | Providing & fixing in position 1000 mm wide , Electrical Insulating Mats as per IS 15652:2006, 2mm thick, suitable up to 3.3 KV , fire retardant,no effect of acids, alkalies and transformer oils, moisture proof, high tensile strength and texture finish / cloth impression (Anti slip , marking on top) . | RM | 3 |  | 0
0
4 | Replacement of existing 250 A tap off box with 400 A tap off box at site with all the necessary accessories complete as required. | Nos. | 0 |  | 0
0
5 | Supply & fixing in position approved shock treatment chart written in English, Hindi and Local language. These charts shall be framed in wooden frame & covered with clear glass. | Nos. | 1 |  | 0
0
6 | Supply & fixing in position the best quality danger notice boards of approved shape & size as reqd. by the local Electrical Inspecting Authority written in English, Hindi & local language. | Nos. | 1 |  | 0
0
7 | Supply & fixing in position the Electrical A 1 Size SLD chart in the UPS/electrical room . These charts shall be framed in wooden frame & covered with clear glass. | Nos. | 1 |  | 0
0
8 | Supplying the first aid box as approved by John Ambulance society. | Nos. | 1 |  | 0
0
9 | Supply & Fixing of NO/NC Relay Module complete as required. | Nos. | 0 |  | 0
0
10 | 2 core -1.5 sq.mm PVC FRLS wires in already laid suitable size of M.S conduit complete as required. | Rmt | 0 |  | 0
0
11 | Supply, Installations, Testing and Commissioning of 2 Kg Fire Suppression System (CQRS) in all Floor Panels of Electrical and UPS Room to be included. - Automatic Direct Low Pressure Fire Suppression System, UL Listed FK-5-1-12 Extinguishing Fluid shall be filled in UL Listed Cylinder, UL Listed Pressure Switch should be integrated in DLP Valve for Indication on Fire Suppression Panel and Main Fire Alarm System, 15 Meter UL Listed Detection Tube shall be UV Protected made of Modified Polyamide associated with End of Line Adapter with Pressure Gauge, master Control Panel with A/V Alarm and Battery Backup along with Potential Free Contact to integrate with existing Fire Alarm System for Central Monitoring. Mounting Bracket with all necessary accessories. complete in all respect. System Component Approval: Cylinder-UL Listed, Gas-UL Listed, Detection Tube-UL Listed, Pressure Switch-UL Listed Make: FireMech / Ceasefire / Honeywell | Nos. | 0 |  | 0
0
| TOTAL CARRIED OVER TO SUMMARY |  |  |  | 0

## Light FixturesB2
Sl.No. | Description | Unit |  | Supply & Installation
|  |  | Qty | Rate In Rs. | Amount in Rs.
H | SUPPLY & INSTALLATION OF LIGHTING FIXTURES |  |  |  |  | *Quoted Installation
1 | Supply & Fixing in position testing and commissioning of the following Lighting fixtures at site including all type of fixing accessories complete as required etc. Use all light fixture shall be LED Type. (Samples of all light fixtures to be submitted to the client/architect/consultant for approval prior to procurement of fixtures) |  |  |  | 0
0
a | 32 Watts LED 600x600mm panel LED light as per approved make. | Nos | 0 |  | 0
0
b | 32 Watts LED 600x600mm panel LED Fire Proof light as per approved make.(Fire proof for Bonded store) | Nos | 0 |  | 0
0
c | 15 watts Suspended Cylindrical LED light as per approved make. | Nos | 0 |  | 0
0
d | Suspended Channel LED light (90x1500) at Cabins as per approved make | Nos | 0 |  | 0
0
e | Suspended Channel LED light (90x750) at Reception as per approved make | Nos | 0 |  | 0
0
f | 13 wattts Surface Mounted LED Down light as per approved make | Nos | 0 |  | 0
0
g | 13 wattts Recessed LED Down light as per approved make | Nos | 25 |  | 0
0
2 | Supply, Installation, Testing & Commissioning of 3 Watts LED Ni Cd Battery backup up to 1.5 hr emergency Exit light Prolite or equivalent make. The sample shall be submitted before ordering. or Equivalent make. | Nos | 3 |  | 0
0
3 | Supply, installation, testing commissioning of recessed ceiling mounted photo cell switching units to provide ON/OFF switching of lighting in response to ambient light levels. | Nos | 0 |  | 0
0
4 | Supply & installation of Passive infra-red presence detector for lighting control to set the parameters of all meeting rooms and cabin (ON/OFF selection of lights)( Lights switch OFF in steps of 1 minute) | Nos | 0 |  | 0
a | Switches lighting OFF when sufficient daylight is present. |  |  |  | 0
b | Used as on ON/OFF daylight dependant switch or in series with a wall switch |  |  |  | 0
c | Lighting level adjustable up to 1500 lux approx. |  |  |  | 0
0
| TOTAL CARRIED OVER TO SUMMARY |  |  |  | 0

## Elect B3
Sl.No. | Description | Unit |  | Supply & Installation
|  |  | Qty | Rate In Rs. | Amount in Rs.
A. | POINT WIRING
All wires shall be FRLS PVC insulated copper conductor. Point wiring rates are inclusive of 3 x 1.5 sq mm insulated copper conductor wires for circuit.(from DB to switch board).
All sockets to be checked with a Check Plug socket tester for live-neutral reverse, no earth,neutral fault, live earth reverse, neutral earth reverse.
The Circuit No. and DB no. label shall be provided on all UPS ,RAW sockets and switchboards with label printer.
Colour coding for conduits to be done for different systems. The whole length of conduits to be painted.
All circuit & point wiring shall be colour coded & shall have ferruling on both end for circuit identification complete as required etc.Labelling on all the switches and sockets to be done with respect to DB reference, phase and circuit no.
Earth loop Impedance Test to be performed. RCD test to be done. Cable Insulation Tests to be done.
Wherever the occupancy sensor is provided in the cabin/ meeting rooms/workstations , the circuit wires from Distribution Board to occupancy sensor and sensor to switch are inclusive in the point wiring rate.
Labeling of all sockets and emergency lights to be provided and Ferruling for all the circuits to be considered
1 | Wiring for the following light points with 3x1.5 Sq.mm FRLS PVC insulated stranded copper conductor wires in concealed M.S. conduits in F.ceiling/walls/ceiling as directed including providing and fixing of 6 amps flush type switches, 5 sided G.I Boxes for housing switc­hes and earth­ing complete as required. Rates are inclusive of 3 x 1.5 sq mm FRLS PVC insulated stranded copper conductor wires for circuit |  |  |  | 0
0
a. | First point controlled by one no. 6 amp switch. | Nos. | 35 |  | 0
0
2 | Same as item No. 1a above but LOOP POINT i.e. wiring of point looped from first point with 3 x 1.5 sq. mm FRLS PVC insulated copper conductor wire in concealed/exposed MS conduit and earthing | Nos. | 63 |  | 0
0
3 | Wiring for the following light points with 1.5 Sq.mm FRLS PVC insulated stranded copper conductor wires in concealed M.S. conduits in F.ceiling/walls/ceiling as direc­ted including providing and fixing of 6 amps flush type switches, 5 sided G.I Boxes for housing switc­hes and earth­ing comple­te as required. Rates are inclusive of 3 x 1.5 sq mm FRLS PVC insulated stranded copper conductor wires for circuit |  |  |  | 0
0
a. | First point controlled by one no. 16 amp switch. | Nos. | 0 |  | 0
0
4 | Wiring for the following light points controlled by MCB in DB (Cost of MCB has been taken elsewhere in the tender) with 3 x 1.5 sq. mm FRLS PVC insulated copper conductor wires in concealed/exposed M.S. conduits as called for and earthing. |  |  |  | 0
0
a. | First point controlled by existing MCB in D.B. To first light Em Light | Nos. | 3 |  | 0
0
5 | Same as item No. 4.a above but LOOP POINT i.e. wiring of point looped from first point with 3x1.5 sq. mm FRLS PVC. insulated copper conductor wire in concealed/exposed M.S. conduit and earthing | Nos. | 27 |  | 0
0
6 | SITC of 2C x 1.5 sq mm non shielded Cable for DALI Ballast wiring in 25 mm dia MS conduit with all fixing accessories complete as required | Rmt. | 0 |  | 0
0
7 | SITC of 4C x 1.5 sq mm shielded Cable for QSM wiring in suitable size of MS conduit with all fixing accessories complete as required. Cable Common – 12 AWG (4.0 mm2); Power – 12 AWG (4.0 mm2); MUX Data – 22 AWG (0.25 mm2); Data – 22 AWG (0.25 mm2); Sense Line – 18 AWG (0.75 mm2); Drain Wire – 24 AWG (0.2 mm2) | Rmt. | 0 |  | 0
0
8 | Wiring for 6/16 amps outlets with 3 X 2.5 sq.mm FRLS PVC insulated copper conductor wires in M.S. Conduits in ceiling/walls/floor as direc­ted incl­u­ding providing & fixing of 6/16 amps flush type 5 pin socket and 16 amps switch with cover plate, 5 sided G.I boxes for housing switches, sockets and earthi­ng complete as required. (for general areas 4 nos loop in one circuits) | Nos. | 11 |  | 0
0
9 | Wiring for inline fan points with 2 x 2.5 sq.mm FRLS PVC insulated stranded copper con­ductor wires in concealed M.S. conduits in F.ceiling/ walls/ Ceiling as directed including providing and fixing of 16 amps flush type switches 16 amps 3 pin socket near inline fan, 5 sided G.I. boxes for housing switches and 16 amps 3 pin socket outlet and earthing and complete as required.(including body earth for GI boxes) | Nos. | 7 |  | 0
0
10 | Wiring for Geyser/Projector/Hand Dryer points with 2 x 4 + 1 x 4 sq mm FRLS PVC insulated copper conductor wires in concealed M.S. conduits in F.ceiling/ walls/ Ceiling as directed including providing & fixing 16 amps flush type switch near the white board and 6/16 amps 6 pin socket near the projector in ceiling , 5 sided G.I. boxes for housing switches and 6/16 A 6 pin socket outlet , earthing and complete as required.(including body earth for GI boxes) ( 1 point per circuit) | Nos. | 12 |  | 0
0
11 | Wiring for VRV Indoor units with 3 x 2.5 sq.mm FRLS PVC insulated stranded copper conductor wires in concealed M.S. conduits in F.ceiling/ walls/ Ceiling as directed including providing providing and fixing of 6 amps flush type switches 16 amps 3 pin socket near VRV points, 5 sided G.I. boxes for housing switches and 16 amps 3 pin socket outlet and earthing and complete as required.(including body earth for GI boxes) (1 point per circuit) | Nos. | 8 |  | 0
0
12 | Wiring for VAV /fire damper points with 3 x 2.5 sq.mm FRLS PVC insulated copper conductor wires in concealed M.S. conduits in F.ceiling/ walls/ Ceiling as directed including providing & fixing 6 amps flush type switches, 6 amps 3 pin socket near VAV points, 5 sided G.I. boxes for housing switches and 6 A sockets earthing and complete as required. The sockets to be fused spur type (MK make). (including body earth for GI boxes) (8 to 10 points per circuits) | Nos. | 0 |  | 0
0
13 | Wiring for 16 amps power outlet poi­nts with 4 sq.mm FRLS PVC insulated stranded copper conductor wires in concealed/recessed M.S. conduit as directed including providing providing and fixing of 16 amps flush type switch and 6 pin socket with cover plate 5 sided G.I. outlet boxes for switches and socket and earthing the third pin with 2.5 sq mm FRLS PVC stranded copper wire complete as required (Only one outlet shall be connected on each circuit) (including body earth for GI boxes) | Nos. | 14 |  | 0
0
14 | Wiring for 16 amps power outlet points with 4 sq.mm FRLS PVC insulated stranded copper conductor wires for the first power outlet and 4 sq.mm FRLS PVC insu­lated stranded copper conductor wires for the second outlet, in concealed M.S. cond­uits in F.ceiling/ walls/Ceiling/floor ducts as directed including providing providing and fixing of 16 amps flush type switch and 6 pin socket with cover plate, 5 sided G.I. outlet boxes for housing switches and socket, and earthing the third pin with 2.5 sq.mm FRLS PVC insulated copper conductor wires complete as required (Two power out­lets shall be connected on each circuit)(including body earth for GI boxes) | Set of Two | 5 |  | 0
0
15 | Wiring for A/C outlet points with 4.0 sq mm FRLS PVC insulated stranded copper conductor wires in M.S. conduitl/wall/floor ducts as directed including providing 25 A socket with 25 amps SP MCB ( Tiny Trip) 5 sided GI Outlet Box for housing and socket and MCB and earthing with 2.5 sq. mm FRLS PVC insulated stranded Copper Conductor wires complete as required. | Nos. | 0 |  | 0
0
| Different colours to be used for 3 core cables for raw power and UPS power. |  |  |  | 0
16 | Wiring for UPS/Raw plug outlets points with three core, 2.5 sqmm FRLS PVC Insulated and PVC sheathed flexible cable with bright annealed electrolytic copper conductor, 1100 volt grade confirming to IS : 694-1990 with latest amendments, in existing Channels/ conduit in ceiling/walls/floor including all cable termination accessories) (including body earth for GI boxes). Colour Coding to be followed | RM | 550 |  | 0
0
17 | Wiring for UPS/Raw plug outlets points with three core, 4.0 sqmm FRLS PVC Insulated and PVC sheathed flexible cable with bright annealed electrolytic copper conductor , 1100 volt grade confirming to IS : 694-1990 with latest amendments, in existing Channels/ conduit in ceiling/walls/floor inclu­ding all cable termination accessories) Earthing of GI Box to be included. Colour Coding to be followed. For Lab & Kitchen Sockets | RM | 560 |  | 0
0
18 | Wiring for Power plug outlets points with three core, 6.0 sqmm FRLS PVC Insulated and PVC sheathed flexible cable with bright annealed electrolytic copper conductor , 1100 volt grade confirming to IS : 694-1990 with latest amendments, in existing Channels/ conduit in ceiling/walls/floor inclu­ding all cable termination accessories). Colour Coding to be followed. | RM | 70 |  | 0
0
19 | Wiring for Power plug outlets points with three core, 10.0 sqmm FRLS PVC Insulated and PVC sheathed flexible cable with bright annealed electrolytic copper conductor , 1100 volt grade confirming to IS : 694-1990 with latest amendments, in existing Channels/ conduit in ceiling/walls/floor inclu­ding all cable termination accessories). Colour Coding to be followed. | RM | 0 |  | 0
0
20 | Wiring for Power plug outlets points with four core, 6.0 sqmm FRLS PVC Insulated and PVC sheathed flexible cable with bright annealed electrolytic copper conductor , 1100 volt grade confirming to IS : 694-1990 with latest amendments, in existing Channels/ conduit in ceiling/walls/floor inclu­ding all cable termination accessories). Colour Coding to be followed. | RM | 75 |  | 0
0
21 | Wiring for Power plug outlets points with four core, 10.0 sqmm FRLS PVC Insulated and PVC sheathed flexible cable with bright annealed electrolytic copper conductor , 1100 volt grade confirming to IS : 694-1990 with latest amendments, in existing Channels/ conduit in ceiling/walls/floor inclu­ding all cable termination accessories). Colour Coding to be followed. | RM | 40 |  | 0
0
| The word UPS shall be printed on all UPS sockets. |  |  |  | 0
| The word RAW shall be printed on all RAW sockets. |  |  |  | 0
| The Circuit No. and DB no. label shall be provided on all UPS ,RAW sockets and switchboards with label printer. |  |  |  | 0
| Contractor is required to submit samples of all types of switches and sockets to Consultant and Architects representative for approval before ordering the material. |  |  |  | 0
0
20 | Providing and fixing of 1 Nos. 6 amp round pin type socket and 1 No. 6 amps switch cover plate, 5 sided G.I. Boxes for housing switches and sockets and earthing complete as required (for UPS/Raw). GI Box to have earth pin for body earthing | Nos. | 32 |  | 0
0
21 | Providing and fixing of 2 Nos. 6 amp round pin type socket and 1 No. 6 amps switch cover plate, 5 sided G.I. Boxes for housing switches and sockets and earthing complete as required (for UPS/Raw). GI Box to have earth pin for body earthing | Nos. | 20 |  | 0
0
22 | Providing and fixing of 3 Nos. 6 amp round pin type socket and 1 No. 6 amps switch cover plate, 5 sided G.I. Boxes for housing switches and sockets and earthing complete as required (for UPS/Raw). GI Box to have earth pin for body earthing | Nos. | 2 |  | 0
0
23 | Providing and fixing of 2 Nos. 6/16 amp round pin type socket and 1 No. 16 amps switch cover plate, 5 sided G.I. Boxes for housing switches and sockets and earthing complete as required (for UPS/Raw). GI Box to have earth pin for body earthing | Nos. | 2 |  | 0
0
24 | Providing and fixing of 1 No.16 amps flush type 6 pin socket and 1 No. 16 amps switch with indicator, cover plate, 5 sided G.I. Boxes for housing switches and sockets and earthing complete as required (for UPS / RAW) GI Boxes to have earth pin for body earthing | Nos. | 2 |  | 0
0
25 | Providing and fixing Underfloor Access Outlets (250 x 250 x 55 - mm 70 compartments 1Trap including providing 2 Nos 6 Amps Round Pin sockets and 1 no. 16 Amp Switch & 2 data outlet complete as required. | Nos. | 0 |  | 0
0
26 | Supply and fixing of the following sizes of thermoplastic moulded plug and socket IEC 309 type in PVC Box of suitable size flush / surface and making connections complete as required. The box shall be IP 44. |  |  |  | 0
a | 3 pin 16/20 A 1 phase industrial socket with mcb & plug top | Nos. | 0 |  | 0
b | 3 pin 32 A 1 phase industrial socket plug top | Nos. | 0 |  | 0
0
27 | For Kitchen Equipments the degree of protection shall be- IP-67 |  |  |  | 0
0
a | 3 pin 25/20 /16 A 1 phase industrial socket with mcb & plug IP 67 | Nos. | 15 |  | 0
b | 3 pin 32 A 1 phase industrial socket with mcb & plug IP 67 | Nos. | 2 |  | 0
c | 5 pin 32 A 3 phase industrial socket with mcb & plug IP 67 | Nos. | 2 |  | 0
d | 5 pin 40 A 3 phase industrial socket with mcb & plug IP 67 | Nos. | 1 |  | 0
e | 5 pin 63 A 3 phase industrial socket with mcb & plug IP 67 | Nos. | 0 |  | 0
0
28 | Providing and fixing in position the following M.S. conduits including all accessories concealed in F. ceiling/wall/floor as required including 1.6 mm thick M.S. junction or pull boxes with 3mm thick perspex sheet cover plate compl­te with 1.6 mm dia. G.I. pull wires in the length of conduit. |  |  |  | 0
0
a. | 20 mm dia conduit ( 1.6 mm thick) | RM | 80 |  | 0
b. | 25 mm dia conduit (1.6 mm thick) | RM | 150 |  | 0
c. | 32 mm dia conduit (2.0 mm thick) | RM | 95 |  | 0
0
29 | The Electrical Contractor shall provide sufficient temporary lighting for working in the Building total area 5780 sq. ft. divided in single floor and maintain the same till completion of the project.It shall include replacement of all fused/faulty lamps.It shall include providing 15 A plug sockets (industrial type with ON/OFF switch/MCB) on 4 sides walls one plug at every 5-8 meter distance. The Contractors will tap off supply from these plugs for his use. Tubelights to maintain a lighting level of 150 lux on the floor,.Each 15 A socket and each Light circuit shall be protected by suitable MCBs.Use three core PVC Insulated PVC sheathed copper conductor cables for wiring.The contractor shall salvage the complete wiring and take it back at the end of the project. | L.S. | 1 |  | 0
0
| TOTAL CARRIED OVER TO SUMMARY |  |  |  | 0
0
B. | CONDUITING FOR TELEPHONE , COMPUTER & CONDUITING AND WIRING FOR T.V. SYSTEM. |  |  |  | 0
0
1 | Providing and fixing in position the following M.S. conduits including all accessories concealed in F. ceiling/wall/floor as required including 1.6 mm thick M.S. junction or pull boxes with 3mm thick perspex sheet cover plate compl­te with 1.6 mm dia. G.I. pull wires in the length of conduit. |  |  |  | 0
0
a. | 20 mm dia conduit( 1.6 mm wall thickness) | RM | 85 |  | 0
b. | 25 mm dia conduit ( 1.6 mm wall thickness) | RM | 160 |  | 0
c. | 32 mm dia conduit ( 1.6 mm wall thickness) | RM | 100 |  | 0
0
2 | Providing and fixing in position suitable 1.2 mm thick G.I./ PVC outlet box for RJ- 45 computer outlet with all fixing accessories as required. | Nos. | 10 |  | 0
0
3 | Supply and fixing of 1.2 mm thick G.I Box along with RG 11 TV Co axial socket with Cover Plate | Nos. | 1 |  | 0
0
4 | Supply drawing connecting testing and commissioning of TV Coaxial cable RG 6 in existing conduit | RM | 70 |  | 0
0
| TOTAL CARRIED OVER TO SUMMARY |  |  |  | 0
0
C. | EARTHING |  |  |  | 0
0
1 | Providing and fixing in position the following copper strips and wires including providing all fixing accessories and effecting proper connections |  |  |  | 0
| Note:- MS Cable markers at the earth bus, panel and DB entries to be provided |  |  |  | 0
a. | G.I. tape 25 mm x 6 mm | RM | 240 |  | 0
b. | Copper tape 25mm x 3 mm | RM | 0 |  | 0
c. | GI wire 8 SWG | RM | 150 |  | 0
d. | GI wire 12 SWG | RM | 100 |  | 0
e. | Supply installation , and making of Exothermic weld suitable to bond GI strip of 25x5 mm with Copper Strip of 25x5 mm with 75mm extensions on either side | Nos. | 0 |  | 0
f. | Copper Earth Link connectors - 200 mm long, 25mm wide and 5 mm thick | Nos. | 0 |  | 0
0
2 | Supply and laying, effecting proper connec­tions, testing & commissioning of the following sizes of 1.1 KV armoured XLPE/ unarmoured FRLS sheathed XLPE insulation, conforming to IS: 7098 (Part-1)- 1988 ( 90 deg C) aluminium /copper conductor cables conforming to IS : 1554 and FRLS Insulated flexible copper cables as per IS 694 laid over MS supports in existing RCC ducts/ laid in ground /laid on Cable Trays including clamping the cables to sup­ports in an approved manner as required complete with all accessories. |  |  |  | 0
0
a | 1c x 50 sq.mm FRLS insulated flexible copper conductor cables | RM | 0 |  | 0
0
b | 1c x 35 sq.mm FRLS insulated flexible copper conductor cables | RM | 0 |  | 0
0
c | 1c x 25 sq.mm FRLS insulated flexible copper conductor cables | RM | 0 |  | 0
0
d | 1c x 16 sq.mm FRLS insulated flexible copper conductor cables | RM | 0 |  | 0
0
e | 1c x 10 sq.mm FRLS insulated flexible copper conductor cables | RM | 70 |  | 0
0
f | 1c x 6 sq.mm FRLS insulated flexible copper conductor cables | RM | 40 |  | 0
0
g | 2 Nos 1 x 10 Sq. mm FRLS insulated flexible copper conductor cables (Green Colour for UPS DB Sub-main Earthing) | RM | 0 |  | 0
0
3 | Supplying and making of end termination for the following size of compression lugs and PG Threaded Nylon Flexible cable glands complete with all fixing accessories as required |  |  |  | 0
0
a | 1c x 50 sq.mm FRLS insulated flexible copper conductor cables | Sets | 0 |  | 0
0
b | 1c x 35 sq.mm FRLS insulated flexible copper conductor cables | Sets | 0 |  | 0
0
c | 1c x 25 sq.mm FRLS insulated flexible copper conductor cables | Sets | 0 |  | 0
0
d | 1c x 16 sq.mm FRLS insulated flexible copper conductor cables | Sets | 0 |  | 0
0
d | 1c x 10 sq.mm FRLS insulated flexible copper conductor cables | Sets | 6 |  | 0
0
4 | Providing earthing station at loca­tion as called for including provid­ing 600 mm x 600 mm x 3 mm thick tinned copper electrode 2 Nos 25 x 3 mm copper strip (for body earthing GI strip can be considerd) up to ground level 20mm dia medium class GI pipe (India Tube Company make or approved equal) CI funnel with 20 gauge GI wire mesh, masonry chamber with concrete base, CI man­hole cover (cover to be heavy duty) with frame (300mm x 300mm) and bitumastic paint and packing the fixture of charcoal and common salt around plate electrode complete as per I.S. ( Minimum depth shall be 4.2 M ) for UPS & Server | Nos. | 0 |  | 0
0
5 | Supply, Installation, testing and commissioning of Maintenance Free Earthing of make Electrolytic Earthing comprising of type 'K' copper 2.4 mm wall thickness, hollow tube 10 feet long, 2.125 inches outer diameter completely filled with non hazardous metallic salts (Terrafill) to achieve an earth resistance of less than 1 ohms. Provide masonry chamber with concrete base, CI man­hole cover (cover to be heavy duty) with frame (300mm x 300mm) and make earth pit sign/ identifcation no in each earth station for UPS & Server | Nos. | 1 |  | 0
0
6 | Supply, installation, testing and commissioning of sheet metal enclosed 450 x 200 x 150 (D) mm insulated earth distribution board with 1 nos. 50 x 6 mm copper tinned earth bars on SMC insulator suitable for 6/8 nos connections complete with all fixing accessories as required. | Nos. | 0 |  | 0
0
7 | Supply, installation, testing and commissioning of sheet metal enclosed 300 x 200 x 150 ( D) mm insulated earth distribution board with 1 nos. 32 x 6 mm copper tinned earth bars on SMC insulator suitable for 6/8 nos connections complete with all fixing accessories as required. | Nos. | 2 |  | 0
0
8 | Supplying and laying of the following sizes of Heavy duty PVC Pipes below paved area including chase cutting and back filling. |  |  |  | 0
a. | 100 mm outer dia | RM | 0 |  | 0
b. | 80 mm outer dia | RM | 10 |  | 0
0
| TOTAL CARRIED OVER TO SUMMARY |  |  |  | 0
0
D | CABLES, MAINS & SUBMAINS |  |  |  | 0
0
1 | Supply and laying, effecting proper connec­tions, testing & commissioning of the following sizes of 1.1 KV armoured XLPE/ unarmoured FRLS sheathed XLPE insulation, conforming to IS: 7098 (Part-1)- 1988 ( 90 deg C) aluminium /copper conductor cables conforming to IS : 1554 and FRLS Insulated flexible copper cables as per IS 694 laid over MS supports in existing RCC ducts/ laid in ground /laid on Cable Trays including clamping the cables to sup­ports in an approved manner as required complete with all accessories. |  |  |  | 0
0
| Note : All cables to be glanded and crimped with suitable sized lugs. All Cable trays to be double earthed. All raceways and cable glands to be earthed with brass round earth clips and wires. |  |  |  | 0
| Earthing ring to be included in all the cable glands. |  |  |  | 0
| Sub main cables should be labelled at both ends |  |  |  | 0
| Joints shall be allowed only at the 2 ends of the cables and not in between. |  |  |  | 0
0
a | 3.5 c x 300 sq.mm1.1 KV grade XLPE Insulated FRLS sheathed armoured aluminium conductor cable | RM | 0 |  | 0
0
b | 3.5 c x 240 sq.mm1.1 KV grade XLPE Insulated FRLS sheathed armoured aluminium conductor cable | RM | 0 |  | 0
0
c | 3.5 c x 185 sq.mm1.1 KV grade XLPE Insulated FRLS sheathed armoured aluminium conductor cable | RM | 0 |  | 0
0
d | 3.5 c x 150 sq.mm1.1 KV grade XLPE Insulated FRLS sheathed armoured aluminium conductor cable | RM | 0 |  | 0
0
e | 3.5 c x 120 sq.mm1.1 KV grade XLPE Insulated FRLS sheathed armoured aluminium conductor cable For SDB L&P (Assumed) | RM | 60 |  | 0
0
f | 3.5 c x 95 sq.mm1.1 KV grade XLPE Insulated FRLS sheathed armoured aluminium conductor cable | RM | 0 |  | 0
0
g | 3.5 c x 70 sq.mm1.1 KV grade XLPE Insulated FRLS sheathed armoured aluminium conductor cable | RM | 0 |  | 0
0
h | 3.5 c x 50 sq.mm1.1 KV grade XLPE Insulated FRLS sheathed armoured aluminium conductor cable For Kitchen Panel | RM | 50 |  | 0
0
i | 4 c x 35 sq.mm1.1 KV grade XLPE Insulated FRLS sheathed armoured aluminium conductor cable | RM | 0 |  | 0
0
j | 4 c x 25 sq.mm1.1 KV grade XLPE Insulated FRLS sheathed armoured aluminium conductor cable For DB and VRV ODU | RM | 185 |  | 0
0
k | 4 c x 25 sq.mm1.1 KV grade XLPE Insulated FRLS sheathed armoured copper conductor cable | RM | 0 |  | 0
0
l | 4 c x 16 sq.mm1.1 KV grade XLPE Insulated FRLS sheathed armoured aluminium conductor cable | RM | 0 |  | 0
0
m | 4 c x 16 sq.mm 1.1 KV grade XLPE Insulated FRLS sheathed armoured copper conductor cable For UPS DB | RM | 0 |  | 0
0
n | 4 c x 10 sq.mm 1.1 KV grade XLPE Insulated FRLS sheathed armoured copper conductor cable | RM | 0 |  | 0
0
p | 4 c x 6 sq.mm 1.1 KV grade XLPE Insulated FRLS sheathed armoured copper conductor cable | RM | 0 |  | 0
0
q | 4 c x 4 sq.mm 1.1 KV grade XLPE Insulated FRLS sheathed armoured copper conductor cable | RM | 65 |  | 0
0
s | 4 c x 2.5 sq.mm 1.1 KV grade XLPE Insulated FRLS sheathed armoured copper conductor cable | RM | 0 |  | 0
0
t | 3 c x 10 sq.mm 1.1 KV grade PVC Insulated FRLS Armoured copper conductor cable | RM | 0 |  | 0
0
u | 3 c x 6 sq.mm 1.1 KV grade XLPE Insulated FRLS sheathed armoured copper conductor cable | RM | 0 |  | 0
0
x | 2 c x 10 sq.mm 1.1 KV grade XLPE Insulated FRLS sheathed armoured copper conductor cable For UPS DB | RM | 45 |  | 0
0
z | 1c x 6 sq.mm FRLS XLPE insulated flexible copper conductor cables | RM | 0 |  | 0
0
aa | 1c x 10 sq.mm FRLS XLPE insulated flexible copper conductor cables | RM | 0 |  | 0
0
ab | 1c x 16 sq.mm FRLS XLPE insulated flexible copper conductor cables | RM | 0 |  | 0
0
ac | 1c x 25 sq.mm FRLS XLPE insulated flexible copper conductor cables | RM | 0 |  | 0
0
ad | 1c x 35 sq.mm FRLS XLPE insulated flexible copper conductor cables | RM | 0 |  | 0
0
2 | Supplying and making terminal joints for the following size of 1.1 KV PVC insulated copper conductor armoured cables including providing heavy duty tinned copper terminal crimping lugs, solder, insulation tape, approved sealing epoxy compound, double compression brass cable glands, effecting gland connec­tions and effecting terminal connections to the equipment complete as required. Use compression lugs and PG Threaded Nylon Flexible cable glands for single core flexible cables |  |  |  | 0
0
a | 3.5 c x 300 sq.mm1.1 KV grade XLPE Insulated FRLS sheathed armoured aluminium conductor cable | Sets | 0 |  | 0
0
b | 3.5 c x 240 sq.mm1.1 KV grade XLPE Insulated FRLS sheathed armoured aluminium conductor cable | Sets | 0 |  | 0
0
c | 3.5 c x 185 sq.mm1.1 KV grade XLPE Insulated FRLS sheathed armoured aluminium conductor cable | Sets | 0 |  | 0
0
d | 3.5 c x 150 sq.mm1.1 KV grade XLPE Insulated FRLS sheathed armoured aluminium conductor cable | Sets | 0 |  | 0
0
e | 3.5 c x 120 sq.mm1.1 KV grade XLPE Insulated FRLS sheathed armoured aluminium conductor cable | Sets | 2 |  | 0
0
f | 3.5 c x 95 sq.mm1.1 KV grade XLPE Insulated FRLS sheathed armoured aluminium conductor cable | Sets | 0 |  | 0
0
g | 3.5 c x 70 sq.mm1.1 KV grade XLPE Insulated FRLS sheathed armoured aluminium conductor cable | Sets | 0 |  | 0
0
h | 3.5 c x 50 sq.mm1.1 KV grade XLPE Insulated FRLS sheathed armoured aluminium conductor cable | Sets | 2 |  | 0
0
i | 4 c x 35 sq.mm1.1 KV grade XLPE Insulated FRLS sheathed armoured aluminium conductor cable | Sets | 0 |  | 0
0
j | 4 c x 25 sq.mm1.1 KV grade XLPE Insulated FRLS sheathed armoured copper conductor cable | Sets | 0 |  | 0
0
k | 4 c x 25 sq.mm1.1 KV grade XLPE Insulated FRLS sheathed armoured AL conductor cable | Sets | 12 |  | 0
0
l | 4 c x 16 sq.mm1.1 KV grade XLPE Insulated FRLS sheathed armoured aluminium conductor cable | Sets | 0 |  | 0
0
m | 4 c x 16 sq.mm 1.1 KV grade XLPE Insulated FRLS sheathed armoured copper conductor cable | Sets | 0 |  | 0
0
n | 4 c x 10 sq.mm 1.1 KV grade XLPE Insulated FRLS sheathed armoured copper conductor cable | Sets | 0 |  | 0
0
p | 4 c x 6 sq.mm 1.1 KV grade XLPE Insulated FRLS sheathed armoured copper conductor cable for VRV ODUs | Sets | 0 |  | 0
0
q | 4 c x 4 sq.mm 1.1 KV grade XLPE Insulated FRLS sheathed armoured copper conductor cable | Sets | 4 |  | 0
0
s | 4 c x 2.5 sq.mm 1.1 KV grade PVC Insulated FRLS sheathed armoured copper conductor cable | Sets | 0 |  | 0
0
u | 3 c x 6 sq.mm 1.1 KV grade XLPE Insulated FRLS sheathed armoured copper conductor cable | Sets | 0 |  | 0
0
w | 2 c x 16 sq.mm 1.1 KV grade XLPE Insulated FRLS sheathed armoured copper conductor cable | Sets | 0 |  | 0
0
x | 2 c x 10 sq.mm 1.1 KV grade XLPE Insulated FRLS sheathed armoured copper conductor cable | Sets | 4 |  | 0
0
aa | 1c x 10 sq.mm FRLS XLPE insulated flexible copper conductor cables | Sets | 0 |  | 0
0
ab | 1c x 16 sq.mm FRLS XLPE insulated flexible copper conductor cables | Sets | 0 |  | 0
0
ac | 1c x 25 sq.mm FRLS XLPE insulated flexible copper conductor cables | Sets | 0 |  | 0
0
ac | 1c x 35 sq.mm FRLS XLPE insulated flexible copper conductor cables | Sets | 0 |  | 0
0
| TOTAL CARRIED OVER TO SUMMARY |  |  |  | 0
0
E | RACEWAYS AND CABLE TRAYS |  |  |  | 0
| Note :- |  |  |  | 0
0
1 | Fabricating supplying to site of installation, installation on ceiling/ surface 1.6 mm thick M.S. powder coated raceways of height 50 mm and 2.0 mm thick openable cover, totally enclosed, the joints between two lengths of channels or between channel and junction box shall be joined together with 3 mm thick M.S. Powder coated coupler plates to make it dust and water proof. The cost shall including all supporting and fixing accessories including dash fasteners. (Orange colour for data and Blue colour for power) |  |  |  | 0
a | 250 mm (wide) x 50 mm (height) | RM | 0 |  | 0
b | 150 mm (wide) x 50 mm (height) | RM | 65 |  | 0
c | 100 mm (wide) x 50 mm (height) | RM | 40 |  | 0
d | 150 mm (wide) x 150 mm (height) | RM | 0 |  | 0
0
2 | Fabricating supplying to site of installation, in floor including chase cutting of floor,leveling, refilling and making good the same from 1.6 mm thick and 2 mm thick cover pregalvanised MS CRCA sheet, totally enclosed, height 40 mm . The two lengths of raceways shall be fitted with Collars , 50 mm wide, 3 mm thick , press fit type. The raceways shall be clamped to the floor slab with GI clamps , 3mm thick and shall be screwed to the floor slab. The joint between raceway and junction box will be made with GI flexible strip( 3 nos), 3 mm thick, 4 inches long ,15 mm wide which will be nut bolted to the Junction box complete as required etc. |  |  |  | 0
0
a | 300 mm x 300 x 60 mm (height) | Nos. | 0 |  | 0
b | 250 mm x 250 x 60 mm (height) | Nos. | 0 |  | 0
c | 200 mm x 200 x 60 mm (height) | Nos. | 10 |  | 0
d | 150 mm x 150 x 60 mm (height) | Nos. | 7 |  | 0
e | 100 mm x 100 x 60 mm (height) | Nos. | 2 |  | 0
0
3 | Fabricating supplying to site of installation, in floor including chase cutting of floor,leveling, refilling and making good the same from 1.6 mm thick and 2 mm thick cover pregalvanised MS CRCA sheet, totally enclosed, height 40 mm . The two lengths of raceways shall be fitted with Collars , 50 mm wide, 3 mm thick , press fit type. The raceways shall be clamped to the floor slab with GI clamps , 3mm thick and shall be screwed to the floor slab. The joint between raceway and junction box will be made with GI flexible strip( 3 nos), 3 mm thick, 4 inches long ,15 mm wide which will be nut bolted to the Junction box complete as required etc. |  |  |  | 0
0
a | 250 mm (wide) x 40 mm (height) | RM | 0 |  | 0
b | 150 mm (wide) x40 mm (height) | RM | 30 |  | 0
c | 100 mm (wide) x 40 mm (height) | RM | 40 |  | 0
0
5 | Fabricating supplying to site of installation, Junction boxes for floor raceways made from 2 mm thick , with 2.5 mm thick G.I. cover including providing neoprene gaskets between the cover and the junction box, cadmium plated flat/round head screws, height as per site condition,totally enclosed. Proper cutouts shall be made in the side walls for raceway entry wherever required. The junction box shall be all side walls should be welded expect top cover and all side walls shall have suitable size of rectangular knock out holes for taking raceways / conduits as required and not a complete cut out. The top cover should be sealed with M Seal to make it dust and water proof complete as required etc. |  |  |  | 0
0
a | 300 mm x 300 x 50 mm (height) | Nos. | 0 |  | 0
b | 200 mm x 200 x 50 mm (height) | Nos. | 8 |  | 0
c | 150 mm x 150 x 50 mm (height) | Nos. | 13 |  | 0
d | 100 mm x 100 x 50 mm (height) | Nos. | 4 |  | 0
0
6 | Design manufacture , supply and fixing in position the cable trays of the following sizes for supporting 1.1 KV grade armoured/unarmoured aluminium /copper conductor cables. Fabricate the cable trays from perforated 1.6/2mm thick M.S. CRCA sheet duly galvanised with expansion coupler plates duly galvanised, with bolts, washer and nuts. Knock out holes for cable connections as per approved design. The tray should comply with the specification of NEC (National Electric Codes) and NEMA (National Electric Manufacturers Association). The steel should be as per IS:226 and galvanising as per IS :2629/BS 729/ASTM 123. The rate shall also include for supporting steel , fish plates , fixing accessories , nuts bolts, supporting down rods , dash fastener, cutting the RCC etc. complete as required. (the horizontal and vertical bends, T's should be factory fabricated and the rate should include for the same) |  |  |  | 0
0
a | 100 mm wide x 40 mm x 2.0 mm thk | RM | 0 |  | 0
b | 150 mm wide x 40 mm x 2.0 mm thk | RM | 65 |  | 0
c | 300 mm wide x 40 mm x 2.0 mm thk | RM | 50 |  | 0
d | 450 mm wide x 40 mm x 2.0 mm thk | RM | 5 |  | 0
e | 600 mm wide x 40 mm x 2.0 mm thk | RM | 0 |  | 0
0
7 | Design manufacture , supply and fixing in position the Ladder Type cable trays of the following sizes for supporting 1.1 KV grade armoured/unarmoured aluminium /copper conductor cables. Fabricate the cable trays to from Ladder Type 2.0 mm thick M.S. Flat/ Angle iron with bolts, washer and nuts. as per approved design. The tray should comply with the specification of NEC (National Electric Codes) and NEMA (National Electric Manufacturers Association). The steel should be as per IS:226 and galvanising as per IS :2629/BS 729/ASTM 123. The rate shall also include for supporting steel ,jointing fish plates , fixing accessories , nuts bolts, supporting down rods, dash fastener, cutting the RCC etc. complete as required. |  |  |  | 0
0
a | 300 mm wide x 50 mm x 2.0 mm thk | RM | 0 |  | 0
8 | Fabricating ,supplying to site of installation, installation of 500 mm size of 105 mm height mesh type EZ -Electroplated Zinc ( Legrand - Cablofil make ) cable tray including threaded G.I. down rods, dash fasteners , cablofil fixing accesories etc. complete as required. Cablofil make | RM | 0 |  | 0
0
| TOTAL CARRIED OVER TO SUMMARY |  |  |  | 0
0
F | DISTRIBUTION BOARDS |  |  |  | 0
0
1 | Supply,inginstalling ,connecting testing and commissioning of the following double door 1/4 rows vertical type 1.6 mm thick and 1. 4 thick door sheet steel enclosed fully recessed type, TPN Miniature Circuit Breakers Distribution Boards dust proof, verm­in proof, with hinged and lockable doors complete with DP MCB's and inter-connection with copper wire , insulated copper bus bar , cable glands­/conduit entry bushes, bonding to earth and paint­ing. Also provide separate neutral busbar for each phase. Provide separate Earth Links for each phase. Use brass thimbles for connections of all wires. 1 row for single phase and 4 rows for 3 phase. Provide separate 4 way 63 A main neutral link also. The phase busbar links shall be factory pre insulated. |  |  |  | 0
| Note :- The IP rating of the DB should be IP 43 . |  |  |  | 0
| Provide DB charts in laminated sheets in all Distribution Boards |  |  |  | 0
| A4 size SLD to be fixed on all DBs. |  |  |  | 0
0
1 | Light & Power Distribution Board |  |  |  | 0
0
a | 10 Way TPN DB, each phase consisting of 8 Nos. 10/20 AMP SP MCB’s and controlled by one number 100 mA sensitivity 63 AMPS DP RCCB backed up with 1 no 63 Amps 4 pole MCB. For VRV DB | Nos | 0 |  | 0
0
b | 12 Way TPN DB, each phase consisting of 10 Nos. 10/20 AMP SP MCB’s and controlled by one number 100 mA sensitivity 63 AMPS DP RCCB backed up with 1 no 63 Amps 4 pole MCB. For Light DB | Nos | 1 |  | 0
0
c | 14 Way TPN DB, each phase consisting of 12 Nos. 10/20 AMP SP MCB’s and controlled by one number 100 mA sensitivity 63 AMPS DP RCCB backed up with 1 no 63 Amps 4 pole MCB. For Power DB | Nos | 1 |  | 0
0
d | 12 Way SPN DB, consisting of 8 Nos. 10/20 AMP SP MCB’s and controlled by one number 100 mAsensitivity 63 AMPS DP RCCB backed up with 63 Amps DP MCB as incomer. For VRV DB | Nos | 1 |  | 0
0
2 | UPS Distribution Boards (All MCB's in workstation DB's should be D Curve) |  |  |  | 0
0
a | 12 Way TPN DB, each phase consisting of 10 Nos. 10/20 AMP SP MCB’s and controlled by one number 63 AMPS DP RCCB (100 mA) for each phase and 1 no. 63 amps 4 pole MCB incomer. | Nos.. | 0 |  | 0
0
b | 14 Way TPN DB, each phase consisting of 12 Nos. 10/20 AMP SP MCB’s and controlled by one number 63 AMPS DP RCCB (100 mA) for each phase and 1 no. 63 amps 4 pole MCB incomer. | Nos.. | 0 |  | 0
0
c | 12 Way SPN DB, consisting of 10 Nos. 10/20 AMP SP MCB’s and controlled by one number 100 mA sensitivity 63 AMPS DP RCCB backed up with 63 Amps DP MCB. For UPS DB | Nos.. | 1 |  | 0
0
d | 12 Way SPN DB, consisting of 4 Nos. 25/32 AMP DP MCB’s and controlled by one number 100 mA sensitivity 63 AMPS DP RCCB ( 100 mA) for backed up with 63 Amps 4D MCB. The bus bar shall be Twin bus bar. For SERVER DB | Nos.. | 0 |  | 0
0
3 | Supply, installation, testing and commissioning of sheet metal with 40 A DP MCB. This shall include cable entry boxes both for incoming and outgoing cable). For 6 KVA UPS. | Nos. | 1 |  | 0
0
4 | Supply, installation, testing and commissioning of sheet metal with 32 A DP MCB. This shall include cable entry boxes both for incoming and outgoing cable). For 2 KVA UPS. | Nos. | 0 |  | 0
0
5 | Supply, installation, testing and commissioning of sheet metal weather proof enclosure with 63 A FP RCBO(300mA) This shall include cable entry boxes both for incoming and outgoing cable) For VRV units. The enclosure shall be IP 42. For VRV Out Door units | Nos. | 2 |  | 0
0
6 | Supply, installation, testing and commissioning of sheet metal weather proof enclosure with 40 A FP RCBO(300mA) This shall include cable entry boxes both for incoming and outgoing cable) For VRV units. The enclosure shall be IP 42. For VRV Out Door units | Nos. | 0 |  | 0
0
7 | Supply, installation, testing and commissioning of sheet metal weatherproof Enclosure with 25/32 A DP MCB. This shall include cable entry boxes both for incoming and outgoing cable). | Nos. | 0 |  | 0
0
8 | Supply, installation, testing and commissioning of sheet metal with 16 A FP MCB. This shall include cable entry boxes both for incoming and outgoing cable). | Nos. | 2 |  | 0
0
| TOTAL CARRIED OVER TO SUMMARY |  |  |  | 0
0
G | SUB DISTRIBUTION PANELS |  |  |  | 0
0
1 | Sub Distribution Panels |  |  |  | 0
| Design, manufacture, supplying & installing at site in positioning, connecting, testing and commissioning of the following cubical type, dead front, 2mm thick sheet steel enclosed, free standing indoor type extendible Sub Distribution Panel with vermin proof hinged lockable doors for each compartment provide bus bar interconnections for incoming and outgoing including feeders earthing and painting and as per specifications. |  |  |  | 0
Note | Provide insulated dedicated earth link in all UPS Panels |  |  |  | 0
| All MCCB's 200 Amps and above shall be Microprocessor based |  |  |  | 0
| All Light & Power panel ,UPS and A.C. Panel incomer MCCB shall have Over current, Earth fault and short circuit protection. |  |  |  | 0
| All Incomer MCCB's in UPS Panels shall be Microprocessor based |  |  |  | 0
| The microprocessor based MCCBs shall have |  |  |  | 0
| Over Load (Phase) |  |  |  | 0
| Current setting Ir(Ir=XIn) OFF 0.4 to 1.0 in steps of 0.1 |  |  |  | 0
| Time delay , tr( Inverse) 10 sec at 6/r |  |  |  | 0
| Over Load (Neutral) |  |  |  | 0
| Current setting In (Intrl =XIr) 0.5, 0.75&1.00 Intrl |  |  |  | 0
| Inverse 10 sec at 6 Intrl/Fixed 200ms |  |  |  | 0
| Short Circuit setting -2- 10 |  |  |  | 0
| Instantaneous - 1.5-1 |  |  |  | 0
| All MCB's in UPS Panels shall be D Curve |  |  |  | 0
| In all Electrical panels protective acrylic sheet to be provided in cable alley and feeders. |  |  |  | 0
| The meters shall be able to monitor all major power quality parameters Voltage , current , frequency , KVAH,KWH,Power factor and individual,harmonics, ethernet ready - IEC-625-22. |  |  |  | 0
| The ATS shall be 4 pole with inbuilt manual operating switch. In case the controller of the ATS fails it should be capable of transferring the load while the ATS is in maintenance. The ATS and controller should be same make |  |  |  | 0
| Provide On / Off and trip indicating lamp on main incomer only. |  |  |  | 0
| Panel construction shall be Form 3b for all Panels with MCCB outgoings and Form 2b for all Panels with MCB's outgoings. |  |  |  | 0
| The Earth fault release/relay and CBCTs shall be same make as OEM Switchgear been used in the Panels. It shall not trip on imbalance of load. |  |  |  | 0
| All meters shall have Modbus card for BMS connectivity |  |  |  | 0
| All the Electrical Panels shall be in accordance with IS 8623 standards |  |  |  | 0
0
a | The SDB L&P shall consists of : |  |  |  | 0
0
| MAIN INCOMER |  |  |  | 0
| 1 Nos. 160 A TPN MCCB (25KA/1 sec)( O/C, S/C,E/F) and neutral isolation link 100% of rated current. Terminals suitable to receive 3.5c x 120 sq. mm . Al Ar cable connection on one side and Busbar connection on the other side. |  |  |  | 0
0
| BUSBAR |  |  |  | 0
| 200 amps 4P busbar chamber of suitable length with Aluminium busbars. All busbars and interconnections shall be of suitable size aluminium strips current density of aluminium shall not be more than 0.8 Amps/ sq.mm.provide 100% capacity for neutral bus bar. |  |  |  | 0
0
| INDICATING PANELS |  |  |  | 0
| 3 nos phase indicating lamps (LED type) each backed up with MCB and switch shall be provided for each incomer. |  |  |  | 0
| Provide Intelligent Panel Meter - multifunctional meter with RS485 for all incoming feeder |  |  |  | 0
| Provide Transient Voltage Surge Suppressor Rating 40kA class II along with 63 A MCCB. Including all necessary accessories. For Switching Operation on each incomer. |  |  |  | 0
| Provide earth fault protection (EF) in the incomer MCCB |  |  |  | 0
0
| OUTGOINGS |  |  |  | 0
| 1 Nos. 100 A TPN MCCB (36 kA/ 1 sec) terminal to receive suitable Cable on one side and Busbar connection on the other side. |  |  |  | 0
| 6 Nos. 63 A 4P MCB (10 kA/ 1 sec) terminal to receive suitable Cable on one side and Busbar connection on the other side. |  |  |  | 0
| 3 Nos. 16 A 4P MCB (10 kA/ 1 sec) terminal to receive suitable Cable on one side and Busbar connection on the other side. |  |  |  | 0
| 2 Nos. 40 A DP MCB (10 kA/ 1 sec) terminal to receive suitable Cable on one side and Busbar connection on the other side. |  |  |  | 0
| 2 Nos. 63 A DP MCB (10 kA/ 1 sec) terminal to receive suitable Cable on one side and Busbar connection on the other side. |  |  |  | 0
0
| The SDB L&P as described above and specifications complete | Set | 1 |  | 0
0
b | The UPS SDB in UPS Room shall consists of : |  |  |  | 0
0
| MAIN INCOMER |  |  |  | 0
| 1 No. 100 A 4P MCCB (25KA/1 sec)( O/C, S/C,E/F). Terminals suitable to receive 4R x 1c x 25 sq. mm Cu. Flexible cable connection on one side and Busbar connection on the other side. |  |  |  | 0
0
| BUSBAR |  |  |  | 0
| 150 amps 4P busbar chamber of suitable length with Copper busbars. All busbars and interconnections shall be of suitable size copper strips current density of copper shall not be more than 1.6 Amps/ sq.mm. |  |  |  | 0
0
| INDICATING PANELS |  |  |  | 0
| 3 nos phase indicating lamps (LED type) each backed up with MCB and switch shall be provided for each incomer. |  |  |  | 0
| Provide on/off indication lamp on each incomer and buscoupler. |  |  |  | 0
| Provide Intelligent Panel Meter - multifunctional meter with RS485 for all incoming feeder |  |  |  | 0
| Provide Transient Voltage Surge Suppressor Rating 40kA class I&II along with 63 A MCB. Including all necessary accessories. For Switching Operation on each incomer. |  |  |  | 0
| Provide earth fault protection (EF) in the incomer MCCB |  |  |  | 0
0
| OUTGOINGS |  |  |  | 0
| 4 Nos. 63 A 4P MCB (10 kA/ 1 sec) terminal to receive suitable Cable on one side and Busbar connection on the other side. |  |  |  | 0
| 2 Nos. 63A DP MCB (10 kA/ 1 sec) terminals to receive suitable Copper Ar. Cable on one side and Busbar connection on the other side. |  |  |  | 0
| The above Panel as described above and specifications complete | Set | 0 |  | 0
0
c | The Kitchen Panel shall consists of : |  |  |  | 0
0
| MAIN INCOMER |  |  |  | 0
| 1 No. 100 A TPN MCCB (36 KA) along with shunt trip suitable to receive 3.5 x 50 sq. mm Al. Ar cable connection on one side and Busbar connection on the other side. |  |  |  | 0
0
| BUSBAR |  |  |  | 0
| 150 amps 4P busbar chamber of suitable length with Aluminium busbars. All busbars and interconnections shall be of suitable size aluminium strips current density of aluminium shall not be more than 0.8 Amps/ sq.mm.provide 100% capacity for neutral bus bar. |  |  |  | 0
0
| INDICATING PANELS |  |  |  | 0
| 3 nos phase indicating lamps (LED type) each backed up with MCB and switch shall be provided for each incomer. |  |  |  | 0
| Provide Intelligent Panel Meter - multifunctional meter with RS485 for all incoming feeder |  |  |  | 0
| Provide TVSS (40KA) |  |  |  | 0
0
| OUTGOINGS |  |  |  | 0
0
| 1 Nos.40A 4P RCBO (10 kA/ 1 sec) terminals to receive suitable Cable on one side and Busbar connection on the other side. The RCBO shall have 30 mA |  |  |  | 0
| 2 Nos.32A 4P RCBO (10 kA/ 1 sec) terminals to receive suitable Cable on one side and Busbar connection on the other side. The RCBO shall have 30 mA |  |  |  | 0
| 2 Nos.32A DP RCBO (10 kA/ 1 sec) terminals to receive suitable Cable on one side and Busbar connection on the other side. The RCBO shall have 30 mA |  |  |  | 0
| 25 Nos.25/16A DP RCBO (10 kA/ 1 sec) terminals to receive suitable Cable on one side and Busbar connection on the other side. The RCBO shall have 30 mA |  |  |  | 0
0
| The above panel as described above and specifications complete as required. | Set | 1 |  | 0
0
2 | The contractor to submit reports of torque tightness tests for all the nut bolt cable joints in all the panels with red marking after the torque tightening has been done as per manufactures recommendation. | Set | 0 |  | 0
0
3 | Providing & fixing in position 1000 mm wide , Electrical Insulating Mats as per IS 15652:2006, 2mm thick, suitable up to 3.3 KV , fire retardant,no effect of acids, alkalies and transformer oils, moisture proof, high tensile strength and texture finish / cloth impression (Anti slip , marking on top) . | RM | 5 |  | 0
0
4 | Replacement of existing 250 A tap off box with 400 A tap off box at site with all the necessary accessories complete as required. | Nos. | 0 |  | 0
0
5 | Supply & fixing in position approved shock treatment chart written in English, Hindi and Local language. These charts shall be framed in wooden frame & covered with clear glass. | Nos. | 1 |  | 0
0
6 | Supply & fixing in position the best quality danger notice boards of approved shape & size as reqd. by the local Electrical Inspecting Authority written in English, Hindi & local language. | Nos. | 1 |  | 0
0
7 | Supply & fixing in position the Electrical A 1 Size SLD chart in the UPS/electrical room . These charts shall be framed in wooden frame & covered with clear glass. | Nos. | 1 |  | 0
0
8 | Supplying the first aid box as approved by John Ambulance society. | Nos. | 1 |  | 0
0
9 | Supply & Fixing of Remotely controlled push button Station in the Ktchen area. Suitable for 1 nos incomer MCCB complete as required. | Nos. | 1 |  | 0
0
10 | Supply & Fixing of NO/NC Relay Module complete as required. | Nos. | 2 |  | 0
0
11 | 2 core -1.5 sq.mm PVC FRLS wires in already laid suitable size of M.S conduit complete as required. | Rmt | 45 |  | 0
0
12 | Supply, Installations, Testing and Commissioning of 2 Kg Fire Suppression System (CQRS) in all Floor Panels of Electrical and UPS Room to be included. - Automatic Direct Low Pressure Fire Suppression System, UL Listed FK-5-1-12 Extinguishing Fluid shall be filled in UL Listed Cylinder, UL Listed Pressure Switch should be integrated in DLP Valve for Indication on Fire Suppression Panel and Main Fire Alarm System, 15 Meter UL Listed Detection Tube shall be UV Protected made of Modified Polyamide associated with End of Line Adapter with Pressure Gauge, master Control Panel with A/V Alarm and Battery Backup along with Potential Free Contact to integrate with existing Fire Alarm System for Central Monitoring. Mounting Bracket with all necessary accessories. complete in all respect. System Component Approval: Cylinder-UL Listed, Gas-UL Listed, Detection Tube-UL Listed, Pressure Switch-UL Listed Make: FireMech / Ceasefire / Honeywell | Nos. | 0 |  | 0
0
| TOTAL CARRIED OVER TO SUMMARY |  |  |  | 0

## Light Fixtures B3
S.No. | Description | Unit |  | Supply & Installation
|  |  | Qty | Rate In Rs. | Amount in Rs.
H | SUPPLY & INSTALLATION OF LIGHTING FIXTURES |  |  |  |  | *Quoted Installation
1 | Supply & Fixing in position testing and commissioning of the following Lighting fixtures at site including all type of fixing accessories complete as required etc. Use all light fixture shall be LED Type. (Samples of all light fixtures to be submitted to the client/architect/consultant for approval prior to procurement of fixtures) |  |  |  | 0
0
a | 32 Watts LED 600x600mm panel LED light as per approved make. | Nos | 45 |  | 0
0
b | 32 Watts LED 600x600mm panel LED Fire Proof light as per approved make.(Fire proof for Bonded store) | Nos | 0 |  | 0
0
c | 15 watts Suspended Cylindrical LED light as per approved make. | Nos | 0 |  | 0
0
d | Suspended Channel LED light (90x1500) at Cabins as per approved make | Nos | 0 |  | 0
0
e | Suspended Channel LED light (60x1200) as per approved make | Nos | 0 |  | 0
0
f | 13 wattts Surface Mounted LED Down light as per approved make | Nos | 0 |  | 0
0
g | 13 wattts Recessed LED Down light as per approved make | Nos | 75 |  | 0
0
h | Supply of track mounted spot light 10W-850lm cylindrical Shape, | Nos | 0 |  | 0
0
i | Track for mounting Spot 1 meter standard length. | Rmt | 0 |  | 0
0
j | 500 mm Dia Suspended Decorative LED hanging light as per Architect /Client basic cost Rs. 5500 | Nos | 0 |  | 0
0
k | 750 mm Dia Suspended Decorative LED hanging light as per Architect /Client basic cost Rs. 7500 | Nos | 0 |  | 0
0
l | 15 Watts LED Wall light as per Architect/Client basic cost Rs. 2500 | Nos | 0 |  | 0
0
2 | Supply, Installation, Testing & Commissioning of 3 Watts LED Ni Cd Battery backup up to 1.5 hr emergency Exit light Prolite or equivalent make. The sample shall be submitted before ordering. or Equivalent make. | Nos | 6 |  | 0
0
3 | Supply, installation, testing commissioning of recessed ceiling mounted photo cell switching units to provide ON/OFF switching of lighting in response to ambient light levels. | Nos | 0 |  | 0
0
4 | Supply & installation of Passive infra-red presence detector for lighting control to set the parameters of all meeting rooms and cabin (ON/OFF selection of lights)( Lights switch OFF in steps of 1 minute) | Nos | 0 |  | 0
a | Switches lighting OFF when sufficient daylight is present. |  |  |  | 0
b | Used as on ON/OFF daylight dependant switch or in series with a wall switch |  |  |  | 0
c | Lighting level adjustable up to 1500 lux approx. |  |  |  | 0
0
| TOTAL CARRIED OVER TO SUMMARY |  |  |  | 0

## ElectB6
Sl.No. | Description | Unit |  | Supply & Installation
|  |  | Qty | Rate In Rs. | Amount in Rs.
A. | POINT WIRING
All wires shall be FRLS PVC insulated copper conductor. Point wiring rates are inclusive of 3 x 1.5 sq mm insulated copper conductor wires for circuit.(from DB to switch board).
All sockets to be checked with a Check Plug socket tester for live-neutral reverse, no earth,neutral fault, live earth reverse, neutral earth reverse.
The Circuit No. and DB no. label shall be provided on all UPS ,RAW sockets and switchboards with label printer.
Colour coding for conduits to be done for different systems. The whole length of conduits to be painted.
All circuit & point wiring shall be colour coded & shall have ferruling on both end for circuit identification complete as required etc.Labelling on all the switches and sockets to be done with respect to DB reference, phase and circuit no.
Earth loop Impedance Test to be performed. RCD test to be done. Cable Insulation Tests to be done.
Wherever the occupancy sensor is provided in the cabin/ meeting rooms/workstations , the circuit wires from Distribution Board to occupancy sensor and sensor to switch are inclusive in the point wiring rate.
Labeling of all sockets and emergency lights to be provided and Ferruling for all the circuits to be considered
1 | Wiring for the following light points with 3x1.5 Sq.mm FRLS PVC insulated stranded copper conductor wires in concealed M.S. conduits in F.ceiling/walls/ceiling as directed including providing and fixing of 6 amps flush type switches, 5 sided G.I Boxes for housing switc­hes and earth­ing complete as required. Rates are inclusive of 3 x 1.5 sq mm FRLS PVC insulated stranded copper conductor wires for circuit
a. | First point controlled by one no. 6 amp switch. | Nos. | 150 |  | 0
0
2 | Same as item No. 1a above but LOOP POINT i.e. wiring of point looped from first point with 3 x 1.5 sq. mm FRLS PVC insulated copper conductor wire in concealed/exposed MS conduit and earthing | Nos. | 320 |  | 0
0
3 | Wiring for the following light points with 1.5 Sq.mm FRLS PVC insulated stranded copper conductor wires in concealed M.S. conduits in F.ceiling/walls/ceiling as direc­ted including providing and fixing of 6 amps flush type switches, 5 sided G.I Boxes for housing switc­hes and earth­ing comple­te as required. Rates are inclusive of 3 x 1.5 sq mm FRLS PVC insulated stranded copper conductor wires for circuit |  |  |  | 0
0
a. | First point controlled by one no. 16 amp switch. | Nos. | 0 |  | 0
0
4 | Wiring for the following light points controlled by MCB in DB (Cost of MCB has been taken elsewhere in the tender) with 3 x 1.5 sq. mm FRLS PVC insulated copper conductor wires in concealed/exposed M.S. conduits as called for and earthing. |  |  |  | 0
0
a. | First point controlled by existing MCB in D.B. To first light Em Light | Nos. | 8 |  | 0
0
5 | Same as item No. 4.a above but LOOP POINT i.e. wiring of point looped from first point with 3x1.5 sq. mm FRLS PVC. insulated copper conductor wire in concealed/exposed M.S. conduit and earthing | Nos. | 89 |  | 0
0
6 | SITC of 2C x 1.5 sq mm non shielded Cable for DALI Ballast wiring in 25 mm dia MS conduit with all fixing accessories complete as required | Rmt. | 0 |  | 0
0
7 | SITC of 4C x 1.5 sq mm shielded Cable for QSM wiring in suitable size of MS conduit with all fixing accessories complete as required. Cable Common – 12 AWG (4.0 mm2); Power – 12 AWG (4.0 mm2); MUX Data – 22 AWG (0.25 mm2); Data – 22 AWG (0.25 mm2); Sense Line – 18 AWG (0.75 mm2); Drain Wire – 24 AWG (0.2 mm2) | Rmt. | 0 |  | 0
0
8 | Wiring for 6/16 amps outlets with 3 X 2.5 sq.mm FRLS PVC insulated copper conductor wires in M.S. Conduits in ceiling/walls/floor as direc­ted incl­u­ding providing & fixing of 6/16 amps flush type 5 pin socket and 16 amps switch with cover plate, 5 sided G.I boxes for housing switches, sockets and earthi­ng complete as required. (for general areas 4 nos loop in one circuits) | Nos. | 60 |  | 0
0
9 | Wiring for inline fan points with 2 x 2.5 sq.mm FRLS PVC insulated stranded copper con­ductor wires in concealed M.S. conduits in F.ceiling/ walls/ Ceiling as directed including providing and fixing of 16 amps flush type switches 16 amps 3 pin socket near inline fan, 5 sided G.I. boxes for housing switches and 16 amps 3 pin socket outlet and earthing and complete as required.(including body earth for GI boxes) | Nos. | 5 |  | 0
0
10 | Wiring for Geyser/Projector/Hand Dryer points with 2 x 4 + 1 x 4 sq mm FRLS PVC insulated copper conductor wires in concealed M.S. conduits in F.ceiling/ walls/ Ceiling as directed including providing & fixing 16 amps flush type switch near the white board and 6/16 amps 6 pin socket near the projector in ceiling , 5 sided G.I. boxes for housing switches and 6/16 A 6 pin socket outlet , earthing and complete as required.(including body earth for GI boxes) ( 1 point per circuit) | Nos. | 12 |  | 0
0
11 | Wiring for VRV Indoor units with 3 x 2.5 sq.mm FRLS PVC insulated stranded copper conductor wires in concealed M.S. conduits in F.ceiling/ walls/ Ceiling as directed including providing providing and fixing of 6 amps flush type switches 16 amps 3 pin socket near VRV points, 5 sided G.I. boxes for housing switches and 16 amps 3 pin socket outlet and earthing and complete as required.(including body earth for GI boxes) (1 point per circuit) | Nos. | 42 |  | 0
0
12 | Wiring for VAV /fire damper points with 3 x 2.5 sq.mm FRLS PVC insulated copper conductor wires in concealed M.S. conduits in F.ceiling/ walls/ Ceiling as directed including providing & fixing 6 amps flush type switches, 6 amps 3 pin socket near VAV points, 5 sided G.I. boxes for housing switches and 6 A sockets earthing and complete as required. The sockets to be fused spur type (MK make). (including body earth for GI boxes) (8 to 10 points per circuits) | Nos. | 0 |  | 0
0
13 | Wiring for 16 amps power outlet poi­nts with 4 sq.mm FRLS PVC insulated stranded copper conductor wires in concealed/recessed M.S. conduit as directed including providing providing and fixing of 16 amps flush type switch and 6 pin socket with cover plate 5 sided G.I. outlet boxes for switches and socket and earthing the third pin with 2.5 sq mm FRLS PVC stranded copper wire complete as required (Only one outlet shall be connected on each circuit) (including body earth for GI boxes) | Nos. | 13 |  | 0
0
14 | Wiring for 16 amps power outlet points with 4 sq.mm FRLS PVC insulated stranded copper conductor wires for the first power outlet and 4 sq.mm FRLS PVC insu­lated stranded copper conductor wires for the second outlet, in concealed M.S. cond­uits in F.ceiling/ walls/Ceiling/floor ducts as directed including providing providing and fixing of 16 amps flush type switch and 6 pin socket with cover plate, 5 sided G.I. outlet boxes for housing switches and socket, and earthing the third pin with 2.5 sq.mm FRLS PVC insulated copper conductor wires complete as required (Two power out­lets shall be connected on each circuit)(including body earth for GI boxes) | Set of Two | 5 |  | 0
0
15 | Wiring for A/C outlet points with 4.0 sq mm FRLS PVC insulated stranded copper conductor wires in M.S. conduitl/wall/floor ducts as directed including providing 25 A socket with 25 amps SP MCB ( Tiny Trip) 5 sided GI Outlet Box for housing and socket and MCB and earthing with 2.5 sq. mm FRLS PVC insulated stranded Copper Conductor wires complete as required. | Nos. | 0 |  | 0
0
| Different colours to be used for 3 core cables for raw power and UPS power. |  |  |  | 0
16 | Wiring for UPS/Raw plug outlets points with three core, 2.5 sqmm FRLS PVC Insulated and PVC sheathed flexible cable with bright annealed electrolytic copper conductor, 1100 volt grade confirming to IS : 694-1990 with latest amendments, in existing Channels/ conduit in ceiling/walls/floor including all cable termination accessories) (including body earth for GI boxes). Colour Coding to be followed | RM | 2400 |  | 0
0
17 | Wiring for UPS/Raw plug outlets points with three core, 4.0 sqmm FRLS PVC Insulated and PVC sheathed flexible cable with bright annealed electrolytic copper conductor , 1100 volt grade confirming to IS : 694-1990 with latest amendments, in existing Channels/ conduit in ceiling/walls/floor inclu­ding all cable termination accessories) Earthing of GI Box to be included. Colour Coding to be followed. For Lab & Kitchen Sockets | RM | 200 |  | 0
0
18 | Wiring for Power plug outlets points with three core, 6.0 sqmm FRLS PVC Insulated and PVC sheathed flexible cable with bright annealed electrolytic copper conductor , 1100 volt grade confirming to IS : 694-1990 with latest amendments, in existing Channels/ conduit in ceiling/walls/floor inclu­ding all cable termination accessories). Colour Coding to be followed. | RM | 45 |  | 0
0
19 | Wiring for Power plug outlets points with three core, 10.0 sqmm FRLS PVC Insulated and PVC sheathed flexible cable with bright annealed electrolytic copper conductor , 1100 volt grade confirming to IS : 694-1990 with latest amendments, in existing Channels/ conduit in ceiling/walls/floor inclu­ding all cable termination accessories). Colour Coding to be followed. | RM | 40 |  | 0
0
| The word UPS shall be printed on all UPS sockets. |  |  |  | 0
| The word RAW shall be printed on all RAW sockets. |  |  |  | 0
| The Circuit No. and DB no. label shall be provided on all UPS ,RAW sockets and switchboards with label printer. |  |  |  | 0
| Contractor is required to submit samples of all types of switches and sockets to Consultant and Architects representative for approval before ordering the material. |  |  |  | 0
0
20 | Providing and fixing of 1 Nos. 6 amp round pin type socket and 1 No. 6 amps switch cover plate, 5 sided G.I. Boxes for housing switches and sockets and earthing complete as required (for UPS/Raw). GI Box to have earth pin for body earthing | Nos. | 158 |  | 0
0
21 | Providing and fixing of 2 Nos. 6 amp round pin type socket and 1 No. 6 amps switch cover plate, 5 sided G.I. Boxes for housing switches and sockets and earthing complete as required (for UPS/Raw). GI Box to have earth pin for body earthing | Nos. | 145 |  | 0
0
22 | Providing and fixing of 3 Nos. 6 amp round pin type socket and 1 No. 6 amps switch cover plate, 5 sided G.I. Boxes for housing switches and sockets and earthing complete as required (for UPS/Raw). GI Box to have earth pin for body earthing | Nos. | 12 |  | 0
0
23 | Providing and fixing of 2 Nos. 6/16 amp round pin type socket and 1 No. 16 amps switch cover plate, 5 sided G.I. Boxes for housing switches and sockets and earthing complete as required (for UPS/Raw). GI Box to have earth pin for body earthing | Nos. | 4 |  | 0
0
24 | Providing and fixing of 1 No.16 amps flush type 6 pin socket and 1 No. 16 amps switch with indicator, cover plate, 5 sided G.I. Boxes for housing switches and sockets and earthing complete as required (for UPS / RAW) GI Boxes to have earth pin for body earthing | Nos. | 4 |  | 0
0
25 | Providing and fixing Underfloor Access Outlets (250 x 250 x 55 - mm 70 compartments 1Trap including providing 2 Nos 6 Amps Round Pin sockets and 1 no. 16 Amp Switch & 2 data outlet complete as required. | Nos. | 8 |  | 0
0
26 | Supply and fixing of the following sizes of thermoplastic moulded plug and socket IEC 309 type in PVC Box of suitable size flush / surface and making connections complete as required. The box shall be IP 44. |  |  |  | 0
a | 3 pin 16/20 A 1 phase industrial socket with mcb & plug top | Nos. | 0 |  | 0
b | 3 pin 32 A 1 phase industrial socket plug top | Nos. | 4 |  | 0
0
27 | Providing and fixing in position the following M.S. conduits including all accessories concealed in F. ceiling/wall/floor as required including 1.6 mm thick M.S. junction or pull boxes with 3mm thick perspex sheet cover plate compl­te with 1.6 mm dia. G.I. pull wires in the length of conduit. |  |  |  | 0
0
a. | 20 mm dia conduit ( 1.6 mm thick) | RM | 90 |  | 0
b. | 25 mm dia conduit (1.6 mm thick) | RM | 200 |  | 0
c. | 32 mm dia conduit (2.0 mm thick) | RM | 110 |  | 0
0
28 | The Electrical Contractor shall provide sufficient temporary lighting for working in the Building total area 17500 sq. ft. divided in single floor and maintain the same till completion of the project.It shall include replacement of all fused/faulty lamps.It shall include providing 15 A plug sockets (industrial type with ON/OFF switch/MCB) on 4 sides walls one plug at every 5-8 meter distance. The Contractors will tap off supply from these plugs for his use. Tubelights to maintain a lighting level of 150 lux on the floor,.Each 15 A socket and each Light circuit shall be protected by suitable MCBs.Use three core PVC Insulated PVC sheathed copper conductor cables for wiring.The contractor shall salvage the complete wiring and take it back at the end of the project. | L.S. | 1 |  | 0
0
| TOTAL CARRIED OVER TO SUMMARY |  |  |  | 0
0
B. | CONDUITING FOR TELEPHONE , COMPUTER & CONDUITING AND WIRING FOR T.V. SYSTEM. |  |  |  | 0
0
1 | Providing and fixing in position the following M.S. conduits including all accessories concealed in F. ceiling/wall/floor as required including 1.6 mm thick M.S. junction or pull boxes with 3mm thick perspex sheet cover plate compl­te with 1.6 mm dia. G.I. pull wires in the length of conduit. |  |  |  | 0
0
a. | 20 mm dia conduit( 1.6 mm wall thickness) | RM | 95 |  | 0
b. | 25 mm dia conduit ( 1.6 mm wall thickness) | RM | 220 |  | 0
c. | 32 mm dia conduit ( 1.6 mm wall thickness) | RM | 105 |  | 0
0
2 | Providing and fixing in position suitable 1.2 mm thick G.I./ PVC outlet box for RJ- 45 computer outlet with all fixing accessories as required. | Nos. | 35 |  | 0
0
3 | Supply and fixing of 1.2 mm thick G.I Box along with RG 11 TV Co axial socket with Cover Plate | Nos. | 1 |  | 0
0
4 | Supply drawing connecting testing and commissioning of TV Coaxial cable RG 6 in existing conduit | RM | 65 |  | 0
0
| TOTAL CARRIED OVER TO SUMMARY |  |  |  | 0
0
C. | EARTHING |  |  |  | 0
0
1 | Providing and fixing in position the following copper strips and wires including providing all fixing accessories and effecting proper connections |  |  |  | 0
| Note:- MS Cable markers at the earth bus, panel and DB entries to be provided |  |  |  | 0
a. | G.I. tape 25 mm x 6 mm | RM | 240 |  | 0
b. | Copper tape 25mm x 3 mm | RM | 6 |  | 0
c. | GI wire 8 SWG | RM | 200 |  | 0
d. | GI wire 12 SWG | RM | 150 |  | 0
e. | Supply installation , and making of Exothermic weld suitable to bond GI strip of 25x5 mm with Copper Strip of 25x5 mm with 75mm extensions on either side | Nos. | 4 |  | 0
f. | Copper Earth Link connectors - 200 mm long, 25mm wide and 5 mm thick | Nos. | 3 |  | 0
0
2 | Supply and laying, effecting proper connec­tions, testing & commissioning of the following sizes of 1.1 KV armoured XLPE/ unarmoured FRLS sheathed XLPE insulation, conforming to IS: 7098 (Part-1)- 1988 ( 90 deg C) aluminium /copper conductor cables conforming to IS : 1554 and FRLS Insulated flexible copper cables as per IS 694 laid over MS supports in existing RCC ducts/ laid in ground /laid on Cable Trays including clamping the cables to sup­ports in an approved manner as required complete with all accessories. |  |  |  | 0
0
a | 1c x 50 sq.mm FRLS insulated flexible copper conductor cables | RM | 140 |  | 0
0
b | 1c x 35 sq.mm FRLS insulated flexible copper conductor cables | RM | 200 |  | 0
0
c | 1c x 25 sq.mm FRLS insulated flexible copper conductor cables | RM | 90 |  | 0
0
d | 1c x 16 sq.mm FRLS insulated flexible copper conductor cables | RM | 120 |  | 0
0
e | 1c x 10 sq.mm FRLS insulated flexible copper conductor cables | RM | 100 |  | 0
0
f | 1c x 6 sq.mm FRLS insulated flexible copper conductor cables | RM | 50 |  | 0
0
g | 2 Nos 1 x 10 Sq. mm FRLS insulated flexible copper conductor cables (Green Colour for UPS DB Sub-main Earthing) | RM | 95 |  | 0
0
3 | Supplying and making of end termination for the following size of compression lugs and PG Threaded Nylon Flexible cable glands complete with all fixing accessories as required |  |  |  | 0
0
a | 1c x 50 sq.mm FRLS insulated flexible copper conductor cables | Sets | 4 |  | 0
0
b | 1c x 35 sq.mm FRLS insulated flexible copper conductor cables | Sets | 8 |  | 0
0
c | 1c x 25 sq.mm FRLS insulated flexible copper conductor cables | Sets | 4 |  | 0
0
d | 1c x 16 sq.mm FRLS insulated flexible copper conductor cables | Sets | 6 |  | 0
0
d | 1c x 10 sq.mm FRLS insulated flexible copper conductor cables | Sets | 14 |  | 0
0
4 | Providing earthing station at loca­tion as called for including provid­ing 600 mm x 600 mm x 3 mm thick tinned copper electrode 2 Nos 25 x 3 mm copper strip (for body earthing GI strip can be considerd) up to ground level 20mm dia medium class GI pipe (India Tube Company make or approved equal) CI funnel with 20 gauge GI wire mesh, masonry chamber with concrete base, CI man­hole cover (cover to be heavy duty) with frame (300mm x 300mm) and bitumastic paint and packing the fixture of charcoal and common salt around plate electrode complete as per I.S. ( Minimum depth shall be 4.2 M ) for UPS & Server | Nos. | 0 |  | 0
0
5 | Supply, Installation, testing and commissioning of Maintenance Free Earthing of make Electrolytic Earthing comprising of type 'K' copper 2.4 mm wall thickness, hollow tube 10 feet long, 2.125 inches outer diameter completely filled with non hazardous metallic salts (Terrafill) to achieve an earth resistance of less than 1 ohms. Provide masonry chamber with concrete base, CI man­hole cover (cover to be heavy duty) with frame (300mm x 300mm) and make earth pit sign/ identifcation no in each earth station for UPS & Server | Nos. | 4 |  | 0
0
6 | Supply, installation, testing and commissioning of sheet metal enclosed 450 x 200 x 150 (D) mm insulated earth distribution board with 1 nos. 50 x 6 mm copper tinned earth bars on SMC insulator suitable for 6/8 nos connections complete with all fixing accessories as required. | Nos. | 2 |  | 0
0
7 | Supply, installation, testing and commissioning of sheet metal enclosed 300 x 200 x 150 ( D) mm insulated earth distribution board with 1 nos. 32 x 6 mm copper tinned earth bars on SMC insulator suitable for 6/8 nos connections complete with all fixing accessories as required. | Nos. | 3 |  | 0
0
8 | Supplying and laying of the following sizes of Heavy duty PVC Pipes below paved area including chase cutting and back filling. |  |  |  | 0
a. | 100 mm outer dia | RM | 5 |  | 0
b. | 80 mm outer dia | RM | 10 |  | 0
0
| TOTAL CARRIED OVER TO SUMMARY |  |  |  | 0
0
D | CABLES, MAINS & SUBMAINS |  |  |  | 0
0
1 | Supply and laying, effecting proper connec­tions, testing & commissioning of the following sizes of 1.1 KV armoured XLPE/ unarmoured FRLS sheathed XLPE insulation, conforming to IS: 7098 (Part-1)- 1988 ( 90 deg C) aluminium /copper conductor cables conforming to IS : 1554 and FRLS Insulated flexible copper cables as per IS 694 laid over MS supports in existing RCC ducts/ laid in ground /laid on Cable Trays including clamping the cables to sup­ports in an approved manner as required complete with all accessories. |  |  |  | 0
0
| Note : All cables to be glanded and crimped with suitable sized lugs. All Cable trays to be double earthed. All raceways and cable glands to be earthed with brass round earth clips and wires. |  |  |  | 0
| Earthing ring to be included in all the cable glands. |  |  |  | 0
| Sub main cables should be labelled at both ends |  |  |  | 0
| Joints shall be allowed only at the 2 ends of the cables and not in between. |  |  |  | 0
0
a | 3.5 c x 300 sq.mm1.1 KV grade XLPE Insulated FRLS sheathed armoured aluminium conductor cable | RM | 0 |  | 0
0
b | 3.5 c x 240 sq.mm1.1 KV grade XLPE Insulated FRLS sheathed armoured aluminium conductor cable For SDB L&P (Assumed) | RM | 120 |  | 0 | 4
0
c | 3.5 c x 185 sq.mm1.1 KV grade XLPE Insulated FRLS sheathed armoured aluminium conductor cable | RM | 0 |  | 0
0
d | 3.5 c x 150 sq.mm1.1 KV grade XLPE Insulated FRLS sheathed armoured aluminium conductor cable | RM | 140 |  | 0
0
e | 3.5 c x 120 sq.mm1.1 KV grade XLPE Insulated FRLS sheathed armoured aluminium conductor cable | RM | 0 |  | 0
0
f | 3.5 c x 95 sq.mm1.1 KV grade XLPE Insulated FRLS sheathed armoured aluminium conductor cable | RM | 0 |  | 0
0
g | 3.5 c x 70 sq.mm1.1 KV grade XLPE Insulated FRLS sheathed armoured aluminium conductor cable | RM | 0 |  | 0
0
h | 3.5 c x 50 sq.mm1.1 KV grade XLPE Insulated FRLS sheathed armoured aluminium conductor cable | RM | 50 |  | 0 | 2
0
i | 4 c x 35 sq.mm1.1 KV grade XLPE Insulated FRLS sheathed armoured aluminium conductor cable | RM | 0 |  | 0
0
j | 4 c x 25 sq.mm1.1 KV grade XLPE Insulated FRLS sheathed armoured aluminium conductor cable For DB and VRV ODU | RM | 680 |  | 0 | 8
0
k | 4 c x 25 sq.mm1.1 KV grade XLPE Insulated FRLS sheathed armoured copper conductor cable | RM | 0 |  | 0
0
l | 4 c x 16 sq.mm1.1 KV grade XLPE Insulated FRLS sheathed armoured aluminium conductor cable | RM | 0 |  | 0
0
m | 4 c x 16 sq.mm 1.1 KV grade XLPE Insulated FRLS sheathed armoured copper conductor cable For UPS DB | RM | 130 |  | 0 | 4
0
n | 4 c x 10 sq.mm 1.1 KV grade XLPE Insulated FRLS sheathed armoured copper conductor cable | RM | 95 |  | 0
0
p | 4 c x 6 sq.mm 1.1 KV grade XLPE Insulated FRLS sheathed armoured copper conductor cable | RM | 0 |  | 0
0
q | 4 c x 4 sq.mm 1.1 KV grade XLPE Insulated FRLS sheathed armoured copper conductor cable | RM | 25 |  | 0 | 4
0
s | 4 c x 2.5 sq.mm 1.1 KV grade XLPE Insulated FRLS sheathed armoured copper conductor cable | RM | 0 |  | 0
0
t | 3 c x 10 sq.mm 1.1 KV grade PVC Insulated FRLS Armoured copper conductor cable | RM | 0 |  | 0
0
u | 3 c x 6 sq.mm 1.1 KV grade XLPE Insulated FRLS sheathed armoured copper conductor cable For Emg DB | RM | 120 |  | 0 | 4
0
x | 2 c x 16 sq.mm 1.1 KV grade XLPE Insulated FRLS sheathed armoured copper conductor cable For Server DB | RM | 50 |  | 0 | 4
0
z | 1c x 6 sq.mm FRLS XLPE insulated flexible copper conductor cables | RM | 0 |  | 0
0
aa | 1c x 10 sq.mm FRLS XLPE insulated flexible copper conductor cables | RM | 0 |  | 0
0
ab | 1c x 16 sq.mm FRLS XLPE insulated flexible copper conductor cables | RM | 0 |  | 0
0
ac | 1c x 25 sq.mm FRLS XLPE insulated flexible copper conductor cables | RM | 0 |  | 0
0
ad | 1c x 35 sq.mm FRLS XLPE insulated flexible copper conductor cables | RM | 135 |  | 0 | 16
0
2 | Supplying and making terminal joints for the following size of 1.1 KV PVC insulated copper conductor armoured cables including providing heavy duty tinned copper terminal crimping lugs, solder, insulation tape, approved sealing epoxy compound, double compression brass cable glands, effecting gland connec­tions and effecting terminal connections to the equipment complete as required. Use compression lugs and PG Threaded Nylon Flexible cable glands for single core flexible cables |  |  |  | 0
0
a | 3.5 c x 300 sq.mm1.1 KV grade XLPE Insulated FRLS sheathed armoured aluminium conductor cable | Sets | 0 |  | 0
0
b | 3.5 c x 240 sq.mm1.1 KV grade XLPE Insulated FRLS sheathed armoured aluminium conductor cable | Sets | 4 |  | 0
0
c | 3.5 c x 185 sq.mm1.1 KV grade XLPE Insulated FRLS sheathed armoured aluminium conductor cable | Sets | 0 |  | 0
0
d | 3.5 c x 150 sq.mm1.1 KV grade XLPE Insulated FRLS sheathed armoured aluminium conductor cable | Sets | 4 |  | 0
0
e | 3.5 c x 120 sq.mm1.1 KV grade XLPE Insulated FRLS sheathed armoured aluminium conductor cable | Sets | 0 |  | 0
0
f | 3.5 c x 95 sq.mm1.1 KV grade XLPE Insulated FRLS sheathed armoured aluminium conductor cable | Sets | 0 |  | 0
0
g | 3.5 c x 70 sq.mm1.1 KV grade XLPE Insulated FRLS sheathed armoured aluminium conductor cable | Sets | 0 |  | 0
0
h | 3.5 c x 50 sq.mm1.1 KV grade XLPE Insulated FRLS sheathed armoured aluminium conductor cable | Sets | 2 |  | 0
0
i | 4 c x 35 sq.mm1.1 KV grade XLPE Insulated FRLS sheathed armoured aluminium conductor cable | Sets | 0 |  | 0
0
j | 4 c x 25 sq.mm1.1 KV grade XLPE Insulated FRLS sheathed armoured copper conductor cable | Sets | 0 |  | 0
0
k | 4 c x 25 sq.mm1.1 KV grade XLPE Insulated FRLS sheathed armoured AL conductor cable | Sets | 64 |  | 0
0
l | 4 c x 16 sq.mm1.1 KV grade XLPE Insulated FRLS sheathed armoured aluminium conductor cable | Sets | 0 |  | 0
0
m | 4 c x 16 sq.mm 1.1 KV grade XLPE Insulated FRLS sheathed armoured copper conductor cable | Sets | 4 |  | 0
0
n | 4 c x 10 sq.mm 1.1 KV grade XLPE Insulated FRLS sheathed armoured copper conductor cable | Sets | 12 |  | 0
0
p | 4 c x 6 sq.mm 1.1 KV grade XLPE Insulated FRLS sheathed armoured copper conductor cable for VRV ODUs | Sets | 0 |  | 0
0
q | 4 c x 4 sq.mm 1.1 KV grade XLPE Insulated FRLS sheathed armoured copper conductor cable | Sets | 4 |  | 0
0
s | 4 c x 2.5 sq.mm 1.1 KV grade PVC Insulated FRLS sheathed armoured copper conductor cable | Sets | 0 |  | 0
0
u | 3 c x 6 sq.mm 1.1 KV grade XLPE Insulated FRLS sheathed armoured copper conductor cable | Sets | 4 |  | 0
0
w | 2 c x 16 sq.mm 1.1 KV grade XLPE Insulated FRLS sheathed armoured copper conductor cable | Sets | 4 |  | 0
0
x | 2 c x 10 sq.mm 1.1 KV grade XLPE Insulated FRLS sheathed armoured copper conductor cable | Sets | 0 |  | 0
0
aa | 1c x 10 sq.mm FRLS XLPE insulated flexible copper conductor cables | Sets | 0 |  | 0
0
ab | 1c x 16 sq.mm FRLS XLPE insulated flexible copper conductor cables | Sets | 0 |  | 0
0
ac | 1c x 25 sq.mm FRLS XLPE insulated flexible copper conductor cables | Sets | 0 |  | 0
0
ac | 1c x 35 sq.mm FRLS XLPE insulated flexible copper conductor cables | Sets | 16 |  | 0
0
| TOTAL CARRIED OVER TO SUMMARY |  |  |  | 0
0
E | RACEWAYS AND CABLE TRAYS |  |  |  | 0
| Note :- |  |  |  | 0
0
1 | Fabricating supplying to site of installation, installation on ceiling/ surface 1.6 mm thick M.S. powder coated raceways of height 50 mm and 2.0 mm thick openable cover, totally enclosed, the joints between two lengths of channels or between channel and junction box shall be joined together with 3 mm thick M.S. Powder coated coupler plates to make it dust and water proof. The cost shall including all supporting and fixing accessories including dash fasteners. (Orange colour for data and Blue colour for power) |  |  |  | 0
a | 250 mm (wide) x 50 mm (height) | RM | 30 |  | 0
b | 150 mm (wide) x 50 mm (height) | RM | 95 |  | 0
c | 100 mm (wide) x 50 mm (height) | RM | 50 |  | 0
d | 150 mm (wide) x 150 mm (height) | RM | 5 |  | 0
0
2 | Fabricating supplying to site of installation, in floor including chase cutting of floor,leveling, refilling and making good the same from 1.6 mm thick and 2 mm thick cover pregalvanised MS CRCA sheet, totally enclosed, height 40 mm . The two lengths of raceways shall be fitted with Collars , 50 mm wide, 3 mm thick , press fit type. The raceways shall be clamped to the floor slab with GI clamps , 3mm thick and shall be screwed to the floor slab. The joint between raceway and junction box will be made with GI flexible strip( 3 nos), 3 mm thick, 4 inches long ,15 mm wide which will be nut bolted to the Junction box complete as required etc. |  |  |  | 0
0
a | 300 mm x 300 x 60 mm (height) | Nos. | 7 |  | 0
b | 250 mm x 250 x 60 mm (height) | Nos. | 0 |  | 0
c | 200 mm x 200 x 60 mm (height) | Nos. | 15 |  | 0
d | 150 mm x 150 x 60 mm (height) | Nos. | 10 |  | 0
e | 100 mm x 100 x 60 mm (height) | Nos. | 4 |  | 0
0
3 | Fabricating supplying to site of installation, in floor including chase cutting of floor,leveling, refilling and making good the same from 1.6 mm thick and 2 mm thick cover pregalvanised MS CRCA sheet, totally enclosed, height 40 mm . The two lengths of raceways shall be fitted with Collars , 50 mm wide, 3 mm thick , press fit type. The raceways shall be clamped to the floor slab with GI clamps , 3mm thick and shall be screwed to the floor slab. The joint between raceway and junction box will be made with GI flexible strip( 3 nos), 3 mm thick, 4 inches long ,15 mm wide which will be nut bolted to the Junction box complete as required etc. |  |  |  | 0
0
a | 250 mm (wide) x 40 mm (height) | RM | 75 |  | 0
b | 150 mm (wide) x40 mm (height) | RM | 50 |  | 0
c | 100 mm (wide) x 40 mm (height) | RM | 130 |  | 0
0
5 | Fabricating supplying to site of installation, Junction boxes for floor raceways made from 2 mm thick , with 2.5 mm thick G.I. cover including providing neoprene gaskets between the cover and the junction box, cadmium plated flat/round head screws, height as per site condition,totally enclosed. Proper cutouts shall be made in the side walls for raceway entry wherever required. The junction box shall be all side walls should be welded expect top cover and all side walls shall have suitable size of rectangular knock out holes for taking raceways / conduits as required and not a complete cut out. The top cover should be sealed with M Seal to make it dust and water proof complete as required etc. |  |  |  | 0
0
a | 300 mm x 300 x 50 mm (height) | Nos. | 17 |  | 0
b | 200 mm x 200 x 50 mm (height) | Nos. | 11 |  | 0
c | 150 mm x 150 x 50 mm (height) | Nos. | 28 |  | 0
d | 100 mm x 100 x 50 mm (height) | Nos. | 10 |  | 0
0
6 | Design manufacture , supply and fixing in position the cable trays of the following sizes for supporting 1.1 KV grade armoured/unarmoured aluminium /copper conductor cables. Fabricate the cable trays from perforated 1.6/2mm thick M.S. CRCA sheet duly galvanised with expansion coupler plates duly galvanised, with bolts, washer and nuts. Knock out holes for cable connections as per approved design. The tray should comply with the specification of NEC (National Electric Codes) and NEMA (National Electric Manufacturers Association). The steel should be as per IS:226 and galvanising as per IS :2629/BS 729/ASTM 123. The rate shall also include for supporting steel , fish plates , fixing accessories , nuts bolts, supporting down rods , dash fastener, cutting the RCC etc. complete as required. (the horizontal and vertical bends, T's should be factory fabricated and the rate should include for the same) |  |  |  | 0
0
a | 100 mm wide x 40 mm x 2.0 mm thk | RM | 0 |  | 0
b | 150 mm wide x 40 mm x 2.0 mm thk | RM | 65 |  | 0
c | 300 mm wide x 40 mm x 2.0 mm thk | RM | 40 |  | 0
d | 450 mm wide x 40 mm x 2.0 mm thk | RM | 10 |  | 0
e | 600 mm wide x 40 mm x 2.0 mm thk | RM | 0 |  | 0
0
7 | Design manufacture , supply and fixing in position the Ladder Type cable trays of the following sizes for supporting 1.1 KV grade armoured/unarmoured aluminium /copper conductor cables. Fabricate the cable trays to from Ladder Type 2.0 mm thick M.S. Flat/ Angle iron with bolts, washer and nuts. as per approved design. The tray should comply with the specification of NEC (National Electric Codes) and NEMA (National Electric Manufacturers Association). The steel should be as per IS:226 and galvanising as per IS :2629/BS 729/ASTM 123. The rate shall also include for supporting steel ,jointing fish plates , fixing accessories , nuts bolts, supporting down rods, dash fastener, cutting the RCC etc. complete as required. |  |  |  | 0
0
a | 300 mm wide x 50 mm x 2.0 mm thk | RM | 2 |  | 0
8 | Fabricating ,supplying to site of installation, installation of 500 mm size of 105 mm height mesh type EZ -Electroplated Zinc ( Legrand - Cablofil make ) cable tray including threaded G.I. down rods, dash fasteners , cablofil fixing accesories etc. complete as required. Cablofil make | RM | 6 |  | 0
0
| TOTAL CARRIED OVER TO SUMMARY |  |  |  | 0
0
F | DISTRIBUTION BOARDS |  |  |  | 0
0
1 | Supply,inginstalling ,connecting testing and commissioning of the following double door 1/4 rows vertical type 1.6 mm thick and 1. 4 thick door sheet steel enclosed fully recessed type, TPN Miniature Circuit Breakers Distribution Boards dust proof, verm­in proof, with hinged and lockable doors complete with DP MCB's and inter-connection with copper wire , insulated copper bus bar , cable glands­/conduit entry bushes, bonding to earth and paint­ing. Also provide separate neutral busbar for each phase. Provide separate Earth Links for each phase. Use brass thimbles for connections of all wires. 1 row for single phase and 4 rows for 3 phase. Provide separate 4 way 63 A main neutral link also. The phase busbar links shall be factory pre insulated. |  |  |  | 0
| Note :- The IP rating of the DB should be IP 43 . |  |  |  | 0
| Provide DB charts in laminated sheets in all Distribution Boards |  |  |  | 0
| A4 size SLD to be fixed on all DBs. |  |  |  | 0
0
1 | Light & Power Distribution Board |  |  |  | 0
0
a | 10 Way TPN DB, each phase consisting of 8 Nos. 10/20 AMP SP MCB’s and controlled by one number 100 mA sensitivity 63 AMPS DP RCCB backed up with 1 no 63 Amps 4 pole MCB. For VRV DB | Nos | 0 |  | 0
0
b | 12 Way TPN DB, each phase consisting of 10 Nos. 10/20 AMP SP MCB’s and controlled by one number 100 mA sensitivity 63 AMPS DP RCCB backed up with 1 no 63 Amps 4 pole MCB. For Light DB | Nos | 2 |  | 0
0
c | 14 Way TPN DB, each phase consisting of 12 Nos. 10/20 AMP SP MCB’s and controlled by one number 100 mA sensitivity 63 AMPS DP RCCB backed up with 1 no 63 Amps 4 pole MCB. For Power DB | Nos | 2 |  | 0
0
d | 12 Way SPN DB, consisting of 8 Nos. 10/20 AMP SP MCB’s and controlled by one number 100 mAsensitivity 63 AMPS DP RCCB backed up with 63 Amps DP MCB as incomer. For Emg DB | Nos | 2 |  | 0
0
2 | UPS Distribution Boards (All MCB's in workstation DB's should be D Curve) |  |  |  | 0
0
a | 12 Way TPN DB, each phase consisting of 10 Nos. 10/20 AMP SP MCB’s and controlled by one number 63 AMPS DP RCCB (100 mA) for each phase and 1 no. 63 amps 4 pole MCB incomer. | Nos.. | 1 |  | 0
0
b | 14 Way TPN DB, each phase consisting of 12 Nos. 10/20 AMP SP MCB’s and controlled by one number 63 AMPS DP RCCB (100 mA) for each phase and 1 no. 63 amps 4 pole MCB incomer. | Nos.. | 1 |  | 0
0
c | 12 Way SPN DB, consisting of 18 Nos. 10/20 AMP SP MCB’s and controlled by one number 100 mA sensitivity 63 AMPS DP RCCB backed up with 63 Amps DP MCB. For UPS DB | Nos.. | 0 |  | 0
0
d | 12 Way SPN DB, consisting of 4 Nos. 25/32 AMP DP MCB’s and controlled by one number 100 mA sensitivity 63 AMPS DP RCCB ( 100 mA) for backed up with 63 Amps 4D MCB. The bus bar shall be Twin bus bar. For SERVER DB | Nos.. | 2 |  | 0
0
3 | Supply, installation, testing and commissioning of sheet metal with 40 A DP MCB. This shall include cable entry boxes both for incoming and outgoing cable). For 6 KVA UPS. | Nos. | 1 |  | 0
0
4 | Supply, installation, testing and commissioning of sheet metal with 32 A DP MCB. This shall include cable entry boxes both for incoming and outgoing cable). For 2 KVA UPS. | Nos. | 1 |  | 0
0
5 | Supply, installation, testing and commissioning of sheet metal weather proof enclosure with 63 A FP RCBO(300mA) This shall include cable entry boxes both for incoming and outgoing cable) For VRV units. The enclosure shall be IP 42. For VRV Out Door units | Nos. | 12 |  | 0
0
6 | Supply, installation, testing and commissioning of sheet metal weather proof enclosure with 40 A FP RCBO(300mA) This shall include cable entry boxes both for incoming and outgoing cable) For VRV units. The enclosure shall be IP 42. For VRV Out Door units | Nos. | 4 |  | 0
0
7 | Supply, installation, testing and commissioning of sheet metal weatherproof Enclosure with 25/32 A DP MCB. This shall include cable entry boxes both for incoming and outgoing cable). | Nos. | 0 |  | 0
0
8 | Supply, installation, testing and commissioning of sheet metal with 16 A FP MCB. This shall include cable entry boxes both for incoming and outgoing cable). | Nos. | 1 |  | 0
0
| TOTAL CARRIED OVER TO SUMMARY |  |  |  | 0
0
G | SUB DISTRIBUTION PANELS |  |  |  | 0
0
1 | Sub Distribution Panels |  |  |  | 0
| Design, manufacture, supplying & installing at site in positioning, connecting, testing and commissioning of the following cubical type, dead front, 2mm thick sheet steel enclosed, free standing indoor type extendible Sub Distribution Panel with vermin proof hinged lockable doors for each compartment provide bus bar interconnections for incoming and outgoing including feeders earthing and painting and as per specifications. |  |  |  | 0
Note | Provide insulated dedicated earth link in all UPS Panels |  |  |  | 0
| All MCCB's 200 Amps and above shall be Microprocessor based |  |  |  | 0
| All Light & Power panel ,UPS and A.C. Panel incomer MCCB shall have Over current, Earth fault and short circuit protection. |  |  |  | 0
| All Incomer MCCB's in UPS Panels shall be Microprocessor based |  |  |  | 0
| The microprocessor based MCCBs shall have |  |  |  | 0
| Over Load (Phase) |  |  |  | 0
| Current setting Ir(Ir=XIn) OFF 0.4 to 1.0 in steps of 0.1 |  |  |  | 0
| Time delay , tr( Inverse) 10 sec at 6/r |  |  |  | 0
| Over Load (Neutral) |  |  |  | 0
| Current setting In (Intrl =XIr) 0.5, 0.75&1.00 Intrl |  |  |  | 0
| Inverse 10 sec at 6 Intrl/Fixed 200ms |  |  |  | 0
| Short Circuit setting -2- 10 |  |  |  | 0
| Instantaneous - 1.5-1 |  |  |  | 0
| All MCB's in UPS Panels shall be D Curve |  |  |  | 0
| In all Electrical panels protective acrylic sheet to be provided in cable alley and feeders. |  |  |  | 0
| The meters shall be able to monitor all major power quality parameters Voltage , current , frequency , KVAH,KWH,Power factor and individual,harmonics, ethernet ready - IEC-625-22. |  |  |  | 0
| The ATS shall be 4 pole with inbuilt manual operating switch. In case the controller of the ATS fails it should be capable of transferring the load while the ATS is in maintenance. The ATS and controller should be same make |  |  |  | 0
| Provide On / Off and trip indicating lamp on main incomer only. |  |  |  | 0
| Panel construction shall be Form 3b for all Panels with MCCB outgoings and Form 2b for all Panels with MCB's outgoings. |  |  |  | 0
| The Earth fault release/relay and CBCTs shall be same make as OEM Switchgear been used in the Panels. It shall not trip on imbalance of load. |  |  |  | 0
| All meters shall have Modbus card for BMS connectivity |  |  |  | 0
| All the Electrical Panels shall be in accordance with IS 8623 standards |  |  |  | 0
0
a | The SDB L&P in UPS room shall consists of : |  |  |  | 0
0
| MAIN INCOMER |  |  |  | 0
| 1 Nos. 500 A TPN MCCB (25KA/1 sec)( O/C, S/C,E/F) and neutral isolation link 100% of rated current. Terminals suitable to receive 2R x 3.5c x 240 sq. mm . Al Ar cable connection on one side and Busbar connection on the other side. |  |  |  | 0
0
| BUSBAR |  |  |  | 0
| 600 amps 4P busbar chamber of suitable length with Aluminium busbars. All busbars and interconnections shall be of suitable size aluminium strips current density of aluminium shall not be more than 0.8 Amps/ sq.mm.provide 100% capacity for neutral bus bar. |  |  |  | 0
0
| INDICATING PANELS |  |  |  | 0
| 3 nos phase indicating lamps (LED type) each backed up with MCB and switch shall be provided for each incomer. |  |  |  | 0
| Provide Intelligent Panel Meter - multifunctional meter with RS485 for all incoming feeder |  |  |  | 0
| Provide Transient Voltage Surge Suppressor Rating 40kA class II along with 63 A MCCB. Including all necessary accessories. For Switching Operation on each incomer. |  |  |  | 0
| Provide earth fault protection (EF) in the incomer MCCB |  |  |  | 0
0
| OUTGOINGS |  |  |  | 0
| 1 Nos. 400 A TPN MCCB (36 kA/ 1 sec) terminal to receive suitable Cable on one side and Busbar connection on the other side. |  |  |  | 0
| 1 Nos. 100 A TPN MCCB (36 kA/ 1 sec) terminal to receive suitable Cable on one side and Busbar connection on the other side. |  |  |  | 0
| 8 Nos. 63 A 4P MCB (10 kA/ 1 sec) terminal to receive suitable Cable on one side and Busbar connection on the other side. |  |  |  | 0
| 2 Nos. 16 A 4P MCB (10 kA/ 1 sec) terminal to receive suitable Cable on one side and Busbar connection on the other side. |  |  |  | 0
| 2 Nos. 40 A DP MCB (10 kA/ 1 sec) terminal to receive suitable Cable on one side and Busbar connection on the other side. |  |  |  | 0
| 2 Nos. 32 A DP MCB (10 kA/ 1 sec) terminal to receive suitable Cable on one side and Busbar connection on the other side. |  |  |  | 0
0
| The SDB L&P as described above and specifications complete | Set | 1 |  | 0
0
b | The UPS SDB in UPS Room shall consists of : |  |  |  | 0
0
| MAIN INCOMER |  |  |  | 0
| 1 No. 100 A 4P MCCB (25KA/1 sec)( O/C, S/C,E/F). Terminals suitable to receive 4R x 1c x 25 sq. mm Cu. Flexible cable connection on one side and Busbar connection on the other side. |  |  |  | 0
0
| BUSBAR |  |  |  | 0
| 150 amps 4P busbar chamber of suitable length with Copper busbars. All busbars and interconnections shall be of suitable size copper strips current density of copper shall not be more than 1.6 Amps/ sq.mm. |  |  |  | 0
0
| INDICATING PANELS |  |  |  | 0
| 3 nos phase indicating lamps (LED type) each backed up with MCB and switch shall be provided for each incomer. |  |  |  | 0
| Provide on/off indication lamp on each incomer and buscoupler. |  |  |  | 0
| Provide Intelligent Panel Meter - multifunctional meter with RS485 for all incoming feeder |  |  |  | 0
| Provide Transient Voltage Surge Suppressor Rating 40kA class I&II along with 63 A MCB. Including all necessary accessories. For Switching Operation on each incomer. |  |  |  | 0
| Provide earth fault protection (EF) in the incomer MCCB |  |  |  | 0
0
| OUTGOINGS |  |  |  | 0
| 4 Nos. 63 A 4P MCB (10 kA/ 1 sec) terminal to receive suitable Cable on one side and Busbar connection on the other side. |  |  |  | 0
| 2 Nos. 63A DP MCB (10 kA/ 1 sec) terminals to receive suitable Copper Ar. Cable on one side and Busbar connection on the other side. |  |  |  | 0
| The above Panel as described above and specifications complete | Set | 1 |  | 0
0
c | The HVAC Panel at terrace shall consists of : |  |  |  | 0
| It is outdoor type |  |  |  | 0
0
| MAIN INCOMER |  |  |  | 0
| Main Incomer 1 Nos 400A TPN MCCB (36KA) and neutral isolation link 100% of rated current.Terminals suitable to receive 2R x 3.5c x 150 sq. mm AL cable connection on one side and Busbar connection on the other side. |  |  |  | 0
0
| BUSBAR |  |  |  | 0
| 500 amps 4P busbar, chamber of suitable length with aluminium busbars. All busbars and interconnections shall be of suitable size Al strips current density of Al shall not be more than 0.8 Amps/ sq.mm. |  |  |  | 0
0
| INDICATING PANELS |  |  |  | 0
| 3 nos phase indicating lamps (LED type) each backed up with MCB and switch shall be provided for each incomer. |  |  |  | 0
| Provide Intelligent Panel Meter - Dual Source Energy Meter EM 6438 with RS 485 port for all incoming feeder |  |  |  | 0
| Provide TVSS (40KA) |  |  |  | 0
0
| OUTGOINGS |  |  |  | 0
0
| 17 Nos. 63 A 4P MCB (10 kA) terminals suitable to receive cable on one side and wire connection to Bus bars.. |  |  |  | 0
| 4 Nos. 40A 4P MCB (10 kA) terminals suitable to receive cable on one side and wire connection to Bus bars.. |  |  |  | 0
0
| The AC PANEL as described above and specifications complete as required. | Set | 1 |  | 0
0
2 | The contractor to submit reports of torque tightness tests for all the nut bolt cable joints in all the panels with red marking after the torque tightening has been done as per manufactures recommendation. | Set | 0 |  | 0
0
3 | Providing & fixing in position 1000 mm wide , Electrical Insulating Mats as per IS 15652:2006, 2mm thick, suitable up to 3.3 KV , fire retardant,no effect of acids, alkalies and transformer oils, moisture proof, high tensile strength and texture finish / cloth impression (Anti slip , marking on top) . | RM | 5 |  | 0
0
4 | Replacement of existing 250 A tap off box with 400 A tap off box at site with all the necessary accessories complete as required. | Nos. | 0 |  | 0
0
5 | Supply & fixing in position approved shock treatment chart written in English, Hindi and Local language. These charts shall be framed in wooden frame & covered with clear glass. | Nos. | 1 |  | 0
0
6 | Supply & fixing in position the best quality danger notice boards of approved shape & size as reqd. by the local Electrical Inspecting Authority written in English, Hindi & local language. | Nos. | 1 |  | 0
0
7 | Supply & fixing in position the Electrical A 1 Size SLD chart in the UPS/electrical room . These charts shall be framed in wooden frame & covered with clear glass. | Nos. | 1 |  | 0
0
8 | Supplying the first aid box as approved by John Ambulance society. | Nos. | 1 |  | 0
0
9 | Supply & Fixing of NO/NC Relay Module complete as required. | Nos. | 0 |  | 0
0
10 | 2 core -1.5 sq.mm PVC FRLS wires in already laid suitable size of M.S conduit complete as required. | Rmt | 0 |  | 0
0
11 | Supply, Installations, Testing and Commissioning of 2 Kg Fire Suppression System (CQRS) in all Floor Panels of Electrical and UPS Room to be included. - Automatic Direct Low Pressure Fire Suppression System, UL Listed FK-5-1-12 Extinguishing Fluid shall be filled in UL Listed Cylinder, UL Listed Pressure Switch should be integrated in DLP Valve for Indication on Fire Suppression Panel and Main Fire Alarm System, 15 Meter UL Listed Detection Tube shall be UV Protected made of Modified Polyamide associated with End of Line Adapter with Pressure Gauge, master Control Panel with A/V Alarm and Battery Backup along with Potential Free Contact to integrate with existing Fire Alarm System for Central Monitoring. Mounting Bracket with all necessary accessories. complete in all respect. System Component Approval: Cylinder-UL Listed, Gas-UL Listed, Detection Tube-UL Listed, Pressure Switch-UL Listed Make: FireMech / Ceasefire / Honeywell | Nos. | 0 |  | 0
0
| TOTAL CARRIED OVER TO SUMMARY |  |  |  | 0

## Elect CONTROL
Sl.No. | Description | Unit
|  |  | Qty | Rate In Rs. | Amount in Rs.
A. | POINT WIRING
All wires shall be FRLS PVC insulated copper conductor. Point wiring rates are inclusive of 3 x 1.5 sq mm insulated copper conductor wires for circuit.(from DB to switch board).
All sockets to be checked with a Check Plug socket tester for live-neutral reverse, no earth,neutral fault, live earth reverse, neutral earth reverse.
The Circuit No. and DB no. label shall be provided on all UPS ,RAW sockets and switchboards with label printer.
Colour coding for conduits to be done for different systems. The whole length of conduits to be painted.
All circuit & point wiring shall be colour coded & shall have ferruling on both end for circuit identification complete as required etc.Labelling on all the switches and sockets to be done with respect to DB reference, phase and circuit no.
Earth loop Impedance Test to be performed. RCD test to be done. Cable Insulation Tests to be done.
Wherever the occupancy sensor is provided in the cabin/ meeting rooms/workstations , the circuit wires from Distribution Board to occupancy sensor and sensor to switch are inclusive in the point wiring rate.
Labeling of all sockets and emergency lights to be provided and Ferruling for all the circuits to be considered
1 | Wiring for the following light points with 3x1.5 Sq.mm FRLS PVC insulated stranded copper conductor wires in concealed M.S. conduits in F.ceiling/walls/ceiling as directed including providing and fixing of 6 amps flush type switches, 5 sided G.I Boxes for housing switc­hes and earth­ing complete as required. Rates are inclusive of 3 x 1.5 sq mm FRLS PVC insulated stranded copper conductor wires for circuit |  |  |  | 0
0
a. | First point controlled by one no. 6 amp switch. | Nos. | 50 |  | 0
0
2 | Same as item No. 1a above but LOOP POINT i.e. wiring of point looped from first point with 3 x 1.5 sq. mm FRLS PVC insulated copper conductor wire in concealed/exposed MS conduit and earthing | Nos. | 98 |  | 0
0
3 | Wiring for the following light points with 1.5 Sq.mm FRLS PVC insulated stranded copper conductor wires in concealed M.S. conduits in F.ceiling/walls/ceiling as direc­ted including providing and fixing of 6 amps flush type switches, 5 sided G.I Boxes for housing switc­hes and earth­ing comple­te as required. Rates are inclusive of 3 x 1.5 sq mm FRLS PVC insulated stranded copper conductor wires for circuit |  |  |  | 0
0
a. | First point controlled by one no. 16 amp switch. | Nos. | 0 |  | 0
0
4 | Wiring for the following light points controlled by MCB in DB (Cost of MCB has been taken elsewhere in the tender) with 3 x 1.5 sq. mm FRLS PVC insulated copper conductor wires in concealed/exposed M.S. conduits as called for and earthing. |  |  |  | 0
0
a. | First point controlled by existing MCB in D.B. To first light Em Light | Nos. | 3 |  | 0
0
5 | Same as item No. 4.a above but LOOP POINT i.e. wiring of point looped from first point with 3x1.5 sq. mm FRLS PVC. insulated copper conductor wire in concealed/exposed M.S. conduit and earthing | Nos. | 28 |  | 0
0
6 | SITC of 2C x 1.5 sq mm non shielded Cable for DALI Ballast wiring in 25 mm dia MS conduit with all fixing accessories complete as required | Rmt. | 0 |  | 0
0
7 | SITC of 4C x 1.5 sq mm shielded Cable for QSM wiring in suitable size of MS conduit with all fixing accessories complete as required. Cable Common – 12 AWG (4.0 mm2); Power – 12 AWG (4.0 mm2); MUX Data – 22 AWG (0.25 mm2); Data – 22 AWG (0.25 mm2); Sense Line – 18 AWG (0.75 mm2); Drain Wire – 24 AWG (0.2 mm2) | Rmt. | 0 |  | 0
0
8 | Wiring for 6/16 amps outlets with 3 X 2.5 sq.mm FRLS PVC insulated copper conductor wires in M.S. Conduits in ceiling/walls/floor as direc­ted incl­u­ding providing & fixing of 6/16 amps flush type 5 pin socket and 16 amps switch with cover plate, 5 sided G.I boxes for housing switches, sockets and earthi­ng complete as required. (for general areas 4 nos loop in one circuits) | Nos. | 27 |  | 0
0
9 | Wiring for inline fan points with 2 x 2.5 sq.mm FRLS PVC insulated stranded copper con­ductor wires in concealed M.S. conduits in F.ceiling/ walls/ Ceiling as directed including providing and fixing of 16 amps flush type switches 16 amps 3 pin socket near inline fan, 5 sided G.I. boxes for housing switches and 16 amps 3 pin socket outlet and earthing and complete as required.(including body earth for GI boxes) | Nos. | 7 |  | 0
0
10 | Wiring for Geyser/Projector/Hand Dryer points with 2 x 4 + 1 x 4 sq mm FRLS PVC insulated copper conductor wires in concealed M.S. conduits in F.ceiling/ walls/ Ceiling as directed including providing & fixing 16 amps flush type switch near the white board and 6/16 amps 6 pin socket near the projector in ceiling , 5 sided G.I. boxes for housing switches and 6/16 A 6 pin socket outlet , earthing and complete as required.(including body earth for GI boxes) ( 1 point per circuit) | Nos. | 6 |  | 0
0
11 | Wiring for VRV Indoor units with 3 x 2.5 sq.mm FRLS PVC insulated stranded copper conductor wires in concealed M.S. conduits in F.ceiling/ walls/ Ceiling as directed including providing providing and fixing of 6 amps flush type switches 16 amps 3 pin socket near VRV points, 5 sided G.I. boxes for housing switches and 16 amps 3 pin socket outlet and earthing and complete as required.(including body earth for GI boxes) (1 point per circuit) | Nos. | 22 |  | 0
0
12 | Wiring for VAV /fire damper points with 3 x 2.5 sq.mm FRLS PVC insulated copper conductor wires in concealed M.S. conduits in F.ceiling/ walls/ Ceiling as directed including providing & fixing 6 amps flush type switches, 6 amps 3 pin socket near VAV points, 5 sided G.I. boxes for housing switches and 6 A sockets earthing and complete as required. The sockets to be fused spur type (MK make). (including body earth for GI boxes) (8 to 10 points per circuits) | Nos. | 0 |  | 0
0
13 | Wiring for 16 amps power outlet poi­nts with 4 sq.mm FRLS PVC insulated stranded copper conductor wires in concealed/recessed M.S. conduit as directed including providing providing and fixing of 16 amps flush type switch and 6 pin socket with cover plate 5 sided G.I. outlet boxes for switches and socket and earthing the third pin with 2.5 sq mm FRLS PVC stranded copper wire complete as required (Only one outlet shall be connected on each circuit) (including body earth for GI boxes) | Nos. | 8 |  | 0
0
14 | Wiring for 16 amps power outlet points with 4 sq.mm FRLS PVC insulated stranded copper conductor wires for the first power outlet and 4 sq.mm FRLS PVC insu­lated stranded copper conductor wires for the second outlet, in concealed M.S. cond­uits in F.ceiling/ walls/Ceiling/floor ducts as directed including providing providing and fixing of 16 amps flush type switch and 6 pin socket with cover plate, 5 sided G.I. outlet boxes for housing switches and socket, and earthing the third pin with 2.5 sq.mm FRLS PVC insulated copper conductor wires complete as required (Two power out­lets shall be connected on each circuit)(including body earth for GI boxes) | Set of Two | 2 |  | 0
0
15 | Wiring for A/C outlet points with 4.0 sq mm FRLS PVC insulated stranded copper conductor wires in M.S. conduitl/wall/floor ducts as directed including providing 25 A socket with 25 amps SP MCB ( Tiny Trip) 5 sided GI Outlet Box for housing and socket and MCB and earthing with 2.5 sq. mm FRLS PVC insulated stranded Copper Conductor wires complete as required. | Nos. | 0 |  | 0
0
| Different colours to be used for 3 core cables for raw power and UPS power. |  |  |  | 0
16 | Wiring for UPS/Raw plug outlets points with three core, 2.5 sqmm FRLS PVC Insulated and PVC sheathed flexible cable with bright annealed electrolytic copper conductor, 1100 volt grade confirming to IS : 694-1990 with latest amendments, in existing Channels/ conduit in ceiling/walls/floor including all cable termination accessories) (including body earth for GI boxes). Colour Coding to be followed | RM | 1150 |  | 0
0
17 | Wiring for UPS/Raw plug outlets points with three core, 4.0 sqmm FRLS PVC Insulated and PVC sheathed flexible cable with bright annealed electrolytic copper conductor , 1100 volt grade confirming to IS : 694-1990 with latest amendments, in existing Channels/ conduit in ceiling/walls/floor inclu­ding all cable termination accessories) Earthing of GI Box to be included. Colour Coding to be followed. For Lab & Kitchen Sockets | RM | 175 |  | 0
0
18 | Wiring for Power plug outlets points with three core, 6.0 sqmm FRLS PVC Insulated and PVC sheathed flexible cable with bright annealed electrolytic copper conductor , 1100 volt grade confirming to IS : 694-1990 with latest amendments, in existing Channels/ conduit in ceiling/walls/floor inclu­ding all cable termination accessories). Colour Coding to be followed. | RM | 45 |  | 0
0
19 | Wiring for Power plug outlets points with three core, 10.0 sqmm FRLS PVC Insulated and PVC sheathed flexible cable with bright annealed electrolytic copper conductor , 1100 volt grade confirming to IS : 694-1990 with latest amendments, in existing Channels/ conduit in ceiling/walls/floor inclu­ding all cable termination accessories). Colour Coding to be followed. | RM | 40 |  | 0
0
| The word UPS shall be printed on all UPS sockets. |  |  |  | 0
| The word RAW shall be printed on all RAW sockets. |  |  |  | 0
| The Circuit No. and DB no. label shall be provided on all UPS ,RAW sockets and switchboards with label printer. |  |  |  | 0
| Contractor is required to submit samples of all types of switches and sockets to Consultant and Architects representative for approval before ordering the material. |  |  |  | 0
0
20 | Providing and fixing of 1 Nos. 6 amp round pin type socket and 1 No. 6 amps switch cover plate, 5 sided G.I. Boxes for housing switches and sockets and earthing complete as required (for UPS/Raw). GI Box to have earth pin for body earthing | Nos. | 53 |  | 0
0
21 | Providing and fixing of 2 Nos. 6 amp round pin type socket and 1 No. 6 amps switch cover plate, 5 sided G.I. Boxes for housing switches and sockets and earthing complete as required (for UPS/Raw). GI Box to have earth pin for body earthing | Nos. | 63 |  | 0
0
22 | Providing and fixing of 3 Nos. 6 amp round pin type socket and 1 No. 6 amps switch cover plate, 5 sided G.I. Boxes for housing switches and sockets and earthing complete as required (for UPS/Raw). GI Box to have earth pin for body earthing | Nos. | 5 |  | 0
0
23 | Providing and fixing of 2 Nos. 6/16 amp round pin type socket and 1 No. 16 amps switch cover plate, 5 sided G.I. Boxes for housing switches and sockets and earthing complete as required (for UPS/Raw). GI Box to have earth pin for body earthing | Nos. | 2 |  | 0
0
24 | Providing and fixing of 1 No.16 amps flush type 6 pin socket and 1 No. 16 amps switch with indicator, cover plate, 5 sided G.I. Boxes for housing switches and sockets and earthing complete as required (for UPS / RAW) GI Boxes to have earth pin for body earthing | Nos. | 2 |  | 0
0
25 | Providing and fixing Underfloor Access Outlets (250 x 250 x 55 - mm 70 compartments 1Trap including providing 2 Nos 6 Amps Round Pin sockets and 1 no. 16 Amp Switch & 2 data outlet complete as required. | Nos. | 0 |  | 0
0
26 | Supply and fixing of the following sizes of thermoplastic moulded plug and socket IEC 309 type in PVC Box of suitable size flush / surface and making connections complete as required. The box shall be IP 44. |  |  |  | 0
a | 3 pin 16/20 A 1 phase industrial socket with mcb & plug top | Nos. | 0 |  | 0
b | 3 pin 32 A 1 phase industrial socket plug top | Nos. | 2 |  | 0
0
27 | Providing and fixing in position the following M.S. conduits including all accessories concealed in F. ceiling/wall/floor as required including 1.6 mm thick M.S. junction or pull boxes with 3mm thick perspex sheet cover plate compl­te with 1.6 mm dia. G.I. pull wires in the length of conduit. |  |  |  | 0
0
a. | 20 mm dia conduit ( 1.6 mm thick) | RM | 60 |  | 0
b. | 25 mm dia conduit (1.6 mm thick) | RM | 110 |  | 0
c. | 32 mm dia conduit (2.0 mm thick) | RM | 75 |  | 0
0
28 | The Electrical Contractor shall provide sufficient temporary lighting for working in the Building total area 3600 sq. ft. divided in single floor and maintain the same till completion of the project.It shall include replacement of all fused/faulty lamps.It shall include providing 15 A plug sockets (industrial type with ON/OFF switch/MCB) on 4 sides walls one plug at every 5-8 meter distance. The Contractors will tap off supply from these plugs for his use. Tubelights to maintain a lighting level of 150 lux on the floor,.Each 15 A socket and each Light circuit shall be protected by suitable MCBs.Use three core PVC Insulated PVC sheathed copper conductor cables for wiring.The contractor shall salvage the complete wiring and take it back at the end of the project. | L.S. | 1 |  | 0
0
| TOTAL CARRIED OVER TO SUMMARY |  |  |  | 0
0
B. | CONDUITING FOR TELEPHONE , COMPUTER & CONDUITING AND WIRING FOR T.V. SYSTEM. |  |  |  | 0
0
1 | Providing and fixing in position the following M.S. conduits including all accessories concealed in F. ceiling/wall/floor as required including 1.6 mm thick M.S. junction or pull boxes with 3mm thick perspex sheet cover plate compl­te with 1.6 mm dia. G.I. pull wires in the length of conduit. |  |  |  | 0
0
a. | 20 mm dia conduit( 1.6 mm wall thickness) | RM | 65 |  | 0
b. | 25 mm dia conduit ( 1.6 mm wall thickness) | RM | 120 |  | 0
c. | 32 mm dia conduit ( 1.6 mm wall thickness) | RM | 80 |  | 0
0
2 | Providing and fixing in position suitable 1.2 mm thick G.I./ PVC outlet box for RJ- 45 computer outlet with all fixing accessories as required. | Nos. | 15 |  | 0
0
3 | Supply and fixing of 1.2 mm thick G.I Box along with RG 11 TV Co axial socket with Cover Plate | Nos. | 1 |  | 0
0
4 | Supply drawing connecting testing and commissioning of TV Coaxial cable RG 6 in existing conduit | RM | 70 |  | 0
0
| TOTAL CARRIED OVER TO SUMMARY |  |  |  | 0
0
C. | EARTHING |  |  |  | 0
0
1 | Providing and fixing in position the following copper strips and wires including providing all fixing accessories and effecting proper connections |  |  |  | 0
| Note:- MS Cable markers at the earth bus, panel and DB entries to be provided |  |  |  | 0
a. | G.I. tape 25 mm x 6 mm | RM | 120 |  | 0
b. | Copper tape 25mm x 3 mm | RM | 5 |  | 0
c. | GI wire 8 SWG | RM | 150 |  | 0
d. | GI wire 12 SWG | RM | 100 |  | 0
e. | Supply installation , and making of Exothermic weld suitable to bond GI strip of 25x5 mm with Copper Strip of 25x5 mm with 75mm extensions on either side | Nos. | 3 |  | 0
f. | Copper Earth Link connectors - 200 mm long, 25mm wide and 5 mm thick | Nos. | 2 |  | 0
0
2 | Supply and laying, effecting proper connec­tions, testing & commissioning of the following sizes of 1.1 KV armoured XLPE/ unarmoured FRLS sheathed XLPE insulation, conforming to IS: 7098 (Part-1)- 1988 ( 90 deg C) aluminium /copper conductor cables conforming to IS : 1554 and FRLS Insulated flexible copper cables as per IS 694 laid over MS supports in existing RCC ducts/ laid in ground /laid on Cable Trays including clamping the cables to sup­ports in an approved manner as required complete with all accessories. |  |  |  | 0
0
a | 1c x 50 sq.mm FRLS insulated flexible copper conductor cables | RM | 0 |  | 0
0
b | 1c x 35 sq.mm FRLS insulated flexible copper conductor cables | RM | 0 |  | 0
0
c | 1c x 25 sq.mm FRLS insulated flexible copper conductor cables | RM | 140 |  | 0
0
d | 1c x 16 sq.mm FRLS insulated flexible copper conductor cables | RM | 85 |  | 0
0
e | 1c x 10 sq.mm FRLS insulated flexible copper conductor cables | RM | 75 |  | 0
0
f | 1c x 6 sq.mm FRLS insulated flexible copper conductor cables | RM | 50 |  | 0
0
g | 2 Nos 1 x 10 Sq. mm FRLS insulated flexible copper conductor cables (Green Colour for UPS DB Sub-main Earthing) | RM | 0 |  | 0
0
3 | Supplying and making of end termination for the following size of compression lugs and PG Threaded Nylon Flexible cable glands complete with all fixing accessories as required |  |  |  | 0
0
a | 1c x 50 sq.mm FRLS insulated flexible copper conductor cables | Sets | 0 |  | 0
0
b | 1c x 35 sq.mm FRLS insulated flexible copper conductor cables | Sets | 0 |  | 0
0
c | 1c x 25 sq.mm FRLS insulated flexible copper conductor cables | Sets | 4 |  | 0
0
d | 1c x 16 sq.mm FRLS insulated flexible copper conductor cables | Sets | 6 |  | 0
0
d | 1c x 10 sq.mm FRLS insulated flexible copper conductor cables | Sets | 10 |  | 0
0
4 | Providing earthing station at loca­tion as called for including provid­ing 600 mm x 600 mm x 3 mm thick tinned copper electrode 2 Nos 25 x 3 mm copper strip (for body earthing GI strip can be considerd) up to ground level 20mm dia medium class GI pipe (India Tube Company make or approved equal) CI funnel with 20 gauge GI wire mesh, masonry chamber with concrete base, CI man­hole cover (cover to be heavy duty) with frame (300mm x 300mm) and bitumastic paint and packing the fixture of charcoal and common salt around plate electrode complete as per I.S. ( Minimum depth shall be 4.2 M ) for UPS & Server | Nos. | 0 |  | 0
0
5 | Supply, Installation, testing and commissioning of Maintenance Free Earthing of make Electrolytic Earthing comprising of type 'K' copper 2.4 mm wall thickness, hollow tube 10 feet long, 2.125 inches outer diameter completely filled with non hazardous metallic salts (Terrafill) to achieve an earth resistance of less than 1 ohms. Provide masonry chamber with concrete base, CI man­hole cover (cover to be heavy duty) with frame (300mm x 300mm) and make earth pit sign/ identifcation no in each earth station for UPS & Server | Nos. | 3 |  | 0
0
6 | Supply, installation, testing and commissioning of sheet metal enclosed 450 x 200 x 150 (D) mm insulated earth distribution board with 1 nos. 50 x 6 mm copper tinned earth bars on SMC insulator suitable for 6/8 nos connections complete with all fixing accessories as required. | Nos. | 1 |  | 0
0
7 | Supply, installation, testing and commissioning of sheet metal enclosed 300 x 200 x 150 ( D) mm insulated earth distribution board with 1 nos. 32 x 6 mm copper tinned earth bars on SMC insulator suitable for 6/8 nos connections complete with all fixing accessories as required. | Nos. | 3 |  | 0
0
8 | Supplying and laying of the following sizes of Heavy duty PVC Pipes below paved area including chase cutting and back filling. |  |  |  | 0
a. | 100 mm outer dia | RM | 0 |  | 0
b. | 80 mm outer dia | RM | 10 |  | 0
0
| TOTAL CARRIED OVER TO SUMMARY |  |  |  | 0
0
D | CABLES, MAINS & SUBMAINS |  |  |  | 0
0
1 | Supply and laying, effecting proper connec­tions, testing & commissioning of the following sizes of 1.1 KV armoured XLPE/ unarmoured FRLS sheathed XLPE insulation, conforming to IS: 7098 (Part-1)- 1988 ( 90 deg C) aluminium /copper conductor cables conforming to IS : 1554 and FRLS Insulated flexible copper cables as per IS 694 laid over MS supports in existing RCC ducts/ laid in ground /laid on Cable Trays including clamping the cables to sup­ports in an approved manner as required complete with all accessories. |  |  |  | 0
0
| Note : All cables to be glanded and crimped with suitable sized lugs. All Cable trays to be double earthed. All raceways and cable glands to be earthed with brass round earth clips and wires. |  |  |  | 0
| Earthing ring to be included in all the cable glands. |  |  |  | 0
| Sub main cables should be labelled at both ends |  |  |  | 0
| Joints shall be allowed only at the 2 ends of the cables and not in between. |  |  |  | 0
0
a | 3.5 c x 300 sq.mm1.1 KV grade XLPE Insulated FRLS sheathed armoured aluminium conductor cable | RM | 0 |  | 0
0
b | 3.5 c x 240 sq.mm1.1 KV grade XLPE Insulated FRLS sheathed armoured aluminium conductor cable | RM | 0 |  | 0
0
c | 3.5 c x 185 sq.mm1.1 KV grade XLPE Insulated FRLS sheathed armoured aluminium conductor cable | RM | 0 |  | 0
0
d | 3.5 c x 150 sq.mm1.1 KV grade XLPE Insulated FRLS sheathed armoured aluminium conductor cable | RM | 0 |  | 0
0
e | 3.5 c x 120 sq.mm1.1 KV grade XLPE Insulated FRLS sheathed armoured aluminium conductor cable For SDB L&P (Assumed) | RM | 60 |  | 0 | 2
0
f | 3.5 c x 95 sq.mm1.1 KV grade XLPE Insulated FRLS sheathed armoured aluminium conductor cable | RM | 0 |  | 0
0
g | 3.5 c x 70 sq.mm1.1 KV grade XLPE Insulated FRLS sheathed armoured aluminium conductor cable | RM | 70 |  | 0 | 2
0
h | 3.5 c x 50 sq.mm1.1 KV grade XLPE Insulated FRLS sheathed armoured aluminium conductor cable | RM | 0 |  | 0
0
i | 4 c x 35 sq.mm1.1 KV grade XLPE Insulated FRLS sheathed armoured aluminium conductor cable | RM | 0 |  | 0
0
j | 4 c x 25 sq.mm1.1 KV grade XLPE Insulated FRLS sheathed armoured aluminium conductor cable For DB and VRV ODU | RM | 330 |  | 0 | 6
0
k | 4 c x 25 sq.mm1.1 KV grade XLPE Insulated FRLS sheathed armoured copper conductor cable | RM | 0 |  | 0
0
l | 4 c x 16 sq.mm1.1 KV grade XLPE Insulated FRLS sheathed armoured aluminium conductor cable | RM | 0 |  | 0
0
m | 4 c x 16 sq.mm 1.1 KV grade XLPE Insulated FRLS sheathed armoured copper conductor cable For UPS DB | RM | 35 |  | 0 | 2
0
n | 4 c x 10 sq.mm 1.1 KV grade XLPE Insulated FRLS sheathed armoured copper conductor cable | RM | 70 |  | 0
0
p | 4 c x 6 sq.mm 1.1 KV grade XLPE Insulated FRLS sheathed armoured copper conductor cable | RM | 0 |  | 0
0
q | 4 c x 4 sq.mm 1.1 KV grade XLPE Insulated FRLS sheathed armoured copper conductor cable | RM | 25 |  | 0 | 4
0
s | 4 c x 2.5 sq.mm 1.1 KV grade XLPE Insulated FRLS sheathed armoured copper conductor cable | RM | 0 |  | 0
0
t | 3 c x 10 sq.mm 1.1 KV grade PVC Insulated FRLS Armoured copper conductor cable | RM | 0 |  | 0
0
u | 3 c x 6 sq.mm 1.1 KV grade XLPE Insulated FRLS sheathed armoured copper conductor cable For Emg & Server DB | RM | 90 |  | 0 | 6
0
x | 2 c x 10 sq.mm 1.1 KV grade XLPE Insulated FRLS sheathed armoured copper conductor cable For UPS DB | RM | 35 |  | 0 | 2
0
z | 1c x 6 sq.mm FRLS XLPE insulated flexible copper conductor cables | RM | 0 |  | 0
0
aa | 1c x 10 sq.mm FRLS XLPE insulated flexible copper conductor cables | RM | 75 |  | 0 | 14
0
ab | 1c x 16 sq.mm FRLS XLPE insulated flexible copper conductor cables | RM | 0 |  | 0
0
ac | 1c x 25 sq.mm FRLS XLPE insulated flexible copper conductor cables | RM | 0 |  | 0
0
ad | 1c x 35 sq.mm FRLS XLPE insulated flexible copper conductor cables | RM | 0 |  | 0
0
2 | Supplying and making terminal joints for the following size of 1.1 KV PVC insulated copper conductor armoured cables including providing heavy duty tinned copper terminal crimping lugs, solder, insulation tape, approved sealing epoxy compound, double compression brass cable glands, effecting gland connec­tions and effecting terminal connections to the equipment complete as required. Use compression lugs and PG Threaded Nylon Flexible cable glands for single core flexible cables |  |  |  | 0
0
a | 3.5 c x 300 sq.mm1.1 KV grade XLPE Insulated FRLS sheathed armoured aluminium conductor cable | Sets | 0 |  | 0
0
b | 3.5 c x 240 sq.mm1.1 KV grade XLPE Insulated FRLS sheathed armoured aluminium conductor cable | Sets | 0 |  | 0
0
c | 3.5 c x 185 sq.mm1.1 KV grade XLPE Insulated FRLS sheathed armoured aluminium conductor cable | Sets | 0 |  | 0
0
d | 3.5 c x 150 sq.mm1.1 KV grade XLPE Insulated FRLS sheathed armoured aluminium conductor cable | Sets | 0 |  | 0
0
e | 3.5 c x 120 sq.mm1.1 KV grade XLPE Insulated FRLS sheathed armoured aluminium conductor cable | Sets | 2 |  | 0
0
f | 3.5 c x 95 sq.mm1.1 KV grade XLPE Insulated FRLS sheathed armoured aluminium conductor cable | Sets | 0 |  | 0
0
g | 3.5 c x 70 sq.mm1.1 KV grade XLPE Insulated FRLS sheathed armoured aluminium conductor cable | Sets | 2 |  | 0
0
h | 3.5 c x 50 sq.mm1.1 KV grade XLPE Insulated FRLS sheathed armoured aluminium conductor cable | Sets | 0 |  | 0
0
i | 4 c x 35 sq.mm1.1 KV grade XLPE Insulated FRLS sheathed armoured aluminium conductor cable | Sets | 0 |  | 0
0
j | 4 c x 25 sq.mm1.1 KV grade XLPE Insulated FRLS sheathed armoured copper conductor cable | Sets | 0 |  | 0
0
k | 4 c x 25 sq.mm1.1 KV grade XLPE Insulated FRLS sheathed armoured AL conductor cable | Sets | 30 |  | 0
0
l | 4 c x 16 sq.mm1.1 KV grade XLPE Insulated FRLS sheathed armoured aluminium conductor cable | Sets | 0 |  | 0
0
m | 4 c x 16 sq.mm 1.1 KV grade XLPE Insulated FRLS sheathed armoured copper conductor cable | Sets | 2 |  | 0
0
n | 4 c x 10 sq.mm 1.1 KV grade XLPE Insulated FRLS sheathed armoured copper conductor cable | Sets | 8 |  | 0
0
p | 4 c x 6 sq.mm 1.1 KV grade XLPE Insulated FRLS sheathed armoured copper conductor cable for VRV ODUs | Sets | 0 |  | 0
0
q | 4 c x 4 sq.mm 1.1 KV grade XLPE Insulated FRLS sheathed armoured copper conductor cable | Sets | 4 |  | 0
0
s | 4 c x 2.5 sq.mm 1.1 KV grade PVC Insulated FRLS sheathed armoured copper conductor cable | Sets | 0 |  | 0
0
u | 3 c x 6 sq.mm 1.1 KV grade XLPE Insulated FRLS sheathed armoured copper conductor cable | Sets | 6 |  | 0
0
w | 2 c x 16 sq.mm 1.1 KV grade XLPE Insulated FRLS sheathed armoured copper conductor cable | Sets | 0 |  | 0
0
x | 2 c x 10 sq.mm 1.1 KV grade XLPE Insulated FRLS sheathed armoured copper conductor cable | Sets | 2 |  | 0
0
aa | 1c x 10 sq.mm FRLS XLPE insulated flexible copper conductor cables | Sets | 14 |  | 0
0
ab | 1c x 16 sq.mm FRLS XLPE insulated flexible copper conductor cables | Sets | 0 |  | 0
0
ac | 1c x 25 sq.mm FRLS XLPE insulated flexible copper conductor cables | Sets | 0 |  | 0
0
ac | 1c x 35 sq.mm FRLS XLPE insulated flexible copper conductor cables | Sets | 0 |  | 0
0
| TOTAL CARRIED OVER TO SUMMARY |  |  |  | 0
0
E | RACEWAYS AND CABLE TRAYS |  |  |  | 0
| Note :- |  |  |  | 0
0
1 | Fabricating supplying to site of installation, installation on ceiling/ surface 1.6 mm thick M.S. powder coated raceways of height 50 mm and 2.0 mm thick openable cover, totally enclosed, the joints between two lengths of channels or between channel and junction box shall be joined together with 3 mm thick M.S. Powder coated coupler plates to make it dust and water proof. The cost shall including all supporting and fixing accessories including dash fasteners. (Orange colour for data and Blue colour for power) |  |  |  | 0
a | 250 mm (wide) x 50 mm (height) | RM | 20 |  | 0
b | 150 mm (wide) x 50 mm (height) | RM | 75 |  | 0
c | 100 mm (wide) x 50 mm (height) | RM | 45 |  | 0
d | 150 mm (wide) x 150 mm (height) | RM | 5 |  | 0
0
2 | Fabricating supplying to site of installation, in floor including chase cutting of floor,leveling, refilling and making good the same from 1.6 mm thick and 2 mm thick cover pregalvanised MS CRCA sheet, totally enclosed, height 40 mm . The two lengths of raceways shall be fitted with Collars , 50 mm wide, 3 mm thick , press fit type. The raceways shall be clamped to the floor slab with GI clamps , 3mm thick and shall be screwed to the floor slab. The joint between raceway and junction box will be made with GI flexible strip( 3 nos), 3 mm thick, 4 inches long ,15 mm wide which will be nut bolted to the Junction box complete as required etc. |  |  |  | 0
0
a | 300 mm x 300 x 60 mm (height) | Nos. | 5 |  | 0
b | 250 mm x 250 x 60 mm (height) | Nos. | 0 |  | 0
c | 200 mm x 200 x 60 mm (height) | Nos. | 12 |  | 0
d | 150 mm x 150 x 60 mm (height) | Nos. | 8 |  | 0
e | 100 mm x 100 x 60 mm (height) | Nos. | 3 |  | 0
0
3 | Fabricating supplying to site of installation, in floor including chase cutting of floor,leveling, refilling and making good the same from 1.6 mm thick and 2 mm thick cover pregalvanised MS CRCA sheet, totally enclosed, height 40 mm . The two lengths of raceways shall be fitted with Collars , 50 mm wide, 3 mm thick , press fit type. The raceways shall be clamped to the floor slab with GI clamps , 3mm thick and shall be screwed to the floor slab. The joint between raceway and junction box will be made with GI flexible strip( 3 nos), 3 mm thick, 4 inches long ,15 mm wide which will be nut bolted to the Junction box complete as required etc. |  |  |  | 0
0
a | 250 mm (wide) x 40 mm (height) | RM | 50 |  | 0
b | 150 mm (wide) x40 mm (height) | RM | 35 |  | 0
c | 100 mm (wide) x 40 mm (height) | RM | 80 |  | 0
0
5 | Fabricating supplying to site of installation, Junction boxes for floor raceways made from 2 mm thick , with 2.5 mm thick G.I. cover including providing neoprene gaskets between the cover and the junction box, cadmium plated flat/round head screws, height as per site condition,totally enclosed. Proper cutouts shall be made in the side walls for raceway entry wherever required. The junction box shall be all side walls should be welded expect top cover and all side walls shall have suitable size of rectangular knock out holes for taking raceways / conduits as required and not a complete cut out. The top cover should be sealed with M Seal to make it dust and water proof complete as required etc. |  |  |  | 0
0
a | 300 mm x 300 x 50 mm (height) | Nos. | 12 |  | 0
b | 200 mm x 200 x 50 mm (height) | Nos. | 8 |  | 0
c | 150 mm x 150 x 50 mm (height) | Nos. | 21 |  | 0
d | 100 mm x 100 x 50 mm (height) | Nos. | 6 |  | 0
0
6 | Design manufacture , supply and fixing in position the cable trays of the following sizes for supporting 1.1 KV grade armoured/unarmoured aluminium /copper conductor cables. Fabricate the cable trays from perforated 1.6/2mm thick M.S. CRCA sheet duly galvanised with expansion coupler plates duly galvanised, with bolts, washer and nuts. Knock out holes for cable connections as per approved design. The tray should comply with the specification of NEC (National Electric Codes) and NEMA (National Electric Manufacturers Association). The steel should be as per IS:226 and galvanising as per IS :2629/BS 729/ASTM 123. The rate shall also include for supporting steel , fish plates , fixing accessories , nuts bolts, supporting down rods , dash fastener, cutting the RCC etc. complete as required. (the horizontal and vertical bends, T's should be factory fabricated and the rate should include for the same) |  |  |  | 0
0
a | 100 mm wide x 40 mm x 2.0 mm thk | RM | 0 |  | 0
b | 150 mm wide x 40 mm x 2.0 mm thk | RM | 45 |  | 0
c | 300 mm wide x 40 mm x 2.0 mm thk | RM | 30 |  | 0
d | 450 mm wide x 40 mm x 2.0 mm thk | RM | 5 |  | 0
e | 600 mm wide x 40 mm x 2.0 mm thk | RM | 0 |  | 0
0
7 | Design manufacture , supply and fixing in position the Ladder Type cable trays of the following sizes for supporting 1.1 KV grade armoured/unarmoured aluminium /copper conductor cables. Fabricate the cable trays to from Ladder Type 2.0 mm thick M.S. Flat/ Angle iron with bolts, washer and nuts. as per approved design. The tray should comply with the specification of NEC (National Electric Codes) and NEMA (National Electric Manufacturers Association). The steel should be as per IS:226 and galvanising as per IS :2629/BS 729/ASTM 123. The rate shall also include for supporting steel ,jointing fish plates , fixing accessories , nuts bolts, supporting down rods, dash fastener, cutting the RCC etc. complete as required. |  |  |  | 0
0
a | 300 mm wide x 50 mm x 2.0 mm thk | RM | 0 |  | 0
8 | Fabricating ,supplying to site of installation, installation of 500 mm size of 105 mm height mesh type EZ -Electroplated Zinc ( Legrand - Cablofil make ) cable tray including threaded G.I. down rods, dash fasteners , cablofil fixing accesories etc. complete as required. Cablofil make | RM | 4 |  | 0
0
| TOTAL CARRIED OVER TO SUMMARY |  |  |  | 0
0
F | DISTRIBUTION BOARDS |  |  |  | 0
0
1 | Supply,inginstalling ,connecting testing and commissioning of the following double door 1/4 rows vertical type 1.6 mm thick and 1. 4 thick door sheet steel enclosed fully recessed type, TPN Miniature Circuit Breakers Distribution Boards dust proof, verm­in proof, with hinged and lockable doors complete with DP MCB's and inter-connection with copper wire , insulated copper bus bar , cable glands­/conduit entry bushes, bonding to earth and paint­ing. Also provide separate neutral busbar for each phase. Provide separate Earth Links for each phase. Use brass thimbles for connections of all wires. 1 row for single phase and 4 rows for 3 phase. Provide separate 4 way 63 A main neutral link also. The phase busbar links shall be factory pre insulated. |  |  |  | 0
| Note :- The IP rating of the DB should be IP 43 . |  |  |  | 0
| Provide DB charts in laminated sheets in all Distribution Boards |  |  |  | 0
| A4 size SLD to be fixed on all DBs. |  |  |  | 0
0
1 | Light & Power Distribution Board |  |  |  | 0
0
a | 10 Way TPN DB, each phase consisting of 8 Nos. 10/20 AMP SP MCB’s and controlled by one number 100 mA sensitivity 63 AMPS DP RCCB backed up with 1 no 63 Amps 4 pole MCB. For VRV DB | Nos | 1 |  | 0
0
b | 12 Way TPN DB, each phase consisting of 10 Nos. 10/20 AMP SP MCB’s and controlled by one number 100 mA sensitivity 63 AMPS DP RCCB backed up with 1 no 63 Amps 4 pole MCB. For Light DB | Nos | 1 |  | 0
0
c | 14 Way TPN DB, each phase consisting of 12 Nos. 10/20 AMP SP MCB’s and controlled by one number 100 mA sensitivity 63 AMPS DP RCCB backed up with 1 no 63 Amps 4 pole MCB. For Power DB | Nos | 1 |  | 0
0
d | 12 Way SPN DB, consisting of 8 Nos. 10/20 AMP SP MCB’s and controlled by one number 100 mAsensitivity 63 AMPS DP RCCB backed up with 63 Amps DP MCB as incomer. For Emg DB | Nos | 1 |  | 0
0
2 | UPS Distribution Boards (All MCB's in workstation DB's should be D Curve) |  |  |  | 0
0
a | 12 Way TPN DB, each phase consisting of 10 Nos. 10/20 AMP SP MCB’s and controlled by one number 63 AMPS DP RCCB (100 mA) for each phase and 1 no. 63 amps 4 pole MCB incomer. | Nos.. | 0 |  | 0
0
b | 14 Way TPN DB, each phase consisting of 12 Nos. 10/20 AMP SP MCB’s and controlled by one number 63 AMPS DP RCCB (100 mA) for each phase and 1 no. 63 amps 4 pole MCB incomer. | Nos.. | 0 |  | 0
0
c | 14 Way SPN DB, consisting of 10 Nos. 10/20 AMP SP MCB’s and controlled by one number 100 mA sensitivity 63 AMPS DP RCCB backed up with 63 Amps DP MCB. For UPS DB | Nos.. | 1 |  | 0
0
d | 12 Way SPN DB, consisting of 4 Nos. 25/32 AMP DP MCB’s and controlled by one number 100 mA sensitivity 63 AMPS DP RCCB ( 100 mA) for backed up with 63 Amps 4D MCB. The bus bar shall be Twin bus bar. For SERVER DB | Nos.. | 2 |  | 0
0
3 | Supply, installation, testing and commissioning of sheet metal with 63 A DP MCB. This shall include cable entry boxes both for incoming and outgoing cable). For 10 KVA UPS. | Nos. | 1 |  | 0
0
4 | Supply, installation, testing and commissioning of sheet metal with 32 A DP MCB. This shall include cable entry boxes both for incoming and outgoing cable). For 3 & 1 KVA UPS. | Nos. | 2 |  | 0
0
5 | Supply, installation, testing and commissioning of sheet metal weather proof enclosure with 63 A FP RCBO(300mA) This shall include cable entry boxes both for incoming and outgoing cable) For VRV units. The enclosure shall be IP 42. For VRV Out Door units | Nos. | 6 |  | 0
0
6 | Supply, installation, testing and commissioning of sheet metal weather proof enclosure with 40 A FP RCBO(300mA) This shall include cable entry boxes both for incoming and outgoing cable) For VRV units. The enclosure shall be IP 42. For VRV Out Door units | Nos. | 2 |  | 0
0
7 | Supply, installation, testing and commissioning of sheet metal weatherproof Enclosure with 25/32 A DP MCB. This shall include cable entry boxes both for incoming and outgoing cable). | Nos. | 0 |  | 0
0
8 | Supply, installation, testing and commissioning of sheet metal with 16 A FP MCB. This shall include cable entry boxes both for incoming and outgoing cable). | Nos. | 1 |  | 0
0
| TOTAL CARRIED OVER TO SUMMARY |  |  |  | 0
0
G | SUB DISTRIBUTION PANELS |  |  |  | 0
0
1 | Sub Distribution Panels |  |  |  | 0
| Design, manufacture, supplying & installing at site in positioning, connecting, testing and commissioning of the following cubical type, dead front, 2mm thick sheet steel enclosed, free standing indoor type extendible Sub Distribution Panel with vermin proof hinged lockable doors for each compartment provide bus bar interconnections for incoming and outgoing including feeders earthing and painting and as per specifications. |  |  |  | 0
Note | Provide insulated dedicated earth link in all UPS Panels |  |  |  | 0
| All MCCB's 200 Amps and above shall be Microprocessor based |  |  |  | 0
| All Light & Power panel ,UPS and A.C. Panel incomer MCCB shall have Over current, Earth fault and short circuit protection. |  |  |  | 0
| All Incomer MCCB's in UPS Panels shall be Microprocessor based |  |  |  | 0
| The microprocessor based MCCBs shall have |  |  |  | 0
| Over Load (Phase) |  |  |  | 0
| Current setting Ir(Ir=XIn) OFF 0.4 to 1.0 in steps of 0.1 |  |  |  | 0
| Time delay , tr( Inverse) 10 sec at 6/r |  |  |  | 0
| Over Load (Neutral) |  |  |  | 0
| Current setting In (Intrl =XIr) 0.5, 0.75&1.00 Intrl |  |  |  | 0
| Inverse 10 sec at 6 Intrl/Fixed 200ms |  |  |  | 0
| Short Circuit setting -2- 10 |  |  |  | 0
| Instantaneous - 1.5-1 |  |  |  | 0
| All MCB's in UPS Panels shall be D Curve |  |  |  | 0
| In all Electrical panels protective acrylic sheet to be provided in cable alley and feeders. |  |  |  | 0
| The meters shall be able to monitor all major power quality parameters Voltage , current , frequency , KVAH,KWH,Power factor and individual,harmonics, ethernet ready - IEC-625-22. |  |  |  | 0
| The ATS shall be 4 pole with inbuilt manual operating switch. In case the controller of the ATS fails it should be capable of transferring the load while the ATS is in maintenance. The ATS and controller should be same make |  |  |  | 0
| Provide On / Off and trip indicating lamp on main incomer only. |  |  |  | 0
| Panel construction shall be Form 3b for all Panels with MCCB outgoings and Form 2b for all Panels with MCB's outgoings. |  |  |  | 0
| The Earth fault release/relay and CBCTs shall be same make as OEM Switchgear been used in the Panels. It shall not trip on imbalance of load. |  |  |  | 0
| All meters shall have Modbus card for BMS connectivity |  |  |  | 0
| All the Electrical Panels shall be in accordance with IS 8623 standards |  |  |  | 0
0
a | The SDB L&P in UPS room shall consists of : |  |  |  | 0
0
| MAIN INCOMER |  |  |  | 0
| 1 Nos. 160 A TPN MCCB (25KA/1 sec)( O/C, S/C,E/F) and neutral isolation link 100% of rated current. Terminals suitable to receive 3.5c x 120 sq. mm . Al Ar cable connection on one side and Busbar connection on the other side. |  |  |  | 0
0
| BUSBAR |  |  |  | 0
| 200 amps 4P busbar chamber of suitable length with Aluminium busbars. All busbars and interconnections shall be of suitable size aluminium strips current density of aluminium shall not be more than 0.8 Amps/ sq.mm.provide 100% capacity for neutral bus bar. |  |  |  | 0
0
| INDICATING PANELS |  |  |  | 0
| 3 nos phase indicating lamps (LED type) each backed up with MCB and switch shall be provided for each incomer. |  |  |  | 0
| Provide Intelligent Panel Meter - multifunctional meter with RS485 for all incoming feeder |  |  |  | 0
| Provide Transient Voltage Surge Suppressor Rating 40kA class II along with 63 A MCCB. Including all necessary accessories. For Switching Operation on each incomer. |  |  |  | 0
| Provide earth fault protection (EF) in the incomer MCCB |  |  |  | 0
0
| OUTGOINGS |  |  |  | 0
| 1 Nos. 125 A TPN MCCB (36 kA/ 1 sec) terminal to receive suitable Cable on one side and Busbar connection on the other side. |  |  |  | 0
| 5 Nos. 63 A 4P MCB (10 kA/ 1 sec) terminal to receive suitable Cable on one side and Busbar connection on the other side. |  |  |  | 0
| 2 Nos. 16 A 4P MCB (10 kA/ 1 sec) terminal to receive suitable Cable on one side and Busbar connection on the other side. |  |  |  | 0
| 2 Nos. 32 A DP MCB (10 kA/ 1 sec) terminal to receive suitable Cable on one side and Busbar connection on the other side. |  |  |  | 0
0
| The SDB L&P as described above and specifications complete | Set | 1 |  | 0
0
b | The UPS SDB in UPS Room shall consists of : |  |  |  | 0
0
| MAIN INCOMER |  |  |  | 0
| 1 No. 100 A 4P MCCB (25KA/1 sec)( O/C, S/C,E/F). Terminals suitable to receive 4R x 1c x 25 sq. mm Cu. Flexible cable connection on one side and Busbar connection on the other side. |  |  |  | 0
0
| BUSBAR |  |  |  | 0
| 150 amps 4P busbar chamber of suitable length with Copper busbars. All busbars and interconnections shall be of suitable size copper strips current density of copper shall not be more than 1.6 Amps/ sq.mm. |  |  |  | 0
0
| INDICATING PANELS |  |  |  | 0
| 3 nos phase indicating lamps (LED type) each backed up with MCB and switch shall be provided for each incomer. |  |  |  | 0
| Provide on/off indication lamp on each incomer and buscoupler. |  |  |  | 0
| Provide Intelligent Panel Meter - multifunctional meter with RS485 for all incoming feeder |  |  |  | 0
| Provide Transient Voltage Surge Suppressor Rating 40kA class I&II along with 63 A MCB. Including all necessary accessories. For Switching Operation on each incomer. |  |  |  | 0
| Provide earth fault protection (EF) in the incomer MCCB |  |  |  | 0
0
| OUTGOINGS |  |  |  | 0
| 4 Nos. 63 A 4P MCB (10 kA/ 1 sec) terminal to receive suitable Cable on one side and Busbar connection on the other side. |  |  |  | 0
| 2 Nos. 63A DP MCB (10 kA/ 1 sec) terminals to receive suitable Copper Ar. Cable on one side and Busbar connection on the other side. |  |  |  | 0
| The above Panel as described above and specifications complete | Set | 0 |  | 0
0
c | The HVAC Panel at terrace shall consists of : |  |  |  | 0
| It is outdoor type |  |  |  | 0
0
| MAIN INCOMER |  |  |  | 0
| Main Incomer 1 Nos 125A TPN MCCB (36KA) and neutral isolation link 100% of rated current.Terminals suitable to receive 3.5c x 70 sq. mm AL cable connection on one side and Busbar connection on the other side. |  |  |  | 0
0
| BUSBAR |  |  |  | 0
| 200 amps 4P busbar, chamber of suitable length with aluminium busbars. All busbars and interconnections shall be of suitable size Al strips current density of Al shall not be more than 0.8 Amps/ sq.mm. |  |  |  | 0
0
| INDICATING PANELS |  |  |  | 0
| 3 nos phase indicating lamps (LED type) each backed up with MCB and switch shall be provided for each incomer. |  |  |  | 0
| Provide Intelligent Panel Meter - Dual Source Energy Meter EM 6438 with RS 485 port for all incoming feeder |  |  |  | 0
| Provide TVSS (40KA) |  |  |  | 0
0
| OUTGOINGS |  |  |  | 0
0
| 6 Nos. 63 A 4P MCB (10 kA) terminals suitable to receive cable on one side and wire connection to Bus bars.. |  |  |  | 0
| 4 Nos. 40A 4P MCB (10 kA) terminals suitable to receive cable on one side and wire connection to Bus bars.. |  |  |  | 0
0
| The AC PANEL as described above and specifications complete as required. | Set | 1 |  | 0
0
2 | The contractor to submit reports of torque tightness tests for all the nut bolt cable joints in all the panels with red marking after the torque tightening has been done as per manufactures recommendation. | Set | 0 |  | 0
0
3 | Providing & fixing in position 1000 mm wide , Electrical Insulating Mats as per IS 15652:2006, 2mm thick, suitable up to 3.3 KV , fire retardant,no effect of acids, alkalies and transformer oils, moisture proof, high tensile strength and texture finish / cloth impression (Anti slip , marking on top) . | RM | 5 |  | 0
0
4 | Replacement of existing 250 A tap off box with 400 A tap off box at site with all the necessary accessories complete as required. | Nos. | 0 |  | 0
0
5 | Supply & fixing in position approved shock treatment chart written in English, Hindi and Local language. These charts shall be framed in wooden frame & covered with clear glass. | Nos. | 1 |  | 0
0
6 | Supply & fixing in position the best quality danger notice boards of approved shape & size as reqd. by the local Electrical Inspecting Authority written in English, Hindi & local language. | Nos. | 1 |  | 0
0
7 | Supply & fixing in position the Electrical A 1 Size SLD chart in the UPS/electrical room . These charts shall be framed in wooden frame & covered with clear glass. | Nos. | 1 |  | 0
0
8 | Supplying the first aid box as approved by John Ambulance society. | Nos. | 1 |  | 0
0
9 | Supply & Fixing of NO/NC Relay Module complete as required. | Nos. | 0 |  | 0
0
10 | 2 core -1.5 sq.mm PVC FRLS wires in already laid suitable size of M.S conduit complete as required. | Rmt | 0 |  | 0
0
11 | Supply, Installations, Testing and Commissioning of 2 Kg Fire Suppression System (CQRS) in all Floor Panels of Electrical and UPS Room to be included. - Automatic Direct Low Pressure Fire Suppression System, UL Listed FK-5-1-12 Extinguishing Fluid shall be filled in UL Listed Cylinder, UL Listed Pressure Switch should be integrated in DLP Valve for Indication on Fire Suppression Panel and Main Fire Alarm System, 15 Meter UL Listed Detection Tube shall be UV Protected made of Modified Polyamide associated with End of Line Adapter with Pressure Gauge, master Control Panel with A/V Alarm and Battery Backup along with Potential Free Contact to integrate with existing Fire Alarm System for Central Monitoring. Mounting Bracket with all necessary accessories. complete in all respect. System Component Approval: Cylinder-UL Listed, Gas-UL Listed, Detection Tube-UL Listed, Pressure Switch-UL Listed Make: FireMech / Ceasefire / Honeywell | Nos. | 0 |  | 0
0
| TOTAL CARRIED OVER TO SUMMARY |  |  |  | 0

## Light Fixtures CONTROL
S.No. | Description | Unit
|  |  | Qty | Rate In Rs. | Amount in Rs.
H | SUPPLY & INSTALLATION OF LIGHTING FIXTURES |  |  |  |  | *Quoted Installation
1 | Supply & Fixing in position testing and commissioning of the following Lighting fixtures at site including all type of fixing accessories complete as required etc. Use all light fixture shall be LED Type. (Samples of all light fixtures to be submitted to the client/architect/consultant for approval prior to procurement of fixtures)
a | 32 Watts LED 600x600mm panel LED light as per approved make. | Nos | 36 |  | 0
0
b | 32 Watts LED 600x600mm panel LED Fire Proof light as per approved make.(Fire proof for Bonded store) | Nos | 0 |  | 0
0
c | 15 watts Suspended Cylindrical LED light as per approved make. | Nos | 0 |  | 0
0
d | Suspended Channel LED light (90x1500) at Cabins as per approved make | Nos | 0 |  | 0
0
e | Suspended Channel LED light (60x1200) as per approved make | Nos | 23 |  | 0
0
f | 13 wattts Surface Mounted LED Down light as per approved make | Nos | 0 |  | 0
0
g | 13 wattts Recessed LED Down light as per approved make | Nos | 110 |  | 0
0
h | Supply of track mounted spot light 10W-850lm cylindrical Shape, | Nos | 0 |  | 0
0
i | Track for mounting Spot 1 meter standard length. | Rmt | 0 |  | 0
0
j | 500 mm Dia Suspended Decorative LED hanging light as per Architect /Client basic cost Rs. 5500 | Nos | 0 |  | 0
0
k | 750 mm Dia Suspended Decorative LED hanging light as per Architect /Client basic cost Rs. 7500 | Nos | 0 |  | 0
0
l | 15 Watts LED Wall light as per Architect/Client basic cost Rs. 2500 | Nos | 0 |  | 0
0
2 | Supply, Installation, Testing & Commissioning of 3 Watts LED Ni Cd Battery backup up to 1.5 hr emergency Exit light Prolite or equivalent make. The sample shall be submitted before ordering. or Equivalent make. | Nos | 6 |  | 0
0
3 | Supply, installation, testing commissioning of recessed ceiling mounted photo cell switching units to provide ON/OFF switching of lighting in response to ambient light levels. | Nos | 0 |  | 0
0
4 | Supply & installation of Passive infra-red presence detector for lighting control to set the parameters of all meeting rooms and cabin (ON/OFF selection of lights)( Lights switch OFF in steps of 1 minute) | Nos | 0 |  | 0
a | Switches lighting OFF when sufficient daylight is present. |  |  |  | 0
b | Used as on ON/OFF daylight dependant switch or in series with a wall switch |  |  |  | 0
c | Lighting level adjustable up to 1500 lux approx. |  |  |  | 0
0
| TOTAL CARRIED OVER TO SUMMARY |  |  |  | 0

## Elect LB
Sl.No. | Description | Unit |  | Supply & Installation
|  |  | Qty | Rate In Rs. | Amount in Rs.
A. | POINT WIRING
All wires shall be FRLS PVC insulated copper conductor. Point wiring rates are inclusive of 3 x 1.5 sq mm insulated copper conductor wires for circuit.(from DB to switch board).
All sockets to be checked with a Check Plug socket tester for live-neutral reverse, no earth,neutral fault, live earth reverse, neutral earth reverse.
The Circuit No. and DB no. label shall be provided on all UPS ,RAW sockets and switchboards with label printer.
Colour coding for conduits to be done for different systems. The whole length of conduits to be painted.
All circuit & point wiring shall be colour coded & shall have ferruling on both end for circuit identification complete as required etc.Labelling on all the switches and sockets to be done with respect to DB reference, phase and circuit no.
Earth loop Impedance Test to be performed. RCD test to be done. Cable Insulation Tests to be done.
Wherever the occupancy sensor is provided in the cabin/ meeting rooms/workstations , the circuit wires from Distribution Board to occupancy sensor and sensor to switch are inclusive in the point wiring rate.
Labeling of all sockets and emergency lights to be provided and Ferruling for all the circuits to be considered
1 | Wiring for the following light points with 3x1.5 Sq.mm FRLS PVC insulated stranded copper conductor wires in concealed M.S. conduits in F.ceiling/walls/ceiling as directed including providing and fixing of 6 amps flush type switches, 5 sided G.I Boxes for housing switc­hes and earth­ing complete as required. Rates are inclusive of 3 x 1.5 sq mm FRLS PVC insulated stranded copper conductor wires for circuit
a. | First point controlled by one no. 6 amp switch. | Nos. | 55 |  | 0
0
2 | Same as item No. 1a above but LOOP POINT i.e. wiring of point looped from first point with 3 x 1.5 sq. mm FRLS PVC insulated copper conductor wire in concealed/exposed MS conduit and earthing | Nos. | 90 |  | 0
0
3 | Wiring for the following light points with 1.5 Sq.mm FRLS PVC insulated stranded copper conductor wires in concealed M.S. conduits in F.ceiling/walls/ceiling as direc­ted including providing and fixing of 6 amps flush type switches, 5 sided G.I Boxes for housing switc­hes and earth­ing comple­te as required. Rates are inclusive of 3 x 1.5 sq mm FRLS PVC insulated stranded copper conductor wires for circuit |  |  |  | 0
0
a. | First point controlled by one no. 16 amp switch. | Nos. | 0 |  | 0
0
4 | Wiring for the following light points controlled by MCB in DB (Cost of MCB has been taken elsewhere in the tender) with 3 x 1.5 sq. mm FRLS PVC insulated copper conductor wires in concealed/exposed M.S. conduits as called for and earthing. |  |  |  | 0
0
a. | First point controlled by existing MCB in D.B. To first light Em Light | Nos. | 4 |  | 0
0
5 | Same as item No. 4.a above but LOOP POINT i.e. wiring of point looped from first point with 3x1.5 sq. mm FRLS PVC. insulated copper conductor wire in concealed/exposed M.S. conduit and earthing | Nos. | 39 |  | 0
0
6 | SITC of 2C x 1.5 sq mm non shielded Cable for DALI Ballast wiring in 25 mm dia MS conduit with all fixing accessories complete as required | Rmt. | 0 |  | 0
0
7 | SITC of 4C x 1.5 sq mm shielded Cable for QSM wiring in suitable size of MS conduit with all fixing accessories complete as required. Cable Common – 12 AWG (4.0 mm2); Power – 12 AWG (4.0 mm2); MUX Data – 22 AWG (0.25 mm2); Data – 22 AWG (0.25 mm2); Sense Line – 18 AWG (0.75 mm2); Drain Wire – 24 AWG (0.2 mm2) | Rmt. | 0 |  | 0
0
8 | Wiring for 6/16 amps outlets with 3 X 2.5 sq.mm FRLS PVC insulated copper conductor wires in M.S. Conduits in ceiling/walls/floor as direc­ted incl­u­ding providing & fixing of 6/16 amps flush type 5 pin socket and 16 amps switch with cover plate, 5 sided G.I boxes for housing switches, sockets and earthi­ng complete as required. (for general areas 4 nos loop in one circuits) | Nos. | 32 |  | 0
0
9 | Wiring for inline fan points with 2 x 2.5 sq.mm FRLS PVC insulated stranded copper con­ductor wires in concealed M.S. conduits in F.ceiling/ walls/ Ceiling as directed including providing and fixing of 16 amps flush type switches 16 amps 3 pin socket near inline fan, 5 sided G.I. boxes for housing switches and 16 amps 3 pin socket outlet and earthing and complete as required.(including body earth for GI boxes) | Nos. | 9 |  | 0
0
10 | Wiring for Geyser/Projector/Hand Dryer points with 2 x 4 + 1 x 4 sq mm FRLS PVC insulated copper conductor wires in concealed M.S. conduits in F.ceiling/ walls/ Ceiling as directed including providing & fixing 16 amps flush type switch near the white board and 6/16 amps 6 pin socket near the projector in ceiling , 5 sided G.I. boxes for housing switches and 6/16 A 6 pin socket outlet , earthing and complete as required.(including body earth for GI boxes) ( 1 point per circuit) | Nos. | 4 |  | 0
0
11 | Wiring for VRV Indoor units with 3 x 2.5 sq.mm FRLS PVC insulated stranded copper conductor wires in concealed M.S. conduits in F.ceiling/ walls/ Ceiling as directed including providing providing and fixing of 6 amps flush type switches 16 amps 3 pin socket near VRV points, 5 sided G.I. boxes for housing switches and 16 amps 3 pin socket outlet and earthing and complete as required.(including body earth for GI boxes) (1 point per circuit) | Nos. | 24 |  | 0
0
12 | Wiring for VAV /fire damper points with 3 x 2.5 sq.mm FRLS PVC insulated copper conductor wires in concealed M.S. conduits in F.ceiling/ walls/ Ceiling as directed including providing & fixing 6 amps flush type switches, 6 amps 3 pin socket near VAV points, 5 sided G.I. boxes for housing switches and 6 A sockets earthing and complete as required. The sockets to be fused spur type (MK make). (including body earth for GI boxes) (8 to 10 points per circuits) | Nos. | 0 |  | 0
0
13 | Wiring for 16 amps power outlet poi­nts with 4 sq.mm FRLS PVC insulated stranded copper conductor wires in concealed/recessed M.S. conduit as directed including providing providing and fixing of 16 amps flush type switch and 6 pin socket with cover plate 5 sided G.I. outlet boxes for switches and socket and earthing the third pin with 2.5 sq mm FRLS PVC stranded copper wire complete as required (Only one outlet shall be connected on each circuit) (including body earth for GI boxes) | Nos. | 5 |  | 0
0
14 | Wiring for 16 amps power outlet points with 4 sq.mm FRLS PVC insulated stranded copper conductor wires for the first power outlet and 4 sq.mm FRLS PVC insu­lated stranded copper conductor wires for the second outlet, in concealed M.S. cond­uits in F.ceiling/ walls/Ceiling/floor ducts as directed including providing providing and fixing of 16 amps flush type switch and 6 pin socket with cover plate, 5 sided G.I. outlet boxes for housing switches and socket, and earthing the third pin with 2.5 sq.mm FRLS PVC insulated copper conductor wires complete as required (Two power out­lets shall be connected on each circuit)(including body earth for GI boxes) | Set of Two | 2 |  | 0
0
15 | Wiring for A/C outlet points with 4.0 sq mm FRLS PVC insulated stranded copper conductor wires in M.S. conduitl/wall/floor ducts as directed including providing 25 A socket with 25 amps SP MCB ( Tiny Trip) 5 sided GI Outlet Box for housing and socket and MCB and earthing with 2.5 sq. mm FRLS PVC insulated stranded Copper Conductor wires complete as required. | Nos. | 0 |  | 0
0
| Different colours to be used for 3 core cables for raw power and UPS power. |  |  |  | 0
16 | Wiring for UPS/Raw plug outlets points with three core, 2.5 sqmm FRLS PVC Insulated and PVC sheathed flexible cable with bright annealed electrolytic copper conductor, 1100 volt grade confirming to IS : 694-1990 with latest amendments, in existing Channels/ conduit in ceiling/walls/floor including all cable termination accessories) (including body earth for GI boxes). Colour Coding to be followed | RM | 800 |  | 0
0
17 | Wiring for UPS/Raw plug outlets points with three core, 4.0 sqmm FRLS PVC Insulated and PVC sheathed flexible cable with bright annealed electrolytic copper conductor , 1100 volt grade confirming to IS : 694-1990 with latest amendments, in existing Channels/ conduit in ceiling/walls/floor inclu­ding all cable termination accessories) Earthing of GI Box to be included. Colour Coding to be followed. For Lab Sockets | RM | 1700 |  | 0
0
18 | Wiring for Power plug outlets points with three core, 6.0 sqmm FRLS PVC Insulated and PVC sheathed flexible cable with bright annealed electrolytic copper conductor , 1100 volt grade confirming to IS : 694-1990 with latest amendments, in existing Channels/ conduit in ceiling/walls/floor inclu­ding all cable termination accessories). Colour Coding to be followed. | RM | 65 |  | 0
0
19 | Wiring for Power plug outlets points with three core, 10.0 sqmm FRLS PVC Insulated and PVC sheathed flexible cable with bright annealed electrolytic copper conductor , 1100 volt grade confirming to IS : 694-1990 with latest amendments, in existing Channels/ conduit in ceiling/walls/floor inclu­ding all cable termination accessories). Colour Coding to be followed. | RM | 0 |  | 0
0
| The word UPS shall be printed on all UPS sockets. |  |  |  | 0
| The word RAW shall be printed on all RAW sockets. |  |  |  | 0
| The Circuit No. and DB no. label shall be provided on all UPS ,RAW sockets and switchboards with label printer. |  |  |  | 0
| Contractor is required to submit samples of all types of switches and sockets to Consultant and Architects representative for approval before ordering the material. |  |  |  | 0
0
20 | Providing and fixing of 1 Nos. 6 amp round pin type socket and 1 No. 6 amps switch cover plate, 5 sided G.I. Boxes for housing switches and sockets and earthing complete as required (for UPS/Raw). GI Box to have earth pin for body earthing | Nos. | 16 |  | 0
0
21 | Providing and fixing of 2 Nos. 6 amp round pin type socket and 1 No. 6 amps switch cover plate, 5 sided G.I. Boxes for housing switches and sockets and earthing complete as required (for UPS/Raw). GI Box to have earth pin for body earthing | Nos. | 26 |  | 0
0
22 | Providing and fixing of 3 Nos. 6 amp round pin type socket and 1 No. 6 amps switch cover plate, 5 sided G.I. Boxes for housing switches and sockets and earthing complete as required (for UPS/Raw). GI Box to have earth pin for body earthing | Nos. | 32 |  | 0
0
23 | Providing and fixing of 2 Nos. 6/16 amp round pin type socket and 1 No. 16 amps switch cover plate, 5 sided G.I. Boxes for housing switches and sockets and earthing complete as required (for UPS/Raw). GI Box to have earth pin for body earthing. For Lab | Nos. | 109 |  | 0
0
24 | Providing and fixing of 1 No.16 amps flush type 6 pin socket and 1 No. 16 amps switch with indicator, cover plate, 5 sided G.I. Boxes for housing switches and sockets and earthing complete as required (for UPS / RAW) GI Boxes to have earth pin for body earthing | Nos. | 2 |  | 0
0
25 | Providing and fixing Underfloor Access Outlets (250 x 250 x 55 - mm 70 compartments 1Trap including providing 2 Nos 6 Amps Round Pin sockets and 1 no. 16 Amp Switch & 2 data outlet complete as required. | Nos. | 2 |  | 0
0
26 | Supply and fixing of the following sizes of thermoplastic moulded plug and socket IEC 309 type in PVC Box of suitable size flush / surface and making connections complete as required. The box shall be IP 44. |  |  |  | 0
a | 3 pin 16/20 A 1 phase industrial socket with mcb & plug top | Nos. | 0 |  | 0
b | 3 pin 32 A 1 phase industrial socket plug top | Nos. | 2 |  | 0
0
27 | Providing and fixing in position the following M.S. conduits including all accessories concealed in F. ceiling/wall/floor as required including 1.6 mm thick M.S. junction or pull boxes with 3mm thick perspex sheet cover plate compl­te with 1.6 mm dia. G.I. pull wires in the length of conduit. |  |  |  | 0
0
a. | 20 mm dia conduit ( 1.6 mm thick) | RM | 90 |  | 0
b. | 25 mm dia conduit (1.6 mm thick) | RM | 200 |  | 0
c. | 32 mm dia conduit (2.0 mm thick) | RM | 110 |  | 0
0
28 | The Electrical Contractor shall provide sufficient temporary lighting for working in the Building total area 7415 sq. ft. divided in single floor and maintain the same till completion of the project.It shall include replacement of all fused/faulty lamps.It shall include providing 15 A plug sockets (industrial type with ON/OFF switch/MCB) on 4 sides walls one plug at every 5-8 meter distance. The Contractors will tap off supply from these plugs for his use. Tubelights to maintain a lighting level of 150 lux on the floor,.Each 15 A socket and each Light circuit shall be protected by suitable MCBs.Use three core PVC Insulated PVC sheathed copper conductor cables for wiring.The contractor shall salvage the complete wiring and take it back at the end of the project. | L.S. | 1 |  | 0
0
| TOTAL CARRIED OVER TO SUMMARY |  |  |  | 0
0
B. | CONDUITING FOR TELEPHONE , COMPUTER & CONDUITING AND WIRING FOR T.V. SYSTEM. |  |  |  | 0
0
1 | Providing and fixing in position the following M.S. conduits including all accessories concealed in F. ceiling/wall/floor as required including 1.6 mm thick M.S. junction or pull boxes with 3mm thick perspex sheet cover plate compl­te with 1.6 mm dia. G.I. pull wires in the length of conduit. |  |  |  | 0
0
a. | 20 mm dia conduit( 1.6 mm wall thickness) | RM | 85 |  | 0
b. | 25 mm dia conduit ( 1.6 mm wall thickness) | RM | 200 |  | 0
c. | 32 mm dia conduit ( 1.6 mm wall thickness) | RM | 100 |  | 0
0
2 | Providing and fixing in position suitable 1.2 mm thick G.I./ PVC outlet box for RJ- 45 computer outlet with all fixing accessories as required. | Nos. | 25 |  | 0
0
3 | Supply and fixing of 1.2 mm thick G.I Box along with RG 11 TV Co axial socket with Cover Plate | Nos. | 1 |  | 0
0
4 | Supply drawing connecting testing and commissioning of TV Coaxial cable RG 6 in existing conduit | RM | 75 |  | 0
0
| TOTAL CARRIED OVER TO SUMMARY |  |  |  | 0
0
C. | EARTHING |  |  |  | 0
0
1 | Providing and fixing in position the following copper strips and wires including providing all fixing accessories and effecting proper connections |  |  |  | 0
| Note:- MS Cable markers at the earth bus, panel and DB entries to be provided |  |  |  | 0
a. | G.I. tape 25 mm x 6 mm | RM | 350 |  | 0
b. | Copper tape 25mm x 3 mm for ESD earthing | RM | 60 |  | 0
c. | GI wire 8 SWG | RM | 200 |  | 0
d. | GI wire 12 SWG | RM | 150 |  | 0
e. | Supply installation , and making of Exothermic weld suitable to bond GI strip of 25x5 mm with Copper Strip of 25x5 mm with 75mm extensions on either side | Nos. | 4 |  | 0
f. | Copper Earth Link connectors - 200 mm long, 25mm wide and 5 mm thick | Nos. | 3 |  | 0
0
2 | Supply and laying, effecting proper connec­tions, testing & commissioning of the following sizes of 1.1 KV armoured XLPE/ unarmoured FRLS sheathed XLPE insulation, conforming to IS: 7098 (Part-1)- 1988 ( 90 deg C) aluminium /copper conductor cables conforming to IS : 1554 and FRLS Insulated flexible copper cables as per IS 694 laid over MS supports in existing RCC ducts/ laid in ground /laid on Cable Trays including clamping the cables to sup­ports in an approved manner as required complete with all accessories. |  |  |  | 0
0
a | 1c x 50 sq.mm FRLS insulated flexible copper conductor cables | RM | 140 |  | 0
0
b | 1c x 35 sq.mm FRLS insulated flexible copper conductor cables | RM | 165 |  | 0
0
c | 1c x 25 sq.mm FRLS insulated flexible copper conductor cables | RM | 70 |  | 0
0
d | 1c x 16 sq.mm FRLS insulated flexible copper conductor cables | RM | 120 |  | 0
0
e | 1c x 10 sq.mm FRLS insulated flexible copper conductor cables | RM | 100 |  | 0
0
f | 1c x 6 sq.mm FRLS insulated flexible copper conductor cables | RM | 50 |  | 0
0
g | 2 Nos 1 x 10 Sq. mm FRLS insulated flexible copper conductor cables (Green Colour for UPS DB Sub-main Earthing) | RM | 95 |  | 0
0
3 | Supplying and making of end termination for the following size of compression lugs and PG Threaded Nylon Flexible cable glands complete with all fixing accessories as required |  |  |  | 0
0
a | 1c x 50 sq.mm FRLS insulated flexible copper conductor cables | Sets | 4 |  | 0
0
b | 1c x 35 sq.mm FRLS insulated flexible copper conductor cables | Sets | 8 |  | 0
0
c | 1c x 25 sq.mm FRLS insulated flexible copper conductor cables | Sets | 4 |  | 0
0
d | 1c x 16 sq.mm FRLS insulated flexible copper conductor cables | Sets | 6 |  | 0
0
d | 1c x 10 sq.mm FRLS insulated flexible copper conductor cables | Sets | 12 |  | 0
0
4 | Providing earthing station at loca­tion as called for including provid­ing 600 mm x 600 mm x 3 mm thick tinned copper electrode 2 Nos 25 x 3 mm copper strip (for body earthing GI strip can be considerd) up to ground level 20mm dia medium class GI pipe (India Tube Company make or approved equal) CI funnel with 20 gauge GI wire mesh, masonry chamber with concrete base, CI man­hole cover (cover to be heavy duty) with frame (300mm x 300mm) and bitumastic paint and packing the fixture of charcoal and common salt around plate electrode complete as per I.S. ( Minimum depth shall be 4.2 M ) for UPS & Server | Nos. | 0 |  | 0
0
5 | Supply, Installation, testing and commissioning of Maintenance Free Earthing of make Electrolytic Earthing comprising of type 'K' copper 2.4 mm wall thickness, hollow tube 10 feet long, 2.125 inches outer diameter completely filled with non hazardous metallic salts (Terrafill) to achieve an earth resistance of less than 1 ohms. Provide masonry chamber with concrete base, CI man­hole cover (cover to be heavy duty) with frame (300mm x 300mm) and make earth pit sign/ identifcation no in each earth station for UPS, Server & Lab | Nos. | 5 |  | 0
0
6 | Supply, installation, testing and commissioning of sheet metal enclosed 450 x 200 x 150 (D) mm insulated earth distribution board with 1 nos. 50 x 6 mm copper tinned earth bars on SMC insulator suitable for 6/8 nos connections complete with all fixing accessories as required. | Nos. | 2 |  | 0
0
7 | Supply, installation, testing and commissioning of sheet metal enclosed 300 x 200 x 150 ( D) mm insulated earth distribution board with 1 nos. 32 x 6 mm copper tinned earth bars on SMC insulator suitable for 6/8 nos connections complete with all fixing accessories as required. | Nos. | 4 |  | 0
0
8 | Supplying and laying of the following sizes of Heavy duty PVC Pipes below paved area including chase cutting and back filling. |  |  |  | 0
a. | 100 mm outer dia | RM | 5 |  | 0
b. | 80 mm outer dia | RM | 10 |  | 0
0
| TOTAL CARRIED OVER TO SUMMARY |  |  |  | 0
0
D | CABLES, MAINS & SUBMAINS |  |  |  | 0
0
1 | Supply and laying, effecting proper connec­tions, testing & commissioning of the following sizes of 1.1 KV armoured XLPE/ unarmoured FRLS sheathed XLPE insulation, conforming to IS: 7098 (Part-1)- 1988 ( 90 deg C) aluminium /copper conductor cables conforming to IS : 1554 and FRLS Insulated flexible copper cables as per IS 694 laid over MS supports in existing RCC ducts/ laid in ground /laid on Cable Trays including clamping the cables to sup­ports in an approved manner as required complete with all accessories. |  |  |  | 0
0
| Note : All cables to be glanded and crimped with suitable sized lugs. All Cable trays to be double earthed. All raceways and cable glands to be earthed with brass round earth clips and wires. |  |  |  | 0
| Earthing ring to be included in all the cable glands. |  |  |  | 0
| Sub main cables should be labelled at both ends |  |  |  | 0
| Joints shall be allowed only at the 2 ends of the cables and not in between. |  |  |  | 0
0
a | 3.5 c x 300 sq.mm1.1 KV grade XLPE Insulated FRLS sheathed armoured aluminium conductor cable | RM | 65 |  | 0 | 2
0
b | 3.5 c x 240 sq.mm1.1 KV grade XLPE Insulated FRLS sheathed armoured aluminium conductor cable For SDB L&P (Assumed) | RM | 0 |  | 0
0
c | 3.5 c x 185 sq.mm1.1 KV grade XLPE Insulated FRLS sheathed armoured aluminium conductor cable | RM | 0 |  | 0
0
d | 3.5 c x 150 sq.mm1.1 KV grade XLPE Insulated FRLS sheathed armoured aluminium conductor cable | RM | 75 |  | 0 | 2
0
e | 3.5 c x 120 sq.mm1.1 KV grade XLPE Insulated FRLS sheathed armoured aluminium conductor cable | RM | 0 |  | 0
0
f | 3.5 c x 95 sq.mm1.1 KV grade XLPE Insulated FRLS sheathed armoured aluminium conductor cable | RM | 0 |  | 0
0
g | 3.5 c x 70 sq.mm1.1 KV grade XLPE Insulated FRLS sheathed armoured aluminium conductor cable | RM | 0 |  | 0
0
h | 3.5 c x 50 sq.mm1.1 KV grade XLPE Insulated FRLS sheathed armoured aluminium conductor cable | RM | 30 |  | 0 | 2
0
i | 4 c x 35 sq.mm1.1 KV grade XLPE Insulated FRLS sheathed armoured aluminium conductor cable | RM | 0 |  | 0
0
j | 4 c x 25 sq.mm1.1 KV grade XLPE Insulated FRLS sheathed armoured aluminium conductor cable For DB and VRV ODU | RM | 630 |  | 0 | 46
0
k | 4 c x 25 sq.mm1.1 KV grade XLPE Insulated FRLS sheathed armoured copper conductor cable | RM | 0 |  | 0
0
l | 4 c x 16 sq.mm1.1 KV grade XLPE Insulated FRLS sheathed armoured aluminium conductor cable | RM | 0 |  | 0
0
m | 4 c x 16 sq.mm 1.1 KV grade XLPE Insulated FRLS sheathed armoured copper conductor cable For UPS DB | RM | 80 |  | 0 | 4
0
n | 4 c x 10 sq.mm 1.1 KV grade XLPE Insulated FRLS sheathed armoured copper conductor cable | RM | 85 |  | 0 | 8
0
p | 4 c x 6 sq.mm 1.1 KV grade XLPE Insulated FRLS sheathed armoured copper conductor cable | RM | 0 |  | 0
0
q | 4 c x 4 sq.mm 1.1 KV grade XLPE Insulated FRLS sheathed armoured copper conductor cable | RM | 20 |  | 0 | 4
0
s | 4 c x 2.5 sq.mm 1.1 KV grade XLPE Insulated FRLS sheathed armoured copper conductor cable | RM | 0 |  | 0
0
t | 3 c x 10 sq.mm 1.1 KV grade PVC Insulated FRLS Armoured copper conductor cable | RM | 0 |  | 0
0
u | 3 c x 6 sq.mm 1.1 KV grade XLPE Insulated FRLS sheathed armoured copper conductor cable For Emg DB | RM | 45 |  | 0 | 2
0
x | 2 c x 10 sq.mm 1.1 KV grade XLPE Insulated FRLS sheathed armoured copper conductor cable For Server DB | RM | 65 |  | 0 | 6
0
z | 1c x 6 sq.mm FRLS XLPE insulated flexible copper conductor cables | RM | 0 |  | 0
0
aa | 1c x 10 sq.mm FRLS XLPE insulated flexible copper conductor cables | RM | 0 |  | 0
0
ab | 1c x 16 sq.mm FRLS XLPE insulated flexible copper conductor cables | RM | 0 |  | 0
0
ac | 1c x 25 sq.mm FRLS XLPE insulated flexible copper conductor cables | RM | 135 |  | 0
0
ad | 1c x 35 sq.mm FRLS XLPE insulated flexible copper conductor cables | RM | 0 |  | 0
0
2 | Supplying and making terminal joints for the following size of 1.1 KV PVC insulated copper conductor armoured cables including providing heavy duty tinned copper terminal crimping lugs, solder, insulation tape, approved sealing epoxy compound, double compression brass cable glands, effecting gland connec­tions and effecting terminal connections to the equipment complete as required. Use compression lugs and PG Threaded Nylon Flexible cable glands for single core flexible cables |  |  |  | 0
0
a | 3.5 c x 300 sq.mm1.1 KV grade XLPE Insulated FRLS sheathed armoured aluminium conductor cable | Sets | 2 |  | 0
0
b | 3.5 c x 240 sq.mm1.1 KV grade XLPE Insulated FRLS sheathed armoured aluminium conductor cable | Sets | 0 |  | 0
0
c | 3.5 c x 185 sq.mm1.1 KV grade XLPE Insulated FRLS sheathed armoured aluminium conductor cable | Sets | 0 |  | 0
0
d | 3.5 c x 150 sq.mm1.1 KV grade XLPE Insulated FRLS sheathed armoured aluminium conductor cable | Sets | 2 |  | 0
0
e | 3.5 c x 120 sq.mm1.1 KV grade XLPE Insulated FRLS sheathed armoured aluminium conductor cable | Sets | 0 |  | 0
0
f | 3.5 c x 95 sq.mm1.1 KV grade XLPE Insulated FRLS sheathed armoured aluminium conductor cable | Sets | 0 |  | 0
0
g | 3.5 c x 70 sq.mm1.1 KV grade XLPE Insulated FRLS sheathed armoured aluminium conductor cable | Sets | 0 |  | 0
0
h | 3.5 c x 50 sq.mm1.1 KV grade XLPE Insulated FRLS sheathed armoured aluminium conductor cable | Sets | 2 |  | 0
0
i | 4 c x 35 sq.mm1.1 KV grade XLPE Insulated FRLS sheathed armoured aluminium conductor cable | Sets | 0 |  | 0
0
j | 4 c x 25 sq.mm1.1 KV grade XLPE Insulated FRLS sheathed armoured copper conductor cable | Sets | 0 |  | 0
0
k | 4 c x 25 sq.mm1.1 KV grade XLPE Insulated FRLS sheathed armoured AL conductor cable | Sets | 48 |  | 0
0
l | 4 c x 16 sq.mm1.1 KV grade XLPE Insulated FRLS sheathed armoured aluminium conductor cable | Sets | 0 |  | 0
0
m | 4 c x 16 sq.mm 1.1 KV grade XLPE Insulated FRLS sheathed armoured copper conductor cable | Sets | 4 |  | 0
0
n | 4 c x 10 sq.mm 1.1 KV grade XLPE Insulated FRLS sheathed armoured copper conductor cable | Sets | 8 |  | 0
0
p | 4 c x 6 sq.mm 1.1 KV grade XLPE Insulated FRLS sheathed armoured copper conductor cable for VRV ODUs | Sets | 0 |  | 0
0
q | 4 c x 4 sq.mm 1.1 KV grade XLPE Insulated FRLS sheathed armoured copper conductor cable | Sets | 4 |  | 0
0
s | 4 c x 2.5 sq.mm 1.1 KV grade PVC Insulated FRLS sheathed armoured copper conductor cable | Sets | 0 |  | 0
0
u | 3 c x 6 sq.mm 1.1 KV grade XLPE Insulated FRLS sheathed armoured copper conductor cable | Sets | 4 |  | 0
0
w | 2 c x 16 sq.mm 1.1 KV grade XLPE Insulated FRLS sheathed armoured copper conductor cable | Sets | 0 |  | 0
0
x | 2 c x 10 sq.mm 1.1 KV grade XLPE Insulated FRLS sheathed armoured copper conductor cable | Sets | 6 |  | 0
0
aa | 1c x 10 sq.mm FRLS XLPE insulated flexible copper conductor cables | Sets | 0 |  | 0
0
ab | 1c x 16 sq.mm FRLS XLPE insulated flexible copper conductor cables | Sets | 0 |  | 0
0
ac | 1c x 25 sq.mm FRLS XLPE insulated flexible copper conductor cables | Sets | 18 |  | 0
0
ac | 1c x 35 sq.mm FRLS XLPE insulated flexible copper conductor cables | Sets | 0 |  | 0
0
| TOTAL CARRIED OVER TO SUMMARY |  |  |  | 0
0
E | RACEWAYS AND CABLE TRAYS |  |  |  | 0
| Note :- |  |  |  | 0
0
1 | Fabricating supplying to site of installation, installation on ceiling/ surface 1.6 mm thick M.S. powder coated raceways of height 50 mm and 2.0 mm thick openable cover, totally enclosed, the joints between two lengths of channels or between channel and junction box shall be joined together with 3 mm thick M.S. Powder coated coupler plates to make it dust and water proof. The cost shall including all supporting and fixing accessories including dash fasteners. (Orange colour for data and Blue colour for power) |  |  |  | 0
a | 250 mm (wide) x 50 mm (height) | RM | 20 |  | 0
b | 150 mm (wide) x 50 mm (height) | RM | 75 |  | 0
c | 100 mm (wide) x 50 mm (height) | RM | 45 |  | 0
d | 150 mm (wide) x 150 mm (height) | RM | 5 |  | 0
0
2 | Fabricating supplying to site of installation, in floor including chase cutting of floor,leveling, refilling and making good the same from 1.6 mm thick and 2 mm thick cover pregalvanised MS CRCA sheet, totally enclosed, height 40 mm . The two lengths of raceways shall be fitted with Collars , 50 mm wide, 3 mm thick , press fit type. The raceways shall be clamped to the floor slab with GI clamps , 3mm thick and shall be screwed to the floor slab. The joint between raceway and junction box will be made with GI flexible strip( 3 nos), 3 mm thick, 4 inches long ,15 mm wide which will be nut bolted to the Junction box complete as required etc. |  |  |  | 0
0
a | 300 mm x 300 x 60 mm (height) | Nos. | 6 |  | 0
b | 250 mm x 250 x 60 mm (height) | Nos. | 0 |  | 0
c | 200 mm x 200 x 60 mm (height) | Nos. | 15 |  | 0
d | 150 mm x 150 x 60 mm (height) | Nos. | 10 |  | 0
e | 100 mm x 100 x 60 mm (height) | Nos. | 4 |  | 0
0
3 | Fabricating supplying to site of installation, in floor including chase cutting of floor,leveling, refilling and making good the same from 1.6 mm thick and 2 mm thick cover pregalvanised MS CRCA sheet, totally enclosed, height 40 mm . The two lengths of raceways shall be fitted with Collars , 50 mm wide, 3 mm thick , press fit type. The raceways shall be clamped to the floor slab with GI clamps , 3mm thick and shall be screwed to the floor slab. The joint between raceway and junction box will be made with GI flexible strip( 3 nos), 3 mm thick, 4 inches long ,15 mm wide which will be nut bolted to the Junction box complete as required etc. |  |  |  | 0
0
a | 250 mm (wide) x 40 mm (height) | RM | 50 |  | 0
b | 150 mm (wide) x40 mm (height) | RM | 30 |  | 0
c | 100 mm (wide) x 40 mm (height) | RM | 60 |  | 0
0
5 | Fabricating supplying to site of installation, Junction boxes for floor raceways made from 2 mm thick , with 2.5 mm thick G.I. cover including providing neoprene gaskets between the cover and the junction box, cadmium plated flat/round head screws, height as per site condition,totally enclosed. Proper cutouts shall be made in the side walls for raceway entry wherever required. The junction box shall be all side walls should be welded expect top cover and all side walls shall have suitable size of rectangular knock out holes for taking raceways / conduits as required and not a complete cut out. The top cover should be sealed with M Seal to make it dust and water proof complete as required etc. |  |  |  | 0
0
a | 300 mm x 300 x 50 mm (height) | Nos. | 12 |  | 0
b | 200 mm x 200 x 50 mm (height) | Nos. | 8 |  | 0
c | 150 mm x 150 x 50 mm (height) | Nos. | 16 |  | 0
d | 100 mm x 100 x 50 mm (height) | Nos. | 5 |  | 0
0
6 | Design manufacture , supply and fixing in position the cable trays of the following sizes for supporting 1.1 KV grade armoured/unarmoured aluminium /copper conductor cables. Fabricate the cable trays from perforated 1.6/2mm thick M.S. CRCA sheet duly galvanised with expansion coupler plates duly galvanised, with bolts, washer and nuts. Knock out holes for cable connections as per approved design. The tray should comply with the specification of NEC (National Electric Codes) and NEMA (National Electric Manufacturers Association). The steel should be as per IS:226 and galvanising as per IS :2629/BS 729/ASTM 123. The rate shall also include for supporting steel , fish plates , fixing accessories , nuts bolts, supporting down rods , dash fastener, cutting the RCC etc. complete as required. (the horizontal and vertical bends, T's should be factory fabricated and the rate should include for the same) |  |  |  | 0
0
a | 100 mm wide x 40 mm x 2.0 mm thk | RM | 0 |  | 0
b | 150 mm wide x 40 mm x 2.0 mm thk | RM | 110 |  | 0
c | 300 mm wide x 40 mm x 2.0 mm thk | RM | 65 |  | 0
d | 450 mm wide x 40 mm x 2.0 mm thk | RM | 10 |  | 0
e | 600 mm wide x 40 mm x 2.0 mm thk | RM | 0 |  | 0
0
7 | Design manufacture , supply and fixing in position the Ladder Type cable trays of the following sizes for supporting 1.1 KV grade armoured/unarmoured aluminium /copper conductor cables. Fabricate the cable trays to from Ladder Type 2.0 mm thick M.S. Flat/ Angle iron with bolts, washer and nuts. as per approved design. The tray should comply with the specification of NEC (National Electric Codes) and NEMA (National Electric Manufacturers Association). The steel should be as per IS:226 and galvanising as per IS :2629/BS 729/ASTM 123. The rate shall also include for supporting steel ,jointing fish plates , fixing accessories , nuts bolts, supporting down rods, dash fastener, cutting the RCC etc. complete as required. |  |  |  | 0
0
a | 300 mm wide x 50 mm x 2.0 mm thk | RM | 5 |  | 0
0
8 | Fabricating ,supplying to site of installation, installation of 500 mm size of 105 mm height mesh type EZ -Electroplated Zinc ( Legrand - Cablofil make ) cable tray including threaded G.I. down rods, dash fasteners , cablofil fixing accesories etc. complete as required. Cablofil make | RM | 5 |  | 0
0
| TOTAL CARRIED OVER TO SUMMARY |  |  |  | 0
0
F | DISTRIBUTION BOARDS |  |  |  | 0
0
1 | Supply,inginstalling ,connecting testing and commissioning of the following double door 1/4 rows vertical type 1.6 mm thick and 1. 4 thick door sheet steel enclosed fully recessed type, TPN Miniature Circuit Breakers Distribution Boards dust proof, verm­in proof, with hinged and lockable doors complete with DP MCB's and inter-connection with copper wire , insulated copper bus bar , cable glands­/conduit entry bushes, bonding to earth and paint­ing. Also provide separate neutral busbar for each phase. Provide separate Earth Links for each phase. Use brass thimbles for connections of all wires. 1 row for single phase and 4 rows for 3 phase. Provide separate 4 way 63 A main neutral link also. The phase busbar links shall be factory pre insulated. |  |  |  | 0
| Note :- The IP rating of the DB should be IP 43 . |  |  |  | 0
| Provide DB charts in laminated sheets in all Distribution Boards |  |  |  | 0
| A4 size SLD to be fixed on all DBs. |  |  |  | 0
0
1 | Light & Power Distribution Board |  |  |  | 0
0
a | 10 Way TPN DB, each phase consisting of 8 Nos. 10/20 AMP SP MCB’s and controlled by one number 100 mA sensitivity 63 AMPS DP RCCB backed up with 1 no 63 Amps 4 pole MCB. | Nos | 0 |  | 0
0
b | 12 Way TPN DB, each phase consisting of 10 Nos. 10/20 AMP SP MCB’s and controlled by one number 100 mA sensitivity 63 AMPS DP RCCB backed up with 1 no 63 Amps 4 pole MCB. For Light & VRV DB | Nos | 3 |  | 0
0
c | 14 Way TPN DB, each phase consisting of 12 Nos. 10/20 AMP SP MCB’s and controlled by one number 100 mA sensitivity 63 AMPS DP RCCB backed up with 1 no 63 Amps 4 pole MCB. For Power DB | Nos | 3 |  | 0
0
d | 12 Way SPN DB, consisting of 8 Nos. 10/20 AMP SP MCB’s and controlled by one number 100 mAsensitivity 63 AMPS DP RCCB backed up with 63 Amps DP MCB as incomer. For Emg DB | Nos | 1 |  | 0
0
2 | UPS Distribution Boards (All MCB's in workstation DB's should be D Curve) |  |  |  | 0
0
a | 12 Way TPN DB, each phase consisting of 10 Nos. 10/20 AMP SP MCB’s and controlled by one number 63 AMPS DP RCCB (100 mA) for each phase and 1 no. 63 amps 4 pole MCB incomer. | Nos.. | 1 |  | 0
0
b | 14 Way TPN DB, each phase consisting of 12 Nos. 10/20 AMP SP MCB’s and controlled by one number 63 AMPS DP RCCB (100 mA) for each phase and 1 no. 63 amps 4 pole MCB incomer. | Nos.. | 1 |  | 0
0
c | 12 Way SPN DB, consisting of 18 Nos. 10/20 AMP SP MCB’s and controlled by one number 100 mA sensitivity 63 AMPS DP RCCB backed up with 63 Amps DP MCB. For UPS DB | Nos.. | 0 |  | 0
0
d | 12 Way SPN DB, consisting of 4 Nos. 25/32 AMP DP MCB’s and controlled by one number 100 mA sensitivity 63 AMPS DP RCCB ( 100 mA) for backed up with 63 Amps 4D MCB. The bus bar shall be Twin bus bar. For SERVER DB | Nos.. | 2 |  | 0
0
3 | Supply, installation, testing and commissioning of sheet metal with 100 A TPN MCB. This shall include cable entry boxes both for incoming and outgoing cable). For 30 KVA UPS. | Nos. | 0 |  | 0
0
4 | Supply, installation, testing and commissioning of sheet metal with 32 A DP MCB. This shall include cable entry boxes both for incoming and outgoing cable). For 3 & 1 KVA UPS. | Nos. | 2 |  | 0
0
5 | Supply, installation, testing and commissioning of sheet metal weather proof enclosure with 63 A FP RCBO(300mA) This shall include cable entry boxes both for incoming and outgoing cable) For VRV units. The enclosure shall be IP 42. For VRV Out Door units | Nos. | 9 |  | 0
0
6 | Supply, installation, testing and commissioning of sheet metal weather proof enclosure with 40 A FP RCBO(300mA) This shall include cable entry boxes both for incoming and outgoing cable) For VRV units. The enclosure shall be IP 42. For VRV Out Door units | Nos. | 2 |  | 0
0
7 | Supply, installation, testing and commissioning of sheet metal weatherproof Enclosure with 25/32 A DP MCB. This shall include cable entry boxes both for incoming and outgoing cable). | Nos. | 0 |  | 0
0
8 | Supply, installation, testing and commissioning of sheet metal with 16 A FP MCB. This shall include cable entry boxes both for incoming and outgoing cable). | Nos. | 1 |  | 0
0
| TOTAL CARRIED OVER TO SUMMARY |  |  |  | 0
0
G | SUB DISTRIBUTION PANELS |  |  |  | 0
0
1 | Sub Distribution Panels |  |  |  | 0
| Design, manufacture, supplying & installing at site in positioning, connecting, testing and commissioning of the following cubical type, dead front, 2mm thick sheet steel enclosed, free standing indoor type extendible Sub Distribution Panel with vermin proof hinged lockable doors for each compartment provide bus bar interconnections for incoming and outgoing including feeders earthing and painting and as per specifications. |  |  |  | 0
Note | Provide insulated dedicated earth link in all UPS Panels |  |  |  | 0
| All MCCB's 200 Amps and above shall be Microprocessor based |  |  |  | 0
| All Light & Power panel ,UPS and A.C. Panel incomer MCCB shall have Over current, Earth fault and short circuit protection. |  |  |  | 0
| All Incomer MCCB's in UPS Panels shall be Microprocessor based |  |  |  | 0
| The microprocessor based MCCBs shall have |  |  |  | 0
| Over Load (Phase) |  |  |  | 0
| Current setting Ir(Ir=XIn) OFF 0.4 to 1.0 in steps of 0.1 |  |  |  | 0
| Time delay , tr( Inverse) 10 sec at 6/r |  |  |  | 0
| Over Load (Neutral) |  |  |  | 0
| Current setting In (Intrl =XIr) 0.5, 0.75&1.00 Intrl |  |  |  | 0
| Inverse 10 sec at 6 Intrl/Fixed 200ms |  |  |  | 0
| Short Circuit setting -2- 10 |  |  |  | 0
| Instantaneous - 1.5-1 |  |  |  | 0
| All MCB's in UPS Panels shall be D Curve |  |  |  | 0
| In all Electrical panels protective acrylic sheet to be provided in cable alley and feeders. |  |  |  | 0
| The meters shall be able to monitor all major power quality parameters Voltage , current , frequency , KVAH,KWH,Power factor and individual,harmonics, ethernet ready - IEC-625-22. |  |  |  | 0
| The ATS shall be 4 pole with inbuilt manual operating switch. In case the controller of the ATS fails it should be capable of transferring the load while the ATS is in maintenance. The ATS and controller should be same make |  |  |  | 0
| Provide On / Off and trip indicating lamp on main incomer only. |  |  |  | 0
| Panel construction shall be Form 3b for all Panels with MCCB outgoings and Form 2b for all Panels with MCB's outgoings. |  |  |  | 0
| The Earth fault release/relay and CBCTs shall be same make as OEM Switchgear been used in the Panels. It shall not trip on imbalance of load. |  |  |  | 0
| All meters shall have Modbus card for BMS connectivity |  |  |  | 0
| All the Electrical Panels shall be in accordance with IS 8623 standards |  |  |  | 0
0
a | The SDB L&P shall consists of : |  |  |  | 0
0
| MAIN INCOMER |  |  |  | 0
| 1 Nos. 320 A TPN MCCB (25KA/1 sec)( O/C, S/C,E/F) and neutral isolation link 100% of rated current. Terminals suitable to receive 3.5c x 300 sq. mm . Al Ar cable connection on one side and Busbar connection on the other side. |  |  |  | 0
0
| BUSBAR |  |  |  | 0
| 400 amps 4P busbar chamber of suitable length with Aluminium busbars. All busbars and interconnections shall be of suitable size aluminium strips current density of aluminium shall not be more than 0.8 Amps/ sq.mm.provide 100% capacity for neutral bus bar. |  |  |  | 0
0
| INDICATING PANELS |  |  |  | 0
| 3 nos phase indicating lamps (LED type) each backed up with MCB and switch shall be provided for each incomer. |  |  |  | 0
| Provide Intelligent Panel Meter - multifunctional meter with RS485 for all incoming feeder |  |  |  | 0
| Provide Transient Voltage Surge Suppressor Rating 40kA class II along with 63 A MCCB. Including all necessary accessories. For Switching Operation on each incomer. |  |  |  | 0
| Provide earth fault protection (EF) in the incomer MCCB |  |  |  | 0
0
| OUTGOINGS |  |  |  | 0
| 1 Nos. 200 A TPN MCCB (36 kA/ 1 sec) terminal to receive suitable Cable on one side and Busbar connection on the other side. |  |  |  | 0
| 1 Nos. 100 A TPN MCCB (36 kA/ 1 sec) terminal to receive suitable Cable on one side and Busbar connection on the other side. |  |  |  | 0
| 8 Nos. 63 A 4P MCB (10 kA/ 1 sec) terminal to receive suitable Cable on one side and Busbar connection on the other side. |  |  |  | 0
| 2 Nos. 16 A 4P MCB (10 kA/ 1 sec) terminal to receive suitable Cable on one side and Busbar connection on the other side. |  |  |  | 0
| 2 Nos. 63 A DP MCB (10 kA/ 1 sec) terminal to receive suitable Cable on one side and Busbar connection on the other side. |  |  |  | 0
| 2 Nos. 32 A DP MCB (10 kA/ 1 sec) terminal to receive suitable Cable on one side and Busbar connection on the other side. |  |  |  | 0
0
| The SDB L&P as described above and specifications complete | Set | 1 |  | 0
0
b | The UPS SDB in UPS Room shall consists of : |  |  |  | 0
0
| MAIN INCOMER |  |  |  | 0
| 1 No. 100 A 4P MCCB (25KA/1 sec)( O/C, S/C,E/F). Terminals suitable to receive 4R x 1c x 25 sq. mm Cu. Flexible cable connection on one side and Busbar connection on the other side. |  |  |  | 0
0
| BUSBAR |  |  |  | 0
| 150 amps 4P busbar chamber of suitable length with Copper busbars. All busbars and interconnections shall be of suitable size copper strips current density of copper shall not be more than 1.6 Amps/ sq.mm. |  |  |  | 0
0
| INDICATING PANELS |  |  |  | 0
| 3 nos phase indicating lamps (LED type) each backed up with MCB and switch shall be provided for each incomer. |  |  |  | 0
| Provide on/off indication lamp on each incomer and buscoupler. |  |  |  | 0
| Provide Intelligent Panel Meter - multifunctional meter with RS485 for all incoming feeder |  |  |  | 0
| Provide Transient Voltage Surge Suppressor Rating 40kA class I&II along with 63 A MCB. Including all necessary accessories. For Switching Operation on each incomer. |  |  |  | 0
| Provide earth fault protection (EF) in the incomer MCCB |  |  |  | 0
0
| OUTGOINGS |  |  |  | 0
| 4 Nos. 63 A 4P MCB (10 kA/ 1 sec) terminal to receive suitable Cable on one side and Busbar connection on the other side. |  |  |  | 0
| 2 Nos. 63A DP MCB (10 kA/ 1 sec) terminals to receive suitable Copper Ar. Cable on one side and Busbar connection on the other side. |  |  |  | 0
| The above Panel as described above and specifications complete | Set | 1 |  | 0
0
c | The HVAC Panel at terrace shall consists of : |  |  |  | 0
| It is outdoor type |  |  |  | 0
0
| MAIN INCOMER |  |  |  | 0
| Main Incomer 1 Nos 200A TPN MCCB (36KA) and neutral isolation link 100% of rated current.Terminals suitable to receive 3.5c x 150 sq. mm AL cable connection on one side and Busbar connection on the other side. |  |  |  | 0
0
| BUSBAR |  |  |  | 0
| 300 amps 4P busbar, chamber of suitable length with aluminium busbars. All busbars and interconnections shall be of suitable size Al strips current density of Al shall not be more than 0.8 Amps/ sq.mm. |  |  |  | 0
0
| INDICATING PANELS |  |  |  | 0
| 3 nos phase indicating lamps (LED type) each backed up with MCB and switch shall be provided for each incomer. |  |  |  | 0
| Provide Intelligent Panel Meter - Dual Source Energy Meter EM 6438 with RS 485 port for all incoming feeder |  |  |  | 0
| Provide TVSS (40KA) |  |  |  | 0
0
| OUTGOINGS |  |  |  | 0
0
| 11 Nos. 63 A 4P MCB (10 kA) terminals suitable to receive cable on one side and wire connection to Bus bars.. |  |  |  | 0
| 4 Nos. 40A 4P MCB (10 kA) terminals suitable to receive cable on one side and wire connection to Bus bars.. |  |  |  | 0
0
| The AC PANEL as described above and specifications complete as required. | Set | 1 |  | 0
0
2 | The contractor to submit reports of torque tightness tests for all the nut bolt cable joints in all the panels with red marking after the torque tightening has been done as per manufactures recommendation. | Set | 0 |  | 0
0
3 | Providing & fixing in position 1000 mm wide , Electrical Insulating Mats as per IS 15652:2006, 2mm thick, suitable up to 3.3 KV , fire retardant,no effect of acids, alkalies and transformer oils, moisture proof, high tensile strength and texture finish / cloth impression (Anti slip , marking on top) . | RM | 5 |  | 0
0
4 | Replacement of existing 250 A tap off box with 400 A tap off box at site with all the necessary accessories complete as required. | Nos. | 0 |  | 0
0
5 | Supply & fixing in position approved shock treatment chart written in English, Hindi and Local language. These charts shall be framed in wooden frame & covered with clear glass. | Nos. | 1 |  | 0
0
6 | Supply & fixing in position the best quality danger notice boards of approved shape & size as reqd. by the local Electrical Inspecting Authority written in English, Hindi & local language. | Nos. | 1 |  | 0
0
7 | Supply & fixing in position the Electrical A 1 Size SLD chart in the UPS/electrical room . These charts shall be framed in wooden frame & covered with clear glass. | Nos. | 1 |  | 0
0
8 | Supplying the first aid box as approved by John Ambulance society. | Nos. | 1 |  | 0
0
9 | Supply & Fixing of NO/NC Relay Module complete as required. | Nos. | 0 |  | 0
0
10 | 2 core -1.5 sq.mm PVC FRLS wires in already laid suitable size of M.S conduit complete as required. | Rmt | 0 |  | 0
0
11 | Supply, Installations, Testing and Commissioning of 2 Kg Fire Suppression System (CQRS) in all Floor Panels of Electrical and UPS Room to be included. - Automatic Direct Low Pressure Fire Suppression System, UL Listed FK-5-1-12 Extinguishing Fluid shall be filled in UL Listed Cylinder, UL Listed Pressure Switch should be integrated in DLP Valve for Indication on Fire Suppression Panel and Main Fire Alarm System, 15 Meter UL Listed Detection Tube shall be UV Protected made of Modified Polyamide associated with End of Line Adapter with Pressure Gauge, master Control Panel with A/V Alarm and Battery Backup along with Potential Free Contact to integrate with existing Fire Alarm System for Central Monitoring. Mounting Bracket with all necessary accessories. complete in all respect. System Component Approval: Cylinder-UL Listed, Gas-UL Listed, Detection Tube-UL Listed, Pressure Switch-UL Listed Make: FireMech / Ceasefire / Honeywell | Nos. | 0 |  | 0
0
| TOTAL CARRIED OVER TO SUMMARY |  |  |  | 0

## Light Fixtures LAB
S.No. | Description | Unit
|  |  | Qty | Rate In Rs. | Amount in Rs.
H | SUPPLY & INSTALLATION OF LIGHTING FIXTURES |  |  |  |  | *Quoted Installation
1 | Supply & Fixing in position testing and commissioning of the following Lighting fixtures at site including all type of fixing accessories complete as required etc. Use all light fixture shall be LED Type. (Samples of all light fixtures to be submitted to the client/architect/consultant for approval prior to procurement of fixtures)
a | 32 Watts LED 600x600mm panel LED light as per approved make. | Nos | 112 |  | 0
0
b | 32 Watts LED 600x600mm panel LED Fire Proof light as per approved make.(Fire proof for Bonded store) | Nos | 0 |  | 0
0
c | 15 watts Suspended Cylindrical LED light as per approved make. | Nos | 0 |  | 0
0
d | Suspended Channel LED light (90x1500) at Cabins as per approved make | Nos | 0 |  | 0
0
e | Suspended Channel LED light (60x1200) as per approved make | Nos | 55 |  | 0
0
f | 13 wattts Surface Mounted LED Down light as per approved make | Nos | 0 |  | 0
0
g | 13 wattts Recessed LED Down light as per approved make | Nos | 10 |  | 0
0
h | Supply of track mounted spot light 10W-850lm cylindrical Shape, | Nos | 0 |  | 0
0
i | Track for mounting Spot 1 meter standard length. | Rmt | 0 |  | 0
0
j | 500 mm Dia Suspended Decorative LED hanging light as per Architect /Client basic cost Rs. 5500 | Nos | 0 |  | 0
0
k | 750 mm Dia Suspended Decorative LED hanging light as per Architect /Client basic cost Rs. 7500 | Nos | 0 |  | 0
0
l | 15 Watts LED Wall light as per Architect/Client basic cost Rs. 2500 | Nos | 0 |  | 0
0
2 | Supply, Installation, Testing & Commissioning of 3 Watts LED Ni Cd Battery backup up to 1.5 hr emergency Exit light Prolite or equivalent make. The sample shall be submitted before ordering. or Equivalent make. | Nos | 6 |  | 0
0
3 | Supply, installation, testing commissioning of recessed ceiling mounted photo cell switching units to provide ON/OFF switching of lighting in response to ambient light levels. | Nos | 0 |  | 0
0
4 | Supply & installation of Passive infra-red presence detector for lighting control to set the parameters of all meeting rooms and cabin (ON/OFF selection of lights)( Lights switch OFF in steps of 1 minute) | Nos | 0 |  | 0
a | Switches lighting OFF when sufficient daylight is present. |  |  |  | 0
b | Used as on ON/OFF daylight dependant switch or in series with a wall switch |  |  |  | 0
c | Lighting level adjustable up to 1500 lux approx. |  |  |  | 0
0
| TOTAL CARRIED OVER TO SUMMARY |  |  |  | 0

## HVAC SUMMARY
SUMMARY OF COSTS
HVAC SYSTEM FOR JSW
AIRCONDITIONING SYSTEM - OVERALL SUMMARY
ITEM | DESCRIPTION |  | AMOUNT
1 | TOTAL HVAC(B1,B3,B6) |  | 0
2 | TOTAL HVAC LAB OR CONTROL |  | 0
| T O T A L | Rs. | 0
1 | Estimated cost being furnished above does not include incidental civil, electrical and plumbing work which shall be carried out by respective agencies.
2 | Cost furnished above doesn't include GST.
3 | shaft sealent for fire isolation not inculuded in HVAC Estimate
4 | Air Curtain not inucluded.
5 | All electrical supply to the equipments are provided by electrical team
6 | GST is not included in above costing

## HVAC
PRICED SCHEDULE OF QUANTITIES
HVAC SYSTEM FOR JSW
S. NO | ITEM DESCRIPTION | UNIT | B1 | AMOUNT | B3 | AMOUNT | B6 | AMOUNT | TOTAL QTY. | RATE | AMOUNT
SECTION 'A' : HVAC WORKS FOR OFFICE SPACES
1.0 | EQUIPMENT
1.1 | VARIABLE REFRIGERANT VOLUME SYSTEM
(HEAT PUMP & COOLING TYPE )
| Supply, Installation, Testing and Commissioning of Variable Refrigerant Volume type multi unit air-conditioning system complete with indoor and outdoor units with individual controller for cooling & heating application as per the specifications and drawings. The quoted price should include clearances charges, local taxes, freight etc. Quoted price shall also be inclusive of loading, unloading, lifting & shifting on outdoor location in space available at same floor level or at terrace at suitable locations as per drawing, positioning charges besides including charges towards structural steel supports, MS base frame duly painted & vibration isolation arrangement etc. | [10 empty] | BLUESTAR
1.1.1 | OUTDOOR UNITS
| Supply, Installation, Testing and Commissioning of air cooled variable refrigerant flow modular type Coolin type units, each comprising of energy efficient multiple scroll compressors, full charge of R-410a refrigerant gas and all accessories as per the specifications. All compressors shall be inverter type. The condensing units shall be suitable to work on cooling as well as heating mode. The condensing units shall be suitable for operation on 415 ±10% volts, 50Hz, 3 phase AC power supply and complete with auto check function for connection error, auto address setting, etc. The outdoor units shall be low noise type. Quoted price shall be inclusive of Power Cable from MCCB to Outdoor unit & MS frame duly applied with 2 coat of primer & one coat of black enamel paint. The outdoor units shall be of following capacities :(Including Y-Joint) | [9 empty] | 0
| Quoted price shall be inclusive of factory applied epoxy | [9 empty] | 0
| coating (to prevent erosion of tubes & fins) of Outdoor units. | [9 empty] | 0
| VRV ODUs shall be capable of operating in following range : i. For Cooling : (-)5degC to 50degC ii. For Heating : (-)20degC to 15.5degC if applicable | [9 empty] | 0
0
0
a. | 60 HP nominal capacity high COP outdoor unit. | No |  | 0 |  | 0 | 1 | 0 | 1 |  | 0
b. | 54 HP nominal capacity high COP outdoor unit. | No |  | 0 | 1 | 0 | 1 | 0 | 2 |  | 0
c. | 52 HP nominal capacity high COP outdoor unit. | No |  | 0 |  | 0 | 1 | 0 | 1 |  | 0
d. | 44 HP nominal capacity high COP outdoor unit. | No |  | 0 |  | 0 | 1 | 0 | 1 |  | 0
d. | 38 HP nominal capacity high COP outdoor unit. | No |  | 0 |  | 0 |  | 0 | 0 |  | 0
e. | 22 HP nominal capacity high COP outdoor unit. | No |  | 0 |  | 0 |  | 0 | 0 |  | 0
f. | 20 HP nominal capacity high COP outdoor unit. | No |  | 0 |  | 0 |  | 0 | 0 |  | 0
g. | 16 HP nominal capacity high COP outdoor unit. | No |  | 0 |  | 0 |  | 0 | 0 |  | 0
h. | 14 HP nominal capacity high COP outdoor unit. | No | 1 | 0 |  | 0 |  | 0 | 1 |  | 0
h. | 8 HP nominal capacity high COP outdoor unit. FOR CRITICAL AREA (1W+1S) | No |  | 0 |  | 0 | 2 | 0 | 2 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
1.2 | INDOOR UNITS |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| Supply, Installation, Testing and Commissioning of variable refrigerant volume modular type indoor units comprising of EEV & all accessories as per the specifications. The indoor units shall be suitable to work on cooling mode. The indoor units shall be suitable for operation on 220 ±6% volts, 50Hz, 1 phase AC power supply. Ductable indoor units shall be suitable to handle extent of ductwork as shown in the design drawings and dehumidified air quantity as mentioned in the heat load summary sheet under "Special Conditions" and the indoor units shall be of following capacities. All Indoor Units shall have inbuilt Drain Pumps . Quoted price shall be inclusive of Plug Top & necessary power cable. |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| DUCTABLE UNIT |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
i. | 2825 CFM Ductable Unit (8.0 TR) | No. |  | 0 |  | 0 | 11 | 0 | 11 |  | 0
iii | 2400 CFM Ductable Unit (6.4 TR) | No. |  | 0 | 5 | 0 |  | 0 | 5 |  | 0 | 6TR
iv | 1377 CFM Ductable Unit (4.0 TR) | No. |  | 0 |  | 0 | 1 | 0 | 1 |  | 0
vi | 1130 CFM Ductable Unit (3.2 TR) | No. |  | 0 |  | 0 |  | 0 | 0 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| 4-WAY CASSETTE UNIT |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| 1218 CFM Cassette unit Type (4.0 TR) | No. |  | 0 |  | 0 | 1 | 0 | 1 |  | 0
i. | 1183 CFM Cassette unit Type (3.2 TR) | No. |  | 0 | 1 | 0 | 8 | 0 | 9 |  | 0
ii. | 830 CFM Cassette unit Type (2.5 TR) | No. |  | 0 |  | 0 | 5 | 0 | 5 |  | 0
iii. | 830 CFM Cassette unit Type (2.0 TR) | No. | 4 | 0 | 1 | 0 | 8 | 0 | 13 |  | 0
iv. | 812 CFM Cassette unit Type (1.6 TR) | No. |  | 0 |  | 0 | 6 | 0 | 6 |  | 0
v. | 600 CFM Cassette unit Type (1.3 TR) | No. |  | 0 |  | 0 | 1 | 0 | 1 |  | 0
vi. | 459 CFM Cassette unit Type (1.0 TR) | No. |  | 0 |  | 0 |  | 0 | 0 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| COMPACT CASSETTE UNIT |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
ii. | 353 CFM Cassette unit Type (1.0TR) | No. |  | 0 |  | 0 | 9 | 0 | 9 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| HI WALL UNIT |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
i | 671 CFM Hi wall Type (2.0TR) | No. |  | 0 |  | 0 |  | 0 | 0 |  | 0
ii | 530 CFM Hi wall Type (1.6TR) | No. | 1 | 0 | 1 | 0 |  | 0 | 2 |  | 0
iii | 459 CFM Hi wall Type (1.3TR) | No. |  | 0 |  | 0 | 2 | 0 | 2 |  | 0
iv | 388 CFM Hi wall Type (1.0TR) | No. |  | 0 |  | 0 |  | 0 | 0 |  | 0
v | 318 CFM Hi wall Type (0.8TR) | No. |  | 0 |  | 0 |  | 0 | 0 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
1.4 | REMOTE CONTROLS |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| Supply of Cordless handset type remote controls for the above indoor units. | No | 5 | 0 | 8 | 0 | 42 | 0 | 55 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| Supply, Installation, Testing & Commissioning of PLC Based Panel for sequencing & operational for non VRF Units for Server Room | No |  | 0 |  | 0 |  | 0 | 0 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
1.5 | CENTRALISED CONTROLLER |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| Supply,Installation, Testing and Commissioning of main centralised controller as per specifications to hook up indoor units as mentioned above. Controller shall however, be suitable for minimum 64 groups of indoor units. Centralised controller shall act as master controller for controlling of outdoor units and their associated indoor units. Controller shall be suitable to configured the inside temperature as per temperature set point on controller. Quoted price shall be inclusive of all necessary cabling as required from ODU & IDUs to controller as required & other accessories as required to make the system proper fucntional. | No | 1 | 0 | 1 | 0 | 1 | 0 | 3 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
1.6 | DRAIN PUMP |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| Supply, Installation, Testing & Commissioning of Condensate Drain Pump with adequate Sump for Hi-wall units complete with water level sensor and accessories as required. Quoted price shall be inclusive of controller, NRVs & water sensors and associated wiring etc. to make installation complete. Drain Pump shall be suitable for operation on 220+6 % volts 50 Hz, 1phase AC power supply. Drain pumps shall automatically ON/Off based on water level. |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| Insulated Drain Tray with Drain Pump @5mtr head | Nos | 1 | 0 | 1 | 0 | 2 | 0 | 4 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
1.8 | INLINE FANS |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| Supply, Installation, Testing & Commissioning of circular /rectangular inline fans for exhaust air complete with sheet metal casing, direct driven centrifugal fan, motor with proper protection and inspection door. Fan shall be suitable for operation on 220+6 % volts, 50 Hz,1 phase AC power supply. Flanges to be provided on both sides to facilitate duct connections. Fan shall be installed as shown in the drawings and will be of following characteristics : All single phase inline fans shall be provided with factory fitted speed regulators. All Fans Should be complete with Plug Top & necessary power cable. |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| Fan Capacity S.P Area to |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| No. (Cfm) (mmWG) to be exhausted |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| IF-2(Circular) 1600 25 Toilet | No |  | 0 | 1 | 0 | 1 | 0 | 2 |  | 0
i | IF-2(Circular) 900 25 Toilet | No |  | 0 | 1 | 0 | 1 | 0 | 2 |  | 0
iii | IF-2(Circular) 500 25 Toilet | No |  | 0 |  | 0 |  | 0 | 0 |  | 0
iv | IF-2(Circular) 400 25 Kitchen | No |  | 0 |  | 0 |  | 0 | 0 |  | 0
v | IF-2(Circular) 300 25 Toilet | No | 1 | 0 |  | 0 |  | 0 | 1 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
1.9 | DRY SCRUBBER : Kitchen Exhaust |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| Supply, Installation, Testing and Commissioning of Dry Scrubber comprising of extract air intake section, electrostatic precipitation technology, dry type air cleaner to remove odour, smoke and fumes from exhaust air. |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| Electrostatic section shall be made of 16 gauge galvanised sheet,high bake epoxy powder coated, washable type aluminium mesh filters, stainless steel spiked ionizers to create high voltage DC field, aluminum collector plates which should be alternatively charged positive and negative with large collecting area with 14" deep cell, to work as magnet for charged smoke and oil particles. Average efficiency of 90-95% in single pass as per DOP test method. Electrostatic Precipitator should be able to charge particles from 0.01 micron to 10 microns through solid state power supply. The system should be fitted with interlock switch for safety. The system should allow connection to a fan section to achieve 500 FPM velocity across the air cleaner. |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| Note: All motor type shall be IE3 type |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| 2500 CFM, 50 mm St. Pressure / 2.2 KW Motor | No |  | 0 | 1 | 0 |  | 0 | 1 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
2 | Air Washer : Kitchen Fresh |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| Supply of double skin air washer comprising of DIDW GI fan, Bacward curved, complete with base frame, casing made out of 0.6 mm + 0.6 mm galvanised sheet powder coated having flanged and bolted panels insulated with 25mm thick injected PUF, wet section & tank shall be made of 18G 304 A SS with FRP coating. Air-washer shall be complete with fill of depth 200 mm & face velocity across the fill shall be limited to 500 FPM. The complete Air-washer shall have an effiency of 90% & shall be complete with IE3 motor, belt, drive with flat belt, GI B Class interconnecting piping, aluminum viscous filter, float valve, quick fill, overflow and drain connection, spray headers, strainer of fire mesh brass screen etc. & of the following capacities. The Air-washer shall be complete with 2 Nos. water circulation pumps including one No. stand by pump. The pump/motor should have suitable protection cover. Selected for 90% adiabatic efficiency of evaporative medium. |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| 2300 CFM 50 mm St. Pressure / 2.2 KW Motor | No |  | 0 | 1 | 0 |  | 0 | 1 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
2.1 | Propeller Fan |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| Supply, Installation, Testing and Commissioning of Propeller Fan, Installing in any position Horizontal or Vertical . Casing of Fans shall be constructed of heavy gauge sheet steel and preferably be powder coated. Support brackets for ceiling suspension or wall mounted shall be welded to the casing for connection to hanger bolts. Threaded Rod of sufficient dia. /channel should be considered for hanging of fans. |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| Provision of all necessary accessories such as Wire Guard on inlet side and bird screen on outlet, Gravity operated louver shutters, Canvass Connection for connecting Fan assembly and Plenum should be considered, If Ducted. |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| Should be suitable for 230 V ± 10% volts Single phase 50Hz, AC supply |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| 200 CFM, 15 mm SP Toilet | No | 2 | 0 | 1 | 0 |  | 0 | 3 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
3 | PIPING |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
3.1 | COPPER REFRIGERANT PIPING |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| Supply, Installation, Testing & Commissioning of high pressure copper refrigerant piping including R410a refrigerant of suitable size as required and duly insulated with19mm/13mm thick closed cell elastomeric insulation with class 'O' fire retardant properties in tubing form. External Refrigerant piping shall be laid on GI covered cable trays. Piping inside occupied spaces shall be supported using MS hangers duly painted with black enamel paint. Entire refrigerant piping work shall be carried out in accordance with the specifications.MS sleeves of requisite size shall be provided at wall crossing. Quoted price shall be inclusive of necessary glass cloth and minimum two layers of UV protection paint to be applied over insulation for all exposed pipes of approved make. Piping shall be of following sizes : |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| Internal Refrigerant piping in exposed ceiling area & external refrigerant piping shall be laid on Ladder type cable trays. Cable trey used for external refrigerant piping shall be covered with cover. |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| Pipe Size Thickness of CSE |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| (O.D.) Insulation |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
a. | 41.3 mm 19 mm | RM |  | 0 | 30 | 0 | 100 | 0 | 130 |  | 0
b. | 34.9 mm 19 mm | RM |  | 0 |  | 0 | 20 | 0 | 20 |  | 0
d. | 28.6 mm 19 mm | RM | 30 | 0 |  | 0 | 30 | 0 | 60 |  | 0
f. | 22.2 mm 19 mm | RM |  | 0 |  | 0 | 60 | 0 | 60 |  | 0
g. | 19.1 mm 13 mm | RM |  | 0 | 20 | 0 | 20 | 0 | 40 |  | 0
h. | 15.9 mm 13 mm | RM |  | 0 | 60 | 0 | 30 | 0 | 90 |  | 0
i. | 12.7 mm 13 mm | RM | 50 | 0 | 30 | 0 | 60 | 0 | 140 |  | 0
j. | 9.5 mm 13 mm | RM |  | 0 | 40 | 0 | 80 | 0 | 120 |  | 0
k. | 6.4 mm 13 mm | RM | 30 | 0 | 20 | 0 | 40 | 0 | 90 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
3.2 | FITTINGS |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| Supply,Installation,Testing & Commissioning of following |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| imported copper fittings to be provided in |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| refrigerant pipe line. |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
a. | Refnet Joints (Y- Joints) | No | 5 | 0 | 10 | 0 | 46 | 0 | 61 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
3.3 | CONDENSATE DRAIN PIPING -cPVC |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| Supply, Installation, Testing and Commissioning of cPVC pipes cut to required lengths and installed for condensate drain. Quoted price shall be inclusive of supply and fixing in position the necessary fittings like elbows, tees reducers etc. and supporting arrangement in accordance with the approved shop drawings and specifications. Pipes shall be insulated with 9mm thick closed cell elastomeric insulation with class 'O' fire retardant properties in tubing form . Pipes shall be of following sizes : |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
a. | 50mm dia | RM |  | 0 |  | 0 |  | 0 | 0 |  | 0
b. | 40mm dia | RM |  | 0 |  | 0 | 15 | 0 | 15 |  | 0
c. | 32mm dia | RM | 8 | 0 | 15 | 0 | 30 | 0 | 53 |  | 0
d. | 25mm dia | RM | 15 | 0 | 25 | 0 | 80 | 0 | 120 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
3.4 | Cable Tray for Copper & Drain Pipe |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| Supply, fabricating and installing following sizes of hot dip galvanized perforated type Cable tray with cover including factory fabricated supports, horizontal and vertical bends, reducers, tees, cross members and other accessories as required and duly suspended from the ceiling with MS suspenders including painting, Covered in Exposed Area on Copper pipe etc. |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| 200 mm wide x 100 mm deep (2 mm) | RM |  | 0 | 50 | 0 | 150 | 0 | 200 |  | 0
| 150 mm wide x 100 mm deep (2 mm) | RM | 50 | 0 | 35 | 0 | 100 | 0 | 185 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
3.5 | FACTORY FABRICATED DUCTING |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| Supply , Installation and Testing of factory fabricated GSS ducting complete with vanes, splitter dampers, fire retardant gaskets hanging arrangement including fully threaded GI rods and GI "C" channels/ rolled steel wires or Gripple Wire Rope Hangers & Supports complete with end fixing, GI "C" channels etc. as approved by clients/consultants in accordance with the approved shop drawings and specifications. Quoted price shall be inclusive of necessary scaffolding charges towards installation of supply/exhaust air ducts outside or within building wherever required. Quoted price should also include necessary charges towards duct supporets including MS angle/channel arrangement as required for ducts being installed outside or within building wherever required. |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| Spacing between duct supports should not exceed 2m in both cases i.e GI rods with GI "C" channels & Gripple Wire Rope Hanger support . In case of Gripple Wire Rope Hanger support for duct sizes above 1800mm, MS angles duly painted with black enamel paint should be used along with neoprene pad in between the duct & MS angle. All duct support to be provided with check nuts (lock nuts). |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| While selecting the duct supports vendor shall ensure vibration free installation.Quoted price shall be inclusive. |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
a. | 24 G (0.60 mm) - 1 mm to 750 mm | SqM |  | 0 | 80 | 0 | 290 | 0 | 370 |  | 0
b. | 22 G (0.80 mm) - 751 mm to 1500 mm | SqM |  | 0 |  | 0 | 150 | 0 | 150 |  | 0
c. | 20 G (1.0 mm) - 1501 mm to 2250 mm | SqM |  | 0 |  | 0 |  | 0 | 0 |  | 0
c. | 18G (1.2 mm) - 2250 mm to Above Plenum | SqM |  | 0 |  | 0 | 60 | 0 | 60 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
3.6 | SITE FABRICATED DUCTING |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| Supply, Fabrication, Installation and Testing of sheet metal ducts complete with vanes, splitter dampers, hanging arrangement including check nuts in accordance with the approved shop drawings and specifications. |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
a. | 24 G (0.60 mm) - 1 mm to 750 mm | SqM |  | 0 | 8 | 0 | 20 | 0 | 28 |  | 0
b. | 22 G (0.80 mm) - 751 mm to 1500 mm | SqM |  | 0 |  | 0 | 5 | 0 | 5 |  | 0
c. | 20 G (1.00 mm) - 1501 mm to 2250 mm | SqM |  | 0 |  | 0 |  | 0 | 0 |  | 0
c. | 18 G (1.2 mm) - 2250 mm to Above & Plenum | SqM |  | 0 |  | 0 |  | 0 | 0 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
3.7 | Flat Oval Spiral Duct |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| Supply hollow partial pieces, Assembling, installation, testing and commissioning of G.S.S. metal ducting & as per ISI specifications & tender drawings. The price shall include with rolamate / TDF Corner flanges with nut bolt, cleat for clamping, self adhesive gasket / sealent (neoprene gasket) & supports (GI Threaded Rod & Chilly clamp (Thickness & Width shall be as per manufacturere Standard) by or Wire Rope Hangers etc. (Gripple Wire & Hangers can be used at site for support) |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| With 13 mm thick internal insulation |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| 22 G (0.80 mm) | SMT |  | 0 | 60 | 0 | 130 | 0 | 190 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
3.8 | DUCO PAINT (For Flat Oval Exposed Duct) |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| Supply and Application of minimum two coats of Duco Paint of colour and shade as approved by the Architects for exposed flat oval spiral/round ducts. Quoted price shall be inclusive of primer before paint and all neceesary arrangement as required for providing the paint over duct. shall be slected as per IGBC guidlines | SMT |  | 0 | 60 | 0 | 130 | 0 | 190 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
3.9 | Supply, Installation, Testing and Balancing of round supply air diffusers with removable key operated butterfly volume control dampers as per the approved shop drawings and specifications.The diffusers shall be anti-smudge flush type as approved by the interior designer. Diffuser shall be complete with GI cone with circular connection at the rear. |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| With Volume Control Dampers |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| 200mm dia Neck Size round diffuser with GI cone | NOS |  | 0 | 6 | 0 | 20 | 0 | 26 |  | 0
| 300mm dia Neck Size round diffuser with GI cone | NOS |  | 0 |  | 0 |  | 0 | 0 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
4 | FLEXIBLE CANVASS CONNECTIONS |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| Supply, Installation, Testing of 125mm deep antivibration flexible joints at the outlet of air handling units/ductable split units//inline fans. Flexible connections shall be constructed using imported fire retardant fabric with extruded aluminium frame/flange on both sides of approved make. | SqM |  | 0 | 2 | 0 | 5 | 0 | 7 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
5 | LINEAR GRILLES |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| Supply, Installation , Testing and Balancing of supply & return air grilles with vcd complete with fixed core as per approved shop drawings and specifications. The grilles shall be of approved colour & shade. |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| Powder coated aluminium grilles of extruded sections with integral flanges on both sides & ends as required complete with corner pieces. |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| i. 100/150/200/250 mm High grilles | SqM |  | 0 | 2 | 0 | 8 | 0 | 10 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
3.1 | Volume control dampers (VCD) |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| Supply,Installation, testing and commissioning of 16 G GSS constructed opposed blade volume control dampers complete with brass bush & manual operating handles within ducts to be provided with suitable links, levers and quadrants for control of volume of air flow for proper air balancing | SQM |  | 0 | 2 | 0 | 4 | 0 | 6 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
3.2 | CURVE GRILLES |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| Supply, installation, testing & commissioning of Powder coated Aluminium curve grilles for supply & return air normal flow one way as per specification & the sizes will be as per tender drawing mention: | SQM |  | 0 | 2 | 0 | 4 | 0 | 6 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
3.2 | AIR TRANSFER GRILLES |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| Supply, Installation and Testing of of extruded aluminium powder coated air transfer grilles to be provided at the door of toilets/pantry. | SqM | 1 | 0 | 1 | 0 | 2 | 0 | 4 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
3.3 | Supply, Installation and testing of Powder coated Aluminium extruded Fresh / Exhaust air louvers with bird screen as specification and shop drawing. | SqM | 1 | 0 | 1 | 0 | 2 | 0 | 4 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| Return Air Baffles |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| Supply, Fabrication, Installation and Testing of return air baffles made of 24 G GS sheet metal (class VIII-120GSM Zinc Coaing) ducts with 12 mm open cell Nitrile Rubber foam within 160-180 Kg/m3 density acoustic insulation, hanging arrangements in accordance with the approved shop drawings and specifications. | SMT |  | 0 | 2 | 0 | 5 | 0 | 7 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
3.4 | INSULATION |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| ACOUSTIC LINING OF DUCTS |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| Using Open Cell Nitirile Rubber |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| Supply and Application of internal acoustic lining of supply air ducting using open cell nitrile rubber insulation with density within 140-180 Kg/m3 as per the approved shop drawings and specifications. Insulation material shall be bonded with the ducts using metal screw and washers to facilitate grip to the GI sheet. |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| 15mm thick lining | SMT |  | 0 |  | 0 | 120 | 0 | 120 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
3.5 | THERMAL INSULATION OF DUCTS |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| (Class 'O' Fire Retardant Properties Closed Cell Elastomeric insulation) |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| Supply and Application of external thermal insulation of supply /return air ducting using closed cell elastomeric nitrile rubber insulation with class 'O' fire retardant properties as per the specifications and drawings. Adhesive - AC Duct King Eco Fresh |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
a. | 13mm thick insulation-For Supply Air ducts in ac area | SqM |  | 0 |  | 0 | 480 | 0 | 480 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
b. | 19mm thick insulation-For Supply Air ducts in non-ac area(Exposed to sun) | SqM |  | 0 |  | 0 |  | 0 | 0 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
3.6 | ELECTRICAL WORKS |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| Power Distribution of HVAC System Shall be covered in main electrical package |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| Incoming power supply shall be provided by main electrical contractor/ |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| electrical consultant at each HVAC Equipment, VRV Indoor & |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| outdoor unit along with a TPN MCCB and earthing. |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
3.7 | Control & Transmission Wiring |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
a. | Providing & fixing control cum transmission wiring of 2 core/4.0Core x 1.5/2.5 sqmm copper in suitable conduits between indoor and out door unit & their remotes. | Rmt. | 60 | 0 | 120 | 0 | 220 | 0 | 400 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| Supply, Installation, Testing & Commissioning of PLC Based Panel for sequencing & operational for VRF Units for UPS & Server Room | Nos. |  | 0 |  | 0 | 3 | 0 | 3 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
1.1 | CO2 SENSOR with display |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| SITC of CO2 Sensor for rooms only with display with (WiFi Enable/BMS Compatible) | Nos. |  | 0 |  | 0 |  | 0 | 0 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
1.2 | INDOOR AIR QUALITY MONITOR WITH DISPLAY |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| SITC of IAQ Monitor with Display to measure the levels of PM 2.5, VOCs, CO2, Temperature, Humidity on a real time basis. The IAQ Monitor shall be RS485 enabled and should be capable of getting connected with Wi-Fi. The Monitor should be capable of sending the indoor air quality information on remote LED displays as well. The Monitor should indicate the quality of air through changing the colours as per the NAAQS standards and should meet the WELL/LEED building standards. | Nos. |  | 0 |  | 0 |  | 0 | 0 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
1.3 | BIO POLAR IONISER |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| The Active Air Purification system should consist of Supply, Installation, Testing and commissioning of Bipolar Ionisation System. The Bipolar Ionisation System must be a combination of Tube Based Model and Needle Point Model (Needle Point should have Nitinol (nickel titanium) Needles) and Carbon Fibre Brush Model, System should produce positive and negative ions for creating a Bio Climate rich in ions and hence neutralising harmful pollutants including pathogens, Volatile Organic Compounds and Particulate Matter. |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| Manufacturers shall provide Test report from Internationally/Nationally recognized Lab for proven efficacy on below pathogens with minimum kill rates for the following pathogens given the allotted time and in a space condition: a) SARS-CoV-2 (COVID-19) Human Strain b) MS2 Bacteriophage (Surrogates COVID-19) c) Omicron Variant of SARS-CoV-2 d) H1N1 e) Total Bacterial Count Reduction rate of more than 90% from NABL Accredited Lab f) Yeas & Mold/Total fungal count Reduction rate of more than 90% from NABL Accredited Lab |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| For Cassette / Hi Wall units | Nos. |  | 0 |  | 0 |  | 0 | 0 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
1.4 | INDOOR AIR PURIFYING IONISERS(For Ductable Units) |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| (REME Cell/Bi Polar Plasma Ionnisers) |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| Supply, Installation, Testing & Commissioning of REME (reflective electromagnetic energy cell) /Bi Polar Plasma Ionisers cell comprising of quad metallic compound target/ hydrated cataytic matrix cell duly enclosed by a poly casing tube, with the capability to produce friendly oxidizers like ionized hydroxyls, hydrogen peroxide, Super Oxide Ions. The tube should be duly encased in poly tube to prevent glass or mercury leakage into the atmosphere. The cell will have built in fiber optic device as remote indication of this operation. |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| The unit shall have inbuilt multipin ion generator along with ultrasonic radio frequency waves for pest repellancy. System should be suitable for all types of indoor units AHU, TFA, Ductable ac, Cassette AC& hi-wall units. The cells shall be installed as required to fit in the plenum, duct at the AHU in the supply air stream. |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| The system shall be capable of reducing microbial bacteria, virus and spores, VoC’, odors and particulates matter. The equipment shall conform to UL, TUV, CSA EU,CE, FDA, ISO, RoHS & CCMB Report standards, certifications as applicable and shall be submitted along with the technical submital. System should kill /deactivate microorganism and shall have proven effectiveness on COVID-19 human strain and its surrogate through Certified National/International lab. Units shall be UL2998 certified for Zero Ozone. |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| The power / control cabling between the ioniser units and the power source / controls shall be included in the cost. The ionizers should be selected by considering a load factor calculation for each specific area where the equipment is to be installed. Length selection should be per duct piece in which is to be installed. Detailed selection chart to be furnished indicating the model number for each unit. Cells Should be complete with Transformers, control cabling and Plug Top & necessary power cable. |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| Total Nos. of ionisers shall be as per air quantity distributed in individual duct drawn from main plenum/ AHUs in approved shop drawing. |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
a. | 2825 CFM Ductable Unit (8.0 TR) | No. |  | 0 |  | 0 |  | 0 | 0 |  | 0
b. | 1377 CFM Ductable Unit (8.0 TR) for TFA | No. |  | 0 |  | 0 |  | 0 | 0 |  | 0
c. | 1624 CFM Ductable Unit (4.5 TR) | No. |  | 0 |  | 0 |  | 0 | 0 |  | 0
d. | 1377 CFM Ductable Unit (4.0 TR) | No. |  | 0 |  | 0 |  | 0 | 0 |  | 0
e. | 1024 CFM Ductable Unit (6.5 TR) for TFA | No. |  | 0 |  | 0 |  | 0 | 0 |  | 0
f. | 1130 CFM Ductable Unit (3.2 TR) | No. |  | 0 |  | 0 |  | 0 | 0 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| Electrically Charged Filter a) "Air purification for ceiling suspended Ductable indoor units and AHUThe air purification system should be suitable to reduce harmful pollutants like particulate matter (PMx), PM 2.5, allergens, pollen, smoke, bacteria, pathogens etc. based on below principle technology viz;Impingement, Polarisation and Agglomeration as a passive air purification It should be a slim structured unit specifically designed for integration in Return Air path of ceiling suspended indoor units/AHU to centrally capture. It should be equivalent to Merv-14 or Higher efficiency for AHU and Ductable* Units with low pressure drop. It should have 3x working principles and it should be aluminium based or powder coated steel casing and should be self-contained. It should be a US patented technology with UL certified components. The units shall meet ANSI/ASHRAE 52.2 standards and have valid test report to verify filtration efficiency. The Basic Media of Electric Filter shall Carry Class 2 Fire Rating Listing by UL.The EAC filter/Electrostatic percipitator (ESP), which have Metal based collection plate shall not be accepted. The Supplier shall carry UL2998 certification or at least Acknowledgement letter from UL2998 for testing against Zero Ozone Emission. The system shall be integrated with the existing pre-section filter area of Units. The test report for pressure drop need to be submitted for passive air purification and the same shall be demonstrated at site." |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| Ionizers shal be suitable for following Equipment |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
a. | 2825 CFM Ductable Unit (8.0 TR) | No. |  | 0 |  | 0 |  | 0 | 0 |  | 0
b. | 1377 CFM Ductable Unit (8.0 TR) for TFA | No. |  | 0 |  | 0 |  | 0 | 0 |  | 0
c. | 1624 CFM Ductable Unit (4.5 TR) | No. |  | 0 |  | 0 |  | 0 | 0 |  | 0
d. | 1377 CFM Ductable Unit (4.0 TR) | No. |  | 0 |  | 0 |  | 0 | 0 |  | 0
e. | 1024 CFM Ductable Unit (6.5 TR) for TFA | No. |  | 0 |  | 0 |  | 0 | 0 |  | 0
f. | 1130 CFM Ductable Unit (3.2 TR) | No. |  | 0 |  | 0 |  | 0 | 0 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
4.5 | STARTER PANEL FOR DRY SCRUBBER |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| Supply, installation, testing & commissioning of the following starters in a sheet metal enclosure complete as required and as per site conditions: |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| DOL/Star Delta Starter of following rating with Auto/ Manual selector switch, MPCB/MCCB, over load relay, single phasing preventor, ON/OFF/ Trip indication lamps, Ammeters with CTs, ON/OFF push Buttons, contractor and suitable No. of Potential free contacts for remote / local operations, indication, interlocking with Fire Alarm panel and Building Management system. (Starter shall have MPCB/MCCB in the incomer as per type -2 coordination for fuseless type feeders.) |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| 2.2 KW For DOL Starter | Nos |  | 0 | 2 | 0 |  | 0 | 2 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| HYDROGEN EXHAUST |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| INLINE FANS - For Hydogen Exhaust |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| Supply, Installation, Testing and Commissioning of circular inline fans for exhaust complete with sheet metal casing, direct driven centrifugal fan constructed out of GSS, class "B" insulated motor with proper protection and inspection door. Fan shall be suitable for operation on 415 ±10% volts, 50Hz, 3 phase AC power supply. Flanges to be provided on both sides to facilitate duct connections. Fan shall be provided with factory fitted speed regulation arrangement. Fan shall be Explosion Proof Type. Fan shall be installed as shown in the drawings and will be of following characteristics : |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| Quoted price shall be inclusive of gravity louvers. |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| Fan Capacity S.P Area to |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| No. (Cfm) (mmWG) to be exhausted |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| IF-1,2 150 15-16 Battery Room | No |  | 0 | 0 | 0 | 1 | 0 | 1 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| HYDROGEN SENSORS |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| Supply, Fixing and Testing of H2 Sensors. Sensors should be capable to give command directly to Inline fan panel after increasing of H2 level beyond certain specified levels. Quoted price shal be inclusive of Power cabling and control cabling as required between sensor & panels etc. Sensors should be able to automatically switch ON/OFF the Fans after increasing/control of H2 level beyond certain specified levels respectively. Price shall also be inclusive of all accessories required to make installation complete whether specified or not. H2 sensors shall be capable for BMS Integration as well. | No |  | 0 | 0 | 0 | 1 | 0 | 1 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| Panels - Hydrogen Exhaust |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| Supply, Installation, Testing and Commissioning of the following cubical type panels made out of 14 guage CRCA structure, base channel, complete with, moulded case circuit breakers, meters, indicating lamps, current transformer etc. Complete in all respects, insulated bus bars with heat shrinkable PVC sleeve in suitable bus chambers, interconnection, small wiring, name plate, danger plate, earth bus etc. & comprising of compartments with hinged door for each feeder & its accessories, cable alley with hinged doors, bus chamber with bolted door etc. The panel being of dust & vermin proof construction with rubber gasket attractively powder coating etc. The panel shall be free standing type / wall mounted type as per relavant drawing and comprising with the following: |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| Notes : |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| 1. All MCCBs shall be with operating handle. |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| 2. CTs burden shall be 15VA & accuracy class 1.0 |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| 3. CTs shall be cast resin type . |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| 4. All MCCBs shall be with thermal magnetic |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| release. |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| 5. All indication lights shall be LED type. |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| 6. All meter shall be digital type. |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| 7. The outgoing starter feeders for pumps,AHUS |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| & ventilation fans shall be provided |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| with push buttons & indicating lamps for |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| status indication. |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| 8. Proper isolation switches to be |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| provided near air handling units and |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| ventilation fans in weather proof enclosure. |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| 9. Bimetal overload relay for all the |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| starters shall have built-in single |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| phasing prevention feature. |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| 10. Electrical interlocking wiring shall be |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| provided as per system requirement. |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| 11. Power cabling/wiring with necessary |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| earthing from source to each panel |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| and each exhaust fan shall be |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| provided by other agencies. |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| 12. All HVAC equipment shall be compatible with |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| BMS and necessary provisions to be made |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| in each panel. |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| Explosion Proof Fan Panel-1 (Location : Near Fan) | No |  | 0 |  | 0 | 1 | 0 | 1 |  | 0
| For Battery Room - 90W |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| 1x250Cfm Fan |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| 10 Amps ,TP MCB -- 1set |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| (0-500) V digital Voltmeter with built in Selector |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| switch -- 1set |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| Digital Ammeter with built in selector |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| switch- 1set |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| Current Transformers - 1set |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| LED type RYB phase indication lights- 1set |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| LED type ON & OFF indication lights -- 1set |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| START-STOP Push Buttons -- 1set |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| 90 Watt DOL starter with built-in single phasing |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| preventer & overload relay -- 1 set |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| Auto-Manual type selector switch |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| to facilitate auto start of Fans |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| after restoration of power -- 01 set. |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| Timer for Scheduled On/Off-- 01 set. |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| Contactors, Potential Free Contacts, Control wiring and |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| safety circuit as required with start-stop push buttons |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| stay put or lockable type -1 set. |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| (Panel to be integrated with Hydrogen Sensor for ON/Off operation). |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| CABLING |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| Supply, laying, affecting connections and Testing of the following sizes of 1.1 KV armoured PVC insulated copper/ aluminium conductor cables. Cables shall be inclusive of all clamps, saddles, screws, cable identification tags, cable terminal joints including terminal lugs, insulating tapes, affecting terminal connections to the equipment as per the specifications and as required. Quoted price shall be inclusive of perforated duly painted 2mm thick MS trays and 8 SWG copper earth wire for AHUs. |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| All cables shall be FRLS type. |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| 3 C x 2.5 Sqmm cable (Copper) | RMT |  | 0 |  | 0 | 1 | 0 | 1 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| TOTAL |  |  | 0 |  | 0 |  | 0 |  |  | 0
Notes
1 | Electrical panel and associated cabling and accessories shall be the part of Electrical BOQ.
2 | Estimated cost being furnished above does not include incidental civil, electrical and plumbing work which shall be carried out by respective agencies.
3 | Cost furnished above doesn't include GST.

## HVAC CONTROL LB
PRICED SCHEDULE OF QUANTITIES
HVAC SYSTEM FOR JSW
S. NO | ITEM DESCRIPTION | UNIT | B2 | AMOUNT | CONTROL ROOM | AMOUNT | LAB | AMOUNT | TOTAL QTY. | RATE | AMOUNT
SECTION 'A' : HVAC WORKS FOR OFFICE SPACES
1.0 | EQUIPMENT
1.1 | VARIABLE REFRIGERANT VOLUME SYSTEM
(HEAT PUMP & COOLING TYPE )
| Supply, Installation, Testing and Commissioning of Variable Refrigerant Volume type multi unit air-conditioning system complete with indoor and outdoor units with individual controller for cooling & heating application as per the specifications and drawings. The quoted price should include clearances charges, local taxes, freight etc. Quoted price shall also be inclusive of loading, unloading, lifting & shifting on outdoor location in space available at same floor level or at terrace at suitable locations as per drawing, positioning charges besides including charges towards structural steel supports, MS base frame duly painted & vibration isolation arrangement etc. |  |  | 0 |  | 0 |  | 0
|  |  |  | 0 |  | 0 |  | 0
1.1.1 | OUTDOOR UNITS |  |  | 0 |  | 0 |  | 0
|  |  |  | 0 |  | 0 |  | 0
| Supply, Installation, Testing and Commissioning of air cooled variable refrigerant flow modular type Coolin type units, each comprising of energy efficient multiple scroll compressors, full charge of R-410a refrigerant gas and all accessories as per the specifications. All compressors shall be inverter type. The condensing units shall be suitable to work on cooling as well as heating mode. The condensing units shall be suitable for operation on 415 ±10% volts, 50Hz, 3 phase AC power supply and complete with auto check function for connection error, auto address setting, etc. The outdoor units shall be low noise type. Quoted price shall be inclusive of Power Cable from MCCB to Outdoor unit & MS frame duly applied with 2 coat of primer & one coat of black enamel paint. The outdoor units shall be of following capacities :(Including Y-Joint) |  |  | 0 |  | 0 |  | 0 |  |  | 0
| Quoted price shall be inclusive of factory applied epoxy |  |  | 0 |  | 0 |  | 0 |  |  | 0
| coating (to prevent erosion of tubes & fins) of Outdoor units. |  |  | 0 |  | 0 |  | 0 |  |  | 0
| VRV ODUs shall be capable of operating in following range : i. For Cooling : (-)5degC to 50degC ii. For Heating : (-)20degC to 15.5degC if applicable |  |  | 0 |  | 0 |  | 0 |  |  | 0 | BLUESTAR
|  |  |  | 0 |  | 0 |  | 0 |  |  | 0
|  |  |  | 0 |  | 0 |  | 0 |  |  | 0
|  |  |  | 0 |  | 0 |  | 0 |  |  | 0
a. | 60 HP nominal capacity high COP outdoor unit. FOR LAB AREA (1W+1S) | No |  | 0 |  | 0 | 2 | 0 | 2 |  | 0
b. | 36 HP nominal capacity high COP outdoor unit. FOR OFFICE AREA | No |  | 0 |  | 0 | 1 | 0 | 1 |  | 0
c. | 28 HP nominal capacity high COP outdoor unit. | No |  | 0 | 1 | 0 |  | 0 | 1 |  | 0
d. | 22 HP nominal capacity high COP outdoor unit. For CONTROL ROOM (1W+1S) | No |  | 0 | 2 | 0 |  | 0 | 2 |  | 0
e. | 14 HP nominal capacity high COP outdoor unit. | No | 1 | 0 |  | 0 |  | 0 | 1 |  | 0
f. | 10 HP nominal capacity high COP outdoor unit. FOR CRITICAL AREA (1W+1S) | No |  | 0 | 2 | 0 | 2 | 0 | 4 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
1.2 | INDOOR UNITS |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| Supply, Installation, Testing and Commissioning of variable refrigerant volume modular type indoor units comprising of EEV & all accessories as per the specifications. The indoor units shall be suitable to work on cooling mode. The indoor units shall be suitable for operation on 220 ±6% volts, 50Hz, 1 phase AC power supply. Ductable indoor units shall be suitable to handle extent of ductwork as shown in the design drawings and dehumidified air quantity as mentioned in the heat load summary sheet under "Special Conditions" and the indoor units shall be of following capacities. All Indoor Units shall have inbuilt Drain Pumps . Quoted price shall be inclusive of Plug Top & necessary power cable. |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| DUCTABLE UNIT |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
i. | 2825 CFM Ductable Unit (8.0 TR) | No. |  | 0 | 4 | 0 | 6 | 0 | 10 |  | 0
iii | 2400 CFM Ductable Unit (6.4 TR) | No. |  | 0 | 2 | 0 | 2 | 0 | 4 |  | 0 | 6TR
iv. | 2047 CFM Ductable Unit (5.5 TR) | No. |  | 0 |  | 0 | 4 | 0 | 4 |  | 0 | 5TR
v. | 1624 CFM Ductable Unit (4.5 TR) | No. |  | 0 |  | 0 | 4 | 0 | 4 |  | 0 | 4TR
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| 4-WAY CASSETTE UNIT |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
i. | 1218 CFM Cassette unit Type (4.0 TR) | No. |  | 0 |  | 0 |  | 0 | 0 |  | 0
ii. | 1183 CFM Cassette unit Type (3.2 TR) | No. |  | 0 |  | 0 | 1 | 0 | 1 |  | 0
iii. | 830 CFM Cassette unit Type (2.5 TR) | No. |  | 0 | 1 | 0 | 1 | 0 | 2 |  | 0
iv. | 830 CFM Cassette unit Type (2.0 TR) | No. | 4 | 0 |  | 0 |  | 0 | 4 |  | 0
v | 812 CFM Cassette unit Type (1.6 TR) | No. |  | 0 |  | 0 | 3 | 0 | 3 |  | 0
vi. | 600 CFM Cassette unit Type (1.3 TR) | No. |  | 0 |  | 0 |  | 0 | 0 |  | 0
vii. | 459 CFM Cassette unit Type (1.0 TR) | No. |  | 0 |  | 0 |  | 0 | 0 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| COMPACT CASSETTE UNIT |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
ii. | 353 CFM Cassette unit Type (1.0TR) | No. |  | 0 | 5 | 0 |  | 0 | 5 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| HI WALL UNIT |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
i | 671 CFM Hi wall Type (2.0TR) | No. |  | 0 | 2 | 0 | 4 | 0 | 6 |  | 0
ii | 530 CFM Hi wall Type (1.6TR) | No. | 1 | 0 | 4 | 0 | 4 | 0 | 9 |  | 0
iii | 459 CFM Hi wall Type (1.3TR) | No. |  | 0 |  | 0 |  | 0 | 0 |  | 0
iv | 388 CFM Hi wall Type (1.0TR) | No. |  | 0 | 4 | 0 |  | 0 | 4 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
1.4 | REMOTE CONTROLS |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| Supply of Cordless handset type remote controls for the above indoor units. | No | 5 | 0 | 22 | 0 | 29 | 0 | 56 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| Supply, Installation, Testing & Commissioning of PLC Based Panel for sequencing & operational for VRF Units for UPS, Battery & Server Room | No |  | 0 | 3 | 0 | 3 | 0 | 6 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
1.5 | CENTRALISED CONTROLLER |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| Supply,Installation, Testing and Commissioning of main centralised controller as per specifications to hook up indoor units as mentioned above. Controller shall however, be suitable for minimum 64 groups of indoor units. Centralised controller shall act as master controller for controlling of outdoor units and their associated indoor units. Controller shall be suitable to configured the inside temperature as per temperature set point on controller. Quoted price shall be inclusive of all necessary cabling as required from ODU & IDUs to controller as required & other accessories as required to make the system proper fucntional. | No | 1 | 0 | 1 | 0 | 1 | 0 | 3 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
1.6 | DRAIN PUMP |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| Supply, Installation, Testing & Commissioning of Condensate Drain Pump with adequate Sump for Hi-wall units complete with water level sensor and accessories as required. Quoted price shall be inclusive of controller, NRVs & water sensors and associated wiring etc. to make installation complete. Drain Pump shall be suitable for operation on 220+6 % volts 50 Hz, 1phase AC power supply. Drain pumps shall automatically ON/Off based on water level. |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| Insulated Drain Tray with Drain Pump @5mtr head | Nos | 1 | 0 | 10 | 0 | 8 | 0 | 19 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
1.8 | INLINE FANS |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| Supply, Installation, Testing & Commissioning of circular /rectangular inline fans for exhaust air complete with sheet metal casing, direct driven centrifugal fan, motor with proper protection and inspection door. Fan shall be suitable for operation on 220+6 % volts, 50 Hz,1 phase AC power supply. Flanges to be provided on both sides to facilitate duct connections. Fan shall be installed as shown in the drawings and will be of following characteristics : All single phase inline fans shall be provided with factory fitted speed regulators. All Fans Should be complete with Plug Top & necessary power cable. |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| Fan Capacity S.P Area to |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| No. (Cfm) (mmWG) to be exhausted |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
i. | IF-2(Circular) 2500 25 Panel Room | No |  | 0 | 1 | 0 |  | 0 | 1 |  | 0
ii. | IF-2(Circular) 1600 25 Toilet | No |  | 0 |  | 0 |  | 0 | 0 |  | 0
iii. | IF-2(Circular) 900 25 Toilet | No |  | 0 |  | 0 |  | 0 | 0 |  | 0
iv | IF-2(Circular) 600 25 Toilet | No |  | 0 | 1 | 0 |  | 0 | 1 |  | 0
v. | IF-2(Circular) 400 25 Storage & Cable Celler | No |  | 0 | 2 | 0 |  | 0 | 2 |  | 0
vi. | IF-2(Circular) 300 25 Toilet ,PDS , Lab area & HVAC Room | No | 2 | 0 | 1 | 0 | 3 | 0 | 6 |  | 0
vii. | IF-2(Circular) 200 25 Pantry & Lab area | No | 2 | 0 | 1 | 0 | 5 | 0 | 8 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
2.1 | Propeller Fan |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| Supply, Installation, Testing and Commissioning of Propeller Fan, Installing in any position Horizontal or Vertical . Casing of Fans shall be constructed of heavy gauge sheet steel and preferably be powder coated. Support brackets for ceiling suspension or wall mounted shall be welded to the casing for connection to hanger bolts. Threaded Rod of sufficient dia. /channel should be considered for hanging of fans. |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| Provision of all necessary accessories such as Wire Guard on inlet side and bird screen on outlet, Gravity operated louver shutters, Canvass Connection for connecting Fan assembly and Plenum should be considered, If Ducted. |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| Should be suitable for 230 V ± 10% volts Single phase 50Hz, AC supply |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| 200 CFM, 15 mm SP For Pantry | No | 2 | 0 |  | 0 |  | 0 | 2 |  | 0
| 150 CFM, 15 mm SP For Pantry | No |  | 0 | 1 | 0 |  | 0 | 1 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
3 | PIPING |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
3.1 | COPPER REFRIGERANT PIPING |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| Supply, Installation, Testing & Commissioning of high pressure copper refrigerant piping including R410a refrigerant of suitable size as required and duly insulated with19mm/13mm thick closed cell elastomeric insulation with class 'O' fire retardant properties in tubing form. External Refrigerant piping shall be laid on GI covered cable trays. Piping inside occupied spaces shall be supported using MS hangers duly painted with black enamel paint. Entire refrigerant piping work shall be carried out in accordance with the specifications.MS sleeves of requisite size shall be provided at wall crossing. Quoted price shall be inclusive of necessary glass cloth and minimum two layers of UV protection paint to be applied over insulation for all exposed pipes of approved make. Piping shall be of following sizes : |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| Internal Refrigerant piping in exposed ceiling area & external refrigerant piping shall be laid on Ladder type cable trays. Cable trey used for external refrigerant piping shall be covered with cover. |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| Pipe Size Thickness of CSE |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| (O.D.) Insulation |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
a. | 41.3 mm 19 mm | RM |  | 0 |  | 0 | 105 | 0 | 105 |  | 0
b. | 34.9 mm 19 mm | RM |  | 0 | 50 | 0 | 30 | 0 | 80 |  | 0
d. | 28.6 mm 19 mm | RM | 30 | 0 | 22 | 0 | 20 | 0 | 72 |  | 0
f. | 22.2 mm 19 mm | RM |  | 0 | 40 | 0 | 36 | 0 | 76 |  | 0
g. | 19.1 mm 13 mm | RM |  | 0 | 45 | 0 | 110 | 0 | 155 |  | 0
h. | 15.9 mm 13 mm | RM |  | 0 | 25 | 0 | 40 | 0 | 65 |  | 0
i. | 12.7 mm 13 mm | RM | 50 | 0 | 55 | 0 | 30 | 0 | 135 |  | 0
j. | 9.5 mm 13 mm | RM |  | 0 | 42 | 0 | 86 | 0 | 128 |  | 0
k. | 6.4 mm 13 mm | RM | 30 | 0 | 48 | 0 | 30 | 0 | 108 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
3.2 | FITTINGS |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| Supply,Installation,Testing & Commissioning of following |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| imported copper fittings to be provided in |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| refrigerant pipe line. |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
a. | Refnet Joints (Y- Joints) | No | 5 | 0 | 23 | 0 | 31 | 0 | 59 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
3.3 | CONDENSATE DRAIN PIPING -cPVC |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| Supply, Installation, Testing and Commissioning of cPVC pipes cut to required lengths and installed for condensate drain. Quoted price shall be inclusive of supply and fixing in position the necessary fittings like elbows, tees reducers etc. and supporting arrangement in accordance with the approved shop drawings and specifications. Pipes shall be insulated with 9mm thick closed cell elastomeric insulation with class 'O' fire retardant properties in tubing form . Pipes shall be of following sizes : |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
a. | 50mm dia | RM |  | 0 |  | 0 |  | 0 | 0 |  | 0
b. | 40mm dia | RM |  | 0 | 10 | 0 | 25 | 0 | 35 |  | 0
c. | 32mm dia | RM | 10 | 0 | 25 | 0 | 40 | 0 | 75 |  | 0
d. | 25mm dia | RM | 15 | 0 | 40 | 0 | 110 | 0 | 165 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
3.4 | Cable Tray for Copper & Drain Pipe |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| Supply, fabricating and installing following sizes of hot dip galvanized perforated type Cable tray with cover including factory fabricated supports, horizontal and vertical bends, reducers, tees, cross members and other accessories as required and duly suspended from the ceiling with MS suspenders including painting, Covered in Exposed Area on Copper pipe etc. |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| 200 mm wide x 100 mm deep (2 mm) | RM |  | 0 | 55 | 0 | 150 | 0 | 205 |  | 0
| 150 mm wide x 100 mm deep (2 mm) | RM | 50 | 0 | 110 | 0 | 100 | 0 | 260 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
3.5 | FACTORY FABRICATED DUCTING |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| Supply , Installation and Testing of factory fabricated GSS ducting complete with vanes, splitter dampers, fire retardant gaskets hanging arrangement including fully threaded GI rods and GI "C" channels/ rolled steel wires or Gripple Wire Rope Hangers & Supports complete with end fixing, GI "C" channels etc. as approved by clients/consultants in accordance with the approved shop drawings and specifications. Quoted price shall be inclusive of necessary scaffolding charges towards installation of supply/exhaust air ducts outside or within building wherever required. Quoted price should also include necessary charges towards duct supporets including MS angle/channel arrangement as required for ducts being installed outside or within building wherever required. |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| Spacing between duct supports should not exceed 2m in both cases i.e GI rods with GI "C" channels & Gripple Wire Rope Hanger support . In case of Gripple Wire Rope Hanger support for duct sizes above 1800mm, MS angles duly painted with black enamel paint should be used along with neoprene pad in between the duct & MS angle. All duct support to be provided with check nuts (lock nuts). |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| While selecting the duct supports vendor shall ensure vibration free installation.Quoted price shall be inclusive. |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
a. | 24 G (0.60 mm) - 1 mm to 750 mm | SqM |  | 0 | 80 | 0 | 100 | 0 | 180 |  | 0
b. | 22 G (0.80 mm) - 751 mm to 1500 mm | SqM |  | 0 | 15 | 0 | 30 | 0 | 45 |  | 0
c. | 20 G (1.0 mm) - 1501 mm to 2250 mm | SqM |  | 0 |  | 0 |  | 0 | 0 |  | 0
c. | 18G (1.2 mm) - 2250 mm to Above Plenum | SqM |  | 0 | 25 | 0 | 45 | 0 | 70 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
3.6 | SITE FABRICATED DUCTING |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| Supply, Fabrication, Installation and Testing of sheet metal ducts complete with vanes, splitter dampers, hanging arrangement including check nuts in accordance with the approved shop drawings and specifications. |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
a. | 24 G (0.60 mm) - 1 mm to 750 mm | SqM |  | 0 | 8 | 0 | 10 | 0 | 18 |  | 0
b. | 22 G (0.80 mm) - 751 mm to 1500 mm | SqM |  | 0 |  | 0 | 4 | 0 | 4 |  | 0
c. | 20 G (1.00 mm) - 1501 mm to 2250 mm | SqM |  | 0 |  | 0 |  | 0 | 0 |  | 0
c. | 18 G (1.2 mm) - 2250 mm to Above & Plenum | SqM |  | 0 |  | 0 | 0 | 0 | 0 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
3.7 | Flat Oval Spiral Duct |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| Supply hollow partial pieces, Assembling, installation, testing and commissioning of G.S.S. metal ducting & as per ISI specifications & tender drawings. The price shall include with rolamate / TDF Corner flanges with nut bolt, cleat for clamping, self adhesive gasket / sealent (neoprene gasket) & supports (GI Threaded Rod & Chilly clamp (Thickness & Width shall be as per manufacturere Standard) by or Wire Rope Hangers etc. (Gripple Wire & Hangers can be used at site for support) |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| With 13 mm thick internal insulation |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| 22 G (0.80 mm) | SMT |  | 0 | 40 | 0 | 60 | 0 | 100 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
3.8 | DUCO PAINT (For Flat Oval Exposed Duct) |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| Supply and Application of minimum two coats of Duco Paint of colour and shade as approved by the Architects for exposed flat oval spiral/round ducts. Quoted price shall be inclusive of primer before paint and all neceesary arrangement as required for providing the paint over duct. shall be slected as per IGBC guidlines | SMT |  | 0 | 40 | 0 | 60 | 0 | 100 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
3.9 | Supply, Installation, Testing and Balancing of round supply air diffusers with removable key operated butterfly volume control dampers as per the approved shop drawings and specifications.The diffusers shall be anti-smudge flush type as approved by the interior designer. Diffuser shall be complete with GI cone with circular connection at the rear. |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| With Volume Control Dampers |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| 200mm dia Neck Size round diffuser with GI cone | NOS |  | 0 |  | 0 | 4 | 0 | 4 |  | 0
| 300mm dia Neck Size round diffuser with GI cone | NOS |  | 0 |  | 0 |  | 0 | 0 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
4 | FLEXIBLE CANVASS CONNECTIONS |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| Supply, Installation, Testing of 125mm deep antivibration flexible joints at the outlet of air handling units/ductable split units//inline fans. Flexible connections shall be constructed using imported fire retardant fabric with extruded aluminium frame/flange on both sides of approved make. | SqM |  | 0 | 5 | 0 | 15 | 0 | 20 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
5 | LINEAR GRILLES |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| Supply, Installation , Testing and Balancing of supply & return air grilles with vcd complete with fixed core as per approved shop drawings and specifications. The grilles shall be of approved colour & shade. |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| Powder coated aluminium grilles of extruded sections with integral flanges on both sides & ends as required complete with corner pieces. |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| i. 100/150/200/250 mm High grilles | SqM |  | 0 | 5 | 0 | 6 | 0 | 11 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
3.1 | Volume control dampers (VCD) |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| Supply,Installation, testing and commissioning of 16 G GSS constructed opposed blade volume control dampers complete with brass bush & manual operating handles within ducts to be provided with suitable links, levers and quadrants for control of volume of air flow for proper air balancing | SQM |  | 0 | 3 | 0 | 3 | 0 | 6 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
3.2 | CURVE GRILLES |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| Supply, installation, testing & commissioning of Powder coated Aluminium curve grilles for supply & return air normal flow one way as per specification & the sizes will be as per tender drawing mention: | SQM |  | 0 | 3 | 0 | 2 | 0 | 5 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
3.2 | AIR TRANSFER GRILLES |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| Supply, Installation and Testing of of extruded aluminium powder coated air transfer grilles to be provided at the door of toilets/pantry. | SqM | 1 | 0 | 2 | 0 | 2 | 0 | 5 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
3.3 | Supply, Installation and testing of Powder coated Aluminium extruded Fresh / Exhaust air louvers with bird screen as specification and shop drawing. | SqM | 1 | 0 | 2 | 0 | 2 | 0 | 5 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| Return Air Baffles |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| Supply, Fabrication, Installation and Testing of return air baffles made of 24 G GS sheet metal (class VIII-120GSM Zinc Coaing) ducts with 12 mm open cell Nitrile Rubber foam within 160-180 Kg/m3 density acoustic insulation, hanging arrangements in accordance with the approved shop drawings and specifications. | SMT |  | 0 | 5 | 0 | 5 | 0 | 10 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
3.4 | INSULATION |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| ACOUSTIC LINING OF DUCTS |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| Using Open Cell Nitirile Rubber |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| Supply and Application of internal acoustic lining of supply air ducting using open cell nitrile rubber insulation with density within 140-180 Kg/m3 as per the approved shop drawings and specifications. Insulation material shall be bonded with the ducts using metal screw and washers to facilitate grip to the GI sheet. |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| 15mm thick lining | SMT |  | 0 | 60 | 0 | 80 | 0 | 140 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
3.5 | THERMAL INSULATION OF DUCTS |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| (Class 'O' Fire Retardant Properties Closed Cell Elastomeric insulation) |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| Supply and Application of external thermal insulation of supply /return air ducting using closed cell elastomeric nitrile rubber insulation with class 'O' fire retardant properties as per the specifications and drawings. Adhesive - AC Duct King Eco Fresh |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
a. | 13mm thick insulation-For Supply Air ducts in ac area | SqM |  | 0 | 108 | 0 | 170 | 0 | 278 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
b. | 19mm thick insulation-For Supply Air ducts in non-ac area(Exposed to sun) | SqM |  | 0 |  | 0 |  | 0 | 0 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
3.6 | ELECTRICAL WORKS |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| Power Distribution of HVAC System Shall be covered in main electrical package |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| Incoming power supply shall be provided by main electrical contractor/ |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| electrical consultant at each HVAC Equipment, VRV Indoor & |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| outdoor unit along with a TPN MCCB and earthing. |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
3.7 | Control & Transmission Wiring |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
a. | Providing & fixing control cum transmission wiring of 2 core/4.0Core x 1.5/2.5 sqmm copper in suitable conduits between indoor and out door unit & their remotes. | Rmt. | 60 | 0 | 165 | 0 | 220 | 0 | 445 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
1.1 | CO2 SENSOR with display |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| SITC of CO2 Sensor for rooms only with display with (WiFi Enable/BMS Compatible) | Nos. |  | 0 |  | 0 |  | 0 | 0 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
1.2 | INDOOR AIR QUALITY MONITOR WITH DISPLAY |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| SITC of IAQ Monitor with Display to measure the levels of PM 2.5, VOCs, CO2, Temperature, Humidity on a real time basis. The IAQ Monitor shall be RS485 enabled and should be capable of getting connected with Wi-Fi. The Monitor should be capable of sending the indoor air quality information on remote LED displays as well. The Monitor should indicate the quality of air through changing the colours as per the NAAQS standards and should meet the WELL/LEED building standards. | Nos. |  | 0 |  | 0 |  | 0 | 0 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
1.3 | BIO POLAR IONISER |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| The Active Air Purification system should consist of Supply, Installation, Testing and commissioning of Bipolar Ionisation System. The Bipolar Ionisation System must be a combination of Tube Based Model and Needle Point Model (Needle Point should have Nitinol (nickel titanium) Needles) and Carbon Fibre Brush Model, System should produce positive and negative ions for creating a Bio Climate rich in ions and hence neutralising harmful pollutants including pathogens, Volatile Organic Compounds and Particulate Matter. |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| Manufacturers shall provide Test report from Internationally/Nationally recognized Lab for proven efficacy on below pathogens with minimum kill rates for the following pathogens given the allotted time and in a space condition: a) SARS-CoV-2 (COVID-19) Human Strain b) MS2 Bacteriophage (Surrogates COVID-19) c) Omicron Variant of SARS-CoV-2 d) H1N1 e) Total Bacterial Count Reduction rate of more than 90% from NABL Accredited Lab f) Yeas & Mold/Total fungal count Reduction rate of more than 90% from NABL Accredited Lab |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| For Cassette / Hi Wall units | Nos. |  | 0 |  | 0 |  | 0 | 0 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
1.4 | INDOOR AIR PURIFYING IONISERS(For Ductable Units) |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| (REME Cell/Bi Polar Plasma Ionnisers) |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| Supply, Installation, Testing & Commissioning of REME (reflective electromagnetic energy cell) /Bi Polar Plasma Ionisers cell comprising of quad metallic compound target/ hydrated cataytic matrix cell duly enclosed by a poly casing tube, with the capability to produce friendly oxidizers like ionized hydroxyls, hydrogen peroxide, Super Oxide Ions. The tube should be duly encased in poly tube to prevent glass or mercury leakage into the atmosphere. The cell will have built in fiber optic device as remote indication of this operation. |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| The unit shall have inbuilt multipin ion generator along with ultrasonic radio frequency waves for pest repellancy. System should be suitable for all types of indoor units AHU, TFA, Ductable ac, Cassette AC& hi-wall units. The cells shall be installed as required to fit in the plenum, duct at the AHU in the supply air stream. |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| The system shall be capable of reducing microbial bacteria, virus and spores, VoC’, odors and particulates matter. The equipment shall conform to UL, TUV, CSA EU,CE, FDA, ISO, RoHS & CCMB Report standards, certifications as applicable and shall be submitted along with the technical submital. System should kill /deactivate microorganism and shall have proven effectiveness on COVID-19 human strain and its surrogate through Certified National/International lab. Units shall be UL2998 certified for Zero Ozone. |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| The power / control cabling between the ioniser units and the power source / controls shall be included in the cost. The ionizers should be selected by considering a load factor calculation for each specific area where the equipment is to be installed. Length selection should be per duct piece in which is to be installed. Detailed selection chart to be furnished indicating the model number for each unit. Cells Should be complete with Transformers, control cabling and Plug Top & necessary power cable. |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| Total Nos. of ionisers shall be as per air quantity distributed in individual duct drawn from main plenum/ AHUs in approved shop drawing. |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
a. | 2825 CFM Ductable Unit (8.0 TR) | No. |  | 0 |  | 0 |  | 0 | 0 |  | 0
b. | 1377 CFM Ductable Unit (8.0 TR) for TFA | No. |  | 0 |  | 0 |  | 0 | 0 |  | 0
c. | 1624 CFM Ductable Unit (4.5 TR) | No. |  | 0 |  | 0 |  | 0 | 0 |  | 0
d. | 1377 CFM Ductable Unit (4.0 TR) | No. |  | 0 |  | 0 |  | 0 | 0 |  | 0
e. | 1024 CFM Ductable Unit (6.5 TR) for TFA | No. |  | 0 |  | 0 |  | 0 | 0 |  | 0
f. | 1130 CFM Ductable Unit (3.2 TR) | No. |  | 0 |  | 0 |  | 0 | 0 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| Electrically Charged Filter a) "Air purification for ceiling suspended Ductable indoor units and AHUThe air purification system should be suitable to reduce harmful pollutants like particulate matter (PMx), PM 2.5, allergens, pollen, smoke, bacteria, pathogens etc. based on below principle technology viz;Impingement, Polarisation and Agglomeration as a passive air purification It should be a slim structured unit specifically designed for integration in Return Air path of ceiling suspended indoor units/AHU to centrally capture. It should be equivalent to Merv-14 or Higher efficiency for AHU and Ductable* Units with low pressure drop. It should have 3x working principles and it should be aluminium based or powder coated steel casing and should be self-contained. It should be a US patented technology with UL certified components. The units shall meet ANSI/ASHRAE 52.2 standards and have valid test report to verify filtration efficiency. The Basic Media of Electric Filter shall Carry Class 2 Fire Rating Listing by UL.The EAC filter/Electrostatic percipitator (ESP), which have Metal based collection plate shall not be accepted. The Supplier shall carry UL2998 certification or at least Acknowledgement letter from UL2998 for testing against Zero Ozone Emission. The system shall be integrated with the existing pre-section filter area of Units. The test report for pressure drop need to be submitted for passive air purification and the same shall be demonstrated at site." |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| Ionizers shal be suitable for following Equipment |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
a. | 2825 CFM Ductable Unit (8.0 TR) | No. |  | 0 |  | 0 |  | 0 | 0 |  | 0
b. | 1377 CFM Ductable Unit (8.0 TR) for TFA | No. |  | 0 |  | 0 |  | 0 | 0 |  | 0
c. | 1624 CFM Ductable Unit (4.5 TR) | No. |  | 0 |  | 0 |  | 0 | 0 |  | 0
d. | 1377 CFM Ductable Unit (4.0 TR) | No. |  | 0 |  | 0 |  | 0 | 0 |  | 0
e. | 1024 CFM Ductable Unit (6.5 TR) for TFA | No. |  | 0 |  | 0 |  | 0 | 0 |  | 0
f. | 1130 CFM Ductable Unit (3.2 TR) | No. |  | 0 |  | 0 |  | 0 | 0 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| HYDROGEN EXHAUST |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| INLINE FANS - For Hydogen Exhaust |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| Supply, Installation, Testing and Commissioning of circular inline fans for exhaust complete with sheet metal casing, direct driven centrifugal fan constructed out of GSS, class "B" insulated motor with proper protection and inspection door. Fan shall be suitable for operation on 415 ±10% volts, 50Hz, 3 phase AC power supply. Flanges to be provided on both sides to facilitate duct connections. Fan shall be provided with factory fitted speed regulation arrangement. Fan shall be Explosion Proof Type. Fan shall be installed as shown in the drawings and will be of following characteristics : |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| Quoted price shall be inclusive of gravity louvers. |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| Fan Capacity S.P Area to |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| No. (Cfm) (mmWG) to be exhausted |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| IF-1,2 150 15-16 Battery Room | No |  | 0 | 1 | 0 | 1 | 0 | 2 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| HYDROGEN SENSORS |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| Supply, Fixing and Testing of H2 Sensors. Sensors should be capable to give command directly to Inline fan panel after increasing of H2 level beyond certain specified levels. Quoted price shal be inclusive of Power cabling and control cabling as required between sensor & panels etc. Sensors should be able to automatically switch ON/OFF the Fans after increasing/control of H2 level beyond certain specified levels respectively. Price shall also be inclusive of all accessories required to make installation complete whether specified or not. H2 sensors shall be capable for BMS Integration as well. | No |  | 0 | 1 | 0 | 1 | 0 | 2 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| Panels - Hydrogen Exhaust |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| Supply, Installation, Testing and Commissioning of the following cubical type panels made out of 14 guage CRCA structure, base channel, complete with, moulded case circuit breakers, meters, indicating lamps, current transformer etc. Complete in all respects, insulated bus bars with heat shrinkable PVC sleeve in suitable bus chambers, interconnection, small wiring, name plate, danger plate, earth bus etc. & comprising of compartments with hinged door for each feeder & its accessories, cable alley with hinged doors, bus chamber with bolted door etc. The panel being of dust & vermin proof construction with rubber gasket attractively powder coating etc. The panel shall be free standing type / wall mounted type as per relavant drawing and comprising with the following: |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| Notes : |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| 1. All MCCBs shall be with operating handle. |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| 2. CTs burden shall be 15VA & accuracy class 1.0 |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| 3. CTs shall be cast resin type . |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| 4. All MCCBs shall be with thermal magnetic |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| release. |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| 5. All indication lights shall be LED type. |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| 6. All meter shall be digital type. |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| 7. The outgoing starter feeders for pumps,AHUS |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| & ventilation fans shall be provided |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| with push buttons & indicating lamps for |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| status indication. |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| 8. Proper isolation switches to be |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| provided near air handling units and |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| ventilation fans in weather proof enclosure. |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| 9. Bimetal overload relay for all the |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| starters shall have built-in single |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| phasing prevention feature. |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| 10. Electrical interlocking wiring shall be |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| provided as per system requirement. |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| 11. Power cabling/wiring with necessary |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| earthing from source to each panel |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| and each exhaust fan shall be |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| provided by other agencies. |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| 12. All HVAC equipment shall be compatible with |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| BMS and necessary provisions to be made |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| in each panel. |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| Explosion Proof Fan Panel-1 (Location : Near Fan) | No |  | 0 | 1 | 0 | 1 | 0 | 2 |  | 0
| For Battery Room - 90W |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| 1x150Cfm Fan |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| 10 Amps ,TP MCB -- 1set |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| (0-500) V digital Voltmeter with built in Selector |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| switch -- 1set |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| Digital Ammeter with built in selector |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| switch- 1set |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| Current Transformers - 1set |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| LED type RYB phase indication lights- 1set |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| LED type ON & OFF indication lights -- 1set |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| START-STOP Push Buttons -- 1set |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| 90 Watt DOL starter with built-in single phasing |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| preventer & overload relay -- 1 set |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| Auto-Manual type selector switch |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| to facilitate auto start of Fans |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| after restoration of power -- 01 set. |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| Timer for Scheduled On/Off-- 01 set. |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| Contactors, Potential Free Contacts, Control wiring and |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| safety circuit as required with start-stop push buttons |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| stay put or lockable type -1 set. |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| (Panel to be integrated with Hydrogen Sensor for ON/Off operation). |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| CABLING |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| Supply, laying, affecting connections and Testing of the following sizes of 1.1 KV armoured PVC insulated copper/ aluminium conductor cables. Cables shall be inclusive of all clamps, saddles, screws, cable identification tags, cable terminal joints including terminal lugs, insulating tapes, affecting terminal connections to the equipment as per the specifications and as required. Quoted price shall be inclusive of perforated duly painted 2mm thick MS trays and 8 SWG copper earth wire for AHUs. |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| All cables shall be FRLS type. |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| 3 C x 2.5 Sqmm cable (Copper) | RMT |  | 0 | 50 | 0 | 50 | 0 | 100 |  | 0
|  |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
| TOTAL |  |  | 0 |  | 0 |  | 0 | 0 |  | 0
Notes
1 | Electrical panel and associated cabling and accessories shall be the part of Electrical BOQ.
2 | Estimated cost being furnished above does not include incidental civil, electrical and plumbing work which shall be carried out by respective agencies.
3 | Cost furnished above doesn't include GST.